## Read Me
Energize Connecticut Heat Pump Qualified Products List (HPQPL)
This Qualified Products List (QPL) is dated 2/26/25
Pre-Approval required for projects totaling more than 20 tons, or more than $30,000 in rebates Please email CommercialHPRebates@ri-message.com to request pre-approval
Air Source Heat Pumps
Air Source Heat Pumps < 5.4 Tons Rebates Available to Residential and Commercial Customers
Minimum Efficiency Requirements1 |  |  |  | HSPF22 | SEER23 | HCR @5°F4 |  | COP5 @5°F
Ductless |  | Mini-Split | Single-Zone | 8.5 | 15.2 | 70% |  | 1.75
Ductless |  | Mini-Split | Multi-Zone
Ducted |  | Mini-Split | Single-Zone | 8.1 | 15.2 | 70% |  | 1.75
Ducted |  | Mini-Split | Multi-Zone
Ducted |  | Central | --
Ducted |  | High Velocity | -- | 7 | 12.5 | 70% |  | 1.5
Single Packaged Roof Top Units (Commercial Only) |  |  |  | 7.2 | 15.2 | 10.6 EER2⁶
Air Source Heat Pumps > 5.4 Tons Rebates Available to Commercial Customers
Equipment Capacity |  |  |  | Minimum Efficiency Requirements
Tons |  | Btu / Hr |  | IEER |  |  | COP @47F
≥ 5.4 to < 11.25 Tons |  | ≥ 65,000 to < 135,000 BTUs |  | 15.4 |  |  | 3.5
≥ 11.25 to < 20 Tons |  | ≥ 135,000 to < 240,000 BTUs |  | 14.6 |  |  | 3.4
≥ 20 to < 30 Tons |  | ≥ 240,000 to < 375,000 BTUs |  | 13 |  |  | 3.3
1 Aligns with ENERGY STAR 6.1 Cold-Climate Specification 2 Heating Season Performance Factor 3 Seasonal Energy Efficiency Ratio 4 Heating Capacity Ratio, calculated by dividing "Heating Capacity at 5°F as calculated by M1" by "Heating Capacity (H1Full) - Single or High Stage (47F), btuh" 5 Coefficient of Performance, "Heating COP at 5°F as calculated by M1"
Variable Refrigerant Flow (VRF) Heat Pumps Rebates Available to Commercial Customers
Equipment Capacity |  |  |  | Minimum Efficiency Requirements
Tons |  | Btu / Hr |  | EER |  | IEER |  | COP @47F
≥ 5.4 to < 11.25 Tons |  | ≥ 65,000 to < 135,000 BTUs |  | 11.3 |  | 18.9 |  | 3.4
≥ 11.25 to < 20 Tons |  | ≥ 135,000 to < 240,000 BTUs |  | 10.9 |  | 18 |  | 3.3
≥ 20 Tons |  | ≥ 240,000 BTUs |  | 9.6 |  | 16.4 |  | 3.25
Ground Source Heat Pumps
Rebates Available to Residential Customers
Minimum Efficiency Requirements
See Energy Star Certified List
Rebates Available to Commercial Customers
Equipment Capacity7 |  |  | Minimum Efficiency Requirements7
Tons | Btu / Hr |  | Type |  |  | EER |  | COP @47F
< 11.25 Tons | < 135,000 BTUs |  | Brine-to-Air |  |  | 17.1 |  | 3.6
< 5.4 Tons | < 65,000 BTUs |  | Brine-to-Water |  |  | 16.1 |  | 3.1
≥ 5.4 to < 11.25 Tons | ≥ 65,000 to < 135,000 BTUs |  | Brine-to-Water |  |  | 16.1 |  | 3
7 The qualifying EER, COP and BTUs are based on the equipment’s Ground-Loop Heat Pump “GLHP” ratings listed by AHRI regardless of the install type
Air to Water Heat Pumps
Rebates Available to Residential Customers
Criteria
• Minimum COP of 1.7 while delivering 110°F supply water at an outside temperature of 5°F.
• Fully displacing existing hydronic heating
• Maximum 6 tons nominal capacity
The Data Fields below are sourced directly from the AHRI Directory of Cerified Product Performance
AHRI Directory
Air Source Heat Pumps < 5.4 Tons |  |  | Air Source Heat Pumps > 5.4 Tons |  | VRF Heat Pumps |  |  | Ground Source Heat Pumps
AHRI Certified Reference Number |  |  | AHRI Certified Reference Number |  | AHRI Certified Reference Number |  |  | AHRI Certified Reference Number | QPL Column Header | AHRI WSHP Data Field | AHRI DGX Data Field
Brand Name |  |  | Brand Name |  | Brand Name |  |  | Brand Name | Outdoor Unit Model Number | Model Number | Compressor Unit Assembly
AHRI Type |  |  | AHRI Type |  | AHRI Type |  |  | AHRI Type | Indoor Unit Model Number(s) | Indoor Unit Model Number | Indoor Air Handler
Indoor Type |  |  | Outdoor Unit Model Number |  | Indoor Type |  |  | Program Type | Full Load Cooling Capacity (Btuh) | Full Load GLHP Cooling Capacity (Btuh) | Full Load Cooling Capacity (Btuh)
Outdoor Unit Model Number |  |  | Indoor Unit Model Number |  | System Model Number |  |  | Outdoor Unit Model Number | Full Load Heating Capacity (Btuh) | Full Load GLHP Heating Capacity (Btuh) | Full Load Heating Capacity (Btuh)
Indoor Unit Model Number(s) |  |  | Cooling Capacity (95F) |  | Module Model Number 1 |  |  | Indoor Unit Model Number(s) | Some of the Residential GSHP column headers are composed of combined data fields across multiple AHRI types. See above which QPL columns align with which AHRI data fields.
Furnace Model Number |  |  | EER (95F) |  | Module Model Number 2 |  |  | Full Load GLHP Cooling Capacity (Btuh)
Cooling Capacity (AFull) - Single or High Stage (95F), btuh |  |  | IEER |  | Module Model Number 3 |  |  | Full Load GLHP Cooling EER (Btuh/watt)
SEER2 |  |  | COP at 47°F |  | Cooling Capacity (95F) |  |  | Full Load GLHP Heating COP
EER2 (AFull) - Single or High Stage (95F) |  |  | Heating Capacity at 47°F |  | EER (95F) |  |  | Full Load GLHP Heating Capacity (Btuh)
HSPF2 (Region IV) |  |  | Heating Capacity at 17°F |  | IEER
Heating Capacity (H1Full) - Single or High Stage (47F), btuh |  |  | COP at 17°F |  | High COP (47F)
Heating Capacity at 5°F as calculated by M1 |  |  |  |  | High Heating Capacity (47F)
Heating COP at 5°F as calculated by M1 |  |  |  |  | Low Heating Capacity (17F)
Heating Capacity at 17°F as calculated by M1 |  |  |  |  | Low COP (17F)
Criteria Category | AHRI Types
Ducted | ·HRCU-A-CB = Split System: Heat Pump with Remote Outdoor Unit-Air-Source ·HRCU-A-C =Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source (Ducted) ·HSP-A = Single-Package Heat Pump Air-Source ·HMSV-A-CB = Multi-Split Heat Pump (Ducted, Mixed) ·HMSR-A-CB = Multi-Split Heat Recovery Heat Pump (Ducted, Mixed)
Ductless | ·HRCU-A-CB-O =Mini-Split Heat Pump, with Remote Outdoor Unit Air-Source, Free Delivery ·HMSV-A-CB-O = Multi-Split Heat Pump, Free Delivery (Non-ducted) ·HMSR-A-CB-O = Multi-Split Heat Recovery Heat Pump, Free Delivery (Non-ducted)
Integrated Controls
Integrated controls automatically switch between a heat pump and fossil fuel heating system at a pre-set outdoor temperature.
If configured to provide automatic changeover from heat pump to backup heating system, switchover temperature must be set below 30°F.
Eligibility
For more information about residential heat pump rebates: Click Here
For more information about commercial heat pump rebates: Click Here
Instant Discounts are no longer available for Air Source Heat Pumps and Variable Refrigerant Flow (VRF) Heat Pumps A stipend of $100/unit will continue to be available to distributors for all eligible systems sold to residential and commercial electric customers

## ASHP < 5.4 Tons
Qualified Product List for Air Source Heat Pumps < 5.4 Tons
AHRI Certified Reference Number | Tonnage | IRA Tax Credit Eligibility 2024 | IRA Tax Credit Eligibility 2025 | Brand Name | AHRI Type | Indoor Type | Outdoor Unit Model Number | Indoor Unit Model Number(s) | Furnace Model Number | Cooling Capacity (AFull) - Single or High Stage (95F), btuh | SEER2 | EER2 (AFull) - Single or High Stage (95F) | HSPF2 (Region IV) | Heating Capacity (H1Full) - Single or High Stage (47F), btuh | Heating Capacity at 5°F as calculated by M1 | Heating Capacity Ratio @ 5°F | Heating COP at 5°F as calculated by M1 | Heating Capacity at 17°F as calculated by M1 | Refrigerant Type
213351328 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PE(S,T)354 |  | 23000 | 15.5 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.81 | 19200 | R-410A
213296455 | 3 | No | No | SAMSUNG | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AC036BXUDCH | MSVT36***8U4YHX |  | 36000 | 17 | 9 | 8.1 | 33600 | 31800 | 94.64% | 1.9 | 36200 | R-410A
216957160 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X2C100M5PTC | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.82 | 35800 | R-454B
211175681 | 2.95 | No | Yes | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1536S1R-**A | MCG48T(C,D)2M | GDD96C110C5M | 35400 | 16.4 | 13 | 8.2 | 32000 | 22400 | 70% | 2.8 | 18700 | R-410A
211176425 | 3.71 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | MCG48T(C,D)2M | GUH96C110C5M | 44500 | 15.4 | 12.3 | 8.3 | 45000 | 31600 | 70.22% | 2.82 | 13700 | R-410A
214649681 | 1.8 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | PE(S,T)354 |  | 21600 | 15.2 | 11.2 | 8.1 | 23600 | 22000 | 93.22% | 1.8 | 16000 | R-410A
214728491 | 1.7 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | PE(S,T)274 |  | 20400 | 18 | 11.7 | 8.5 | 23200 | 17600 | 75.86% | 2 | 22400 | R-410A
214728492 | 1.73 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | PE(S,T)284 |  | 20800 | 18 | 11.7 | 8.5 | 23200 | 17600 | 75.86% | 2 | 22400 | R-410A
211176421 | 3.58 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | (C,M,V)CG48P(B,C,D)1M+TXV | GUH96C110C5M | 43000 | 15.3 | 12.3 | 8.3 | 45000 | 31600 | 70.22% | 2.79 | 13500 | R-410A
211176431 | 3.67 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | MCG60T(C,D)2M | GUH96C110C5M | 44000 | 15.5 | 12.4 | 8.4 | 45000 | 31600 | 70.22% | 2.86 | 13400 | R-410A
213296454 | 4 | No | No | SAMSUNG | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AC048BXUPCH | MSVT48***9U4YHX |  | 48000 | 17 | 8.6 | 8.5 | 43000 | 41500 | 96.51% | 1.94 | 45500 | R-410A
215654393 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | RE(S,T)304 |  | 22200 | 15.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.76 | 19100 | R-410A
213821648 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96MSN1002122A* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.71 | 29000 | R-410A
213205525 | 2.88 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80ES(N,L)0901714A* | 34600 | 16 | 9.9 | 8.5 | 38500 | 31400 | 81.56% | 2.75 | 29000 | R-410A
213205576 | 2.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92ESN0601412A* | 35400 | 15.2 | 9.5 | 8.1 | 39500 | 32000 | 81.01% | 2.52 | 29600 | R-410A
213205611 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92ESN1002122A* | 35400 | 15.5 | 10.5 | 8.5 | 39500 | 31600 | 80% | 2.71 | 29400 | R-410A
216955363 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C080M5PCA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
216955372 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1B060M4PSC | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
216955397 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060D3PSC | 31400 | 16 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
216955413 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100D5VSB | 31800 | 16.5 | 12 | 8.1 | 29200 | 20600 | 70.55% | 2.92 | 20200 | R-454B
215654392 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PE(S,T)284 |  | 22200 | 15.2 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.73 | 19100 | R-410A
216955422 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1B080U4PSB | 31800 | 16 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.93 | 20000 | R-454B
214572633 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X42L21A*+WALLCON | *97CMN0802120B* | 31800 | 17 | 11 | 8.5 | 32800 | 24400 | 74.39% | 1.9 | 31200 | R-410A
214572853 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X48L24A*+WALLCON | *95CSU1002122B* | 32400 | 17.5 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 2 | 31400 | R-410A
214572953 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L21A*+WALLCON | *80CTL0702120B* | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 25000 | 78.12% | 2 | 31200 | R-410A
213204404 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0451712A* | 23800 | 17 | 10 | 8.5 | 26200 | 24800 | 94.66% | 2.57 | 24400 | R-410A
213204424 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0701712A* | 23200 | 17 | 10 | 8.5 | 25600 | 25200 | 98.44% | 2.55 | 24600 | R-410A
213204455 | 1.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0901714A* | 23200 | 16.7 | 10 | 8.3 | 25600 | 26200 | 102.3% | 2.71 | 25200 | R-410A
213204822 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)1102120A* | 23800 | 16.5 | 10.3 | 8.5 | 26200 | 20200 | 77.1% | 2.99 | 19100 | R-410A
213204942 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0601412A* | 23200 | 15.9 | 9.8 | 8.5 | 26000 | 20400 | 78.46% | 2.97 | 19100 | R-410A
213204991 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0401410A* | 23000 | 16 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
213205008 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0401712A* | 23200 | 16 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
216955378 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1C100M5PSC | 32000 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.95 | 20200 | R-454B
216955428 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2B060U4PSB | 31600 | 16 | 11.7 | 8.1 | 28600 | 20600 | 72.03% | 2.91 | 20000 | R-454B
213752180 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M17**12 | 23600 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.87 | 19800 | R-410A
216764403 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC007AS3 | S9V2C100D4VSB | 31800 | 16.5 | 11.5 | 9 | 31600 | 23600 | 74.68% | 2.1 | 21000 | R-454B
216764404 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC007AS3 | S8X1C100M5PSC | 33400 | 17.1 | 12 | 9 | 32600 | 24000 | 73.62% | 2.1 | 21200 | R-454B
216764405 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC009AS3 | *UHMC100CCV4 | 34000 | 17.5 | 12.5 | 9 | 32200 | 23800 | 73.91% | 2.2 | 21000 | R-454B
216764436 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D008AS3 | L8V1C100U5VSB | 43000 | 16.5 | 12 | 9 | 44500 | 32600 | 73.26% | 2.2 | 29600 | R-454B
216764486 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCD010AS3 | S9V2C100U4VSB | 43000 | 16.5 | 12 | 9 | 44000 | 32000 | 72.73% | 2.1 | 29200 | R-454B
216764505 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D010AS3 | S9V2D120U5PSC | 52500 | 16.5 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 33800 | R-454B
216764537 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TXCD010AS3 | S8X1D120M5PSC | 52000 | 16.5 | 11.2 | 8.7 | 51000 | 38500 | 75.49% | 2.2 | 33800 | R-454B
213752199 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M17**16 | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752266 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*B110M21**20 | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213752314 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*B090V17**16 | 23400 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.87 | 20000 | R-410A
213752416 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2E100M21**20 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752531 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SP6A080V17**16 | 23800 | 16 | 9 | 8.1 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213752635 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B045M14**12 | 23400 | 17 | 10 | 8.5 | 27000 | 20400 | 75.56% | 2.88 | 19400 | R-410A
216955359 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B080M4PCA | 32000 | 16 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216955361 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B080M4PDA | 32000 | 16 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216955411 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100D4VSB | 32000 | 16.5 | 12 | 8.1 | 29200 | 20600 | 70.55% | 2.89 | 20200 | R-454B
216955426 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2B040U3PSB | 31800 | 16 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.94 | 20200 | R-454B
216955477 | 2.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2A040M3PSC | 30600 | 16 | 12 | 8.1 | 27800 | 20200 | 72.66% | 2.82 | 19700 | R-454B
216956813 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | S9X1B080D4PSB | 32400 | 16 | 12 | 8.1 | 29200 | 21000 | 71.92% | 2.9 | 20400 | R-454B
216956814 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | S9X2B040D3PSB | 32200 | 16 | 12 | 8.1 | 29000 | 20600 | 71.03% | 2.9 | 20200 | R-454B
213205159 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0702116A* | 29600 | 15.2 | 9 | 8.1 | 33600 | 23800 | 70.83% | 2.69 | 23200 | R-410A
213205274 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *80ES(N,L)1552420A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.7 | 23400 | R-410A
211176503 | 3.75 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | MCG48T(C,D)2M | GUH97M090C3M | 45000 | 15.2 | 12.3 | 8.1 | 45000 | 31600 | 70.22% | 2.8 | 13700 | R-410A
216955350 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | *UHMB060CCV3 | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.94 | 20200 | R-454B
216955370 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C100M5PDA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
216955387 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2C080M5PTC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216955418 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1B040U3PSB | 31800 | 16 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.94 | 20200 | R-454B
215678015 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN1002122B* | 56000 | 18.5 | 9 | 9 | 60000 | 42000 | 70% | 2.02 | 51500 | R-454B
213204827 | 1.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92ESN0401410A* | 23000 | 15.3 | 9.8 | 8.4 | 26000 | 20400 | 78.46% | 2.92 | 19100 | R-410A
213204888 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92ESN0802120A* | 23800 | 17 | 10.4 | 8.5 | 26000 | 20200 | 77.69% | 3.03 | 19000 | R-410A
213204893 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92ESN0802120A* | 23800 | 17 | 10.3 | 8.5 | 26000 | 20200 | 77.69% | 3.03 | 19000 | R-410A
213203932 | 1.5 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0451412A* | 18000 | 16.5 | 11 | 8.5 | 18700 | 13800 | 73.8% | 2.29 | 14200 | R-410A
213205011 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0401712A* | 23400 | 16 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
214573053 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L24A*+WALLCON | *97CMN0802120B* | 33200 | 17.5 | 11.5 | 8.5 | 31800 | 24800 | 77.99% | 2 | 31200 | R-410A
215439645 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80TC0805C*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
211175680 | 2.95 | No | Yes | Century | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1536S1R-**A | MCG48T(C,D)2M | GDD96C110C5M | 35400 | 16.4 | 13 | 8.2 | 32000 | 22400 | 70% | 2.8 | 18600 | R-410A
213205058 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0802120A* | 23600 | 17 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
215869093 | 2.65 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X36A1 | 5PX*C005AS3 | S9V2C100U5VSB+LRP | 31800 | 18.1 | 10 | 8.5 | 32800 | 25400 | 77.44% | 2.1 | 31000 | R-454B
216955369 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C100M5PCB | 32200 | 16.5 | 12 | 8.1 | 29000 | 21000 | 72.41% | 2.95 | 20400 | R-454B
216955385 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2B080M4PTC | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.94 | 20200 | R-454B
216764587 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S8X2A040M3PTC | 32400 | 17.1 | 11.5 | 8.7 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
215418108 | 4.33 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-4860A | HG86960+TD |  | 52000 | 15.2 | 10.5 | 8.6 | 51000 | 36800 | 72.16% | 1.9 | 41000 | R-410A
213205035 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0601714A* | 23800 | 16.5 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.91 | 19100 | R-410A
213205055 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0802120A* | 23600 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213205062 | 1.88 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN1002120A* | 22600 | 16.8 | 10.2 | 8.4 | 25200 | 19900 | 78.97% | 2.94 | 18600 | R-410A
213205080 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN1002122A* | 23600 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
216955349 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | *UHMB060ACV3 | 32000 | 16 | 11.7 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
215941129 | 3.79 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN1202422A* | 45500 | 21.5 | 11.5 | 9.5 | 48500 | 36600 | 75.46% | 2 | 39500 | R-454B
215941599 | 3.71 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN0802120A* | 44500 | 20 | 11 | 8.1 | 52000 | 38000 | 73.08% | 1.9 | 43500 | R-454B
215941749 | 3.79 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *97CTN1002122A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.9 | 43500 | R-454B
213203934 | 1.49 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0451412A* | 17900 | 16.5 | 11 | 8.5 | 18700 | 15300 | 81.82% | 2.35 | 15400 | R-410A
213203977 | 1.45 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *95ESN0261410A* | 17400 | 15.9 | 10.8 | 8.5 | 18600 | 13900 | 74.73% | 2.26 | 14300 | R-410A
215654391 | 1.8 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PE(S,T)274 |  | 21600 | 15.2 | 9.8 | 8.5 | 26200 | 20200 | 77.1% | 2.71 | 19100 | R-410A
216955371 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C100M5PDB | 32200 | 16.5 | 12 | 8.1 | 29000 | 21000 | 72.41% | 2.95 | 20400 | R-454B
216955396 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B040U3VSB | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.95 | 20200 | R-454B
216956809 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | L9X1B070U4VSA | 32400 | 16 | 11.7 | 8.1 | 28600 | 20800 | 72.73% | 2.91 | 20200 | R-454B
216956811 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | S9X1B060D3PSB | 32800 | 16 | 12 | 8.1 | 29400 | 20800 | 70.75% | 2.93 | 20400 | R-454B
216957155 | 4.42 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X1D120M5PSC | 53000 | 15.5 | 11.7 | 8.1 | 50500 | 35600 | 70.5% | 2.9 | 34800 | R-454B
216957159 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X2C100M5PSC | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.82 | 35800 | R-454B
211176509 | 3.71 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | MCG60T(C,D)2M | GUH97M090C3M | 44500 | 15.3 | 12.4 | 8.2 | 45000 | 32000 | 71.11% | 2.86 | 13800 | R-410A
213204387 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0451412A* | 23800 | 16.5 | 10.4 | 8.5 | 26000 | 26000 | 100% | 2.76 | 25200 | R-410A
213205038 | 1.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0801716A* | 22800 | 16.8 | 10.2 | 8.4 | 25600 | 19900 | 77.73% | 2.96 | 18700 | R-410A
216955402 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060U4PSC | 32000 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.91 | 20200 | R-454B
216955420 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1B060U4PSB | 31600 | 16 | 11.7 | 8.1 | 28600 | 20600 | 72.03% | 2.91 | 20000 | R-454B
216955242 | 2.53 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2A040M3PDB | 30400 | 16 | 11.7 | 8.1 | 27400 | 19900 | 72.63% | 2.8 | 19300 | R-454B
216955386 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2C080M5PSC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216955403 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060U4VSB | 31800 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.93 | 20200 | R-454B
216955404 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B080D4PSC | 31400 | 16 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
216955419 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1B060D3PSB | 31600 | 16 | 12 | 8.1 | 29200 | 21000 | 71.92% | 2.83 | 20400 | R-454B
215676265 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CMN1202422B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
216957163 | 4.42 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X2D120M5PTC | 53000 | 15.5 | 11.7 | 8.1 | 50500 | 35600 | 70.5% | 2.9 | 34800 | R-454B
214728487 | 1.34 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24HDN1-M15G | RE(S,T)244 |  | 16100 | 15.2 | 10 | 8.1 | 17700 | 12900 | 72.88% | 1.81 | 15000 | R-410A
216955365 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C080M5PCB | 32000 | 16.5 | 12 | 8.1 | 29000 | 20600 | 71.03% | 2.95 | 20200 | R-454B
216955383 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2B060M4PTC | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
216955474 | 2.53 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | L8V1A060U3VSB | 30400 | 16 | 11.7 | 8.1 | 27400 | 20000 | 72.99% | 2.84 | 19500 | R-454B
216955375 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1B080M4PTC | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.94 | 20200 | R-454B
216955356 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B060M4PCB | 31800 | 16 | 12 | 8.1 | 28400 | 20600 | 72.54% | 2.91 | 20000 | R-454B
216955358 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B060M4PDB | 31800 | 16 | 12 | 8.1 | 28400 | 20600 | 72.54% | 2.91 | 20000 | R-454B
216955390 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2D120M5PSC | 32200 | 16.5 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.91 | 20000 | R-454B
216955432 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2C080U5PSB | 32000 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.95 | 20200 | R-454B
216955475 | 2.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1A040M3PSC | 30600 | 16 | 12 | 8.1 | 27800 | 20200 | 72.66% | 2.82 | 19700 | R-454B
213205077 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN1002122A* | 23400 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213612208 | 3.75 | Yes | No | GUARDIAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RHP15048B21 | L(E,G)M60A4 |  | 45000 | 15.5 | 11.8 | 8.1 | 45500 | 37800 | 83.08% | 3.7 | 34600 | R-410A
215678235 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CSU0601716B* | 24000 | 17 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19700 | R-454B
215678335 | 1.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *97CTN0801716A* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
213204443 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0702116A* | 23800 | 17 | 10.5 | 8.1 | 26200 | 27000 | 103.1% | 2.69 | 25800 | R-410A
213204813 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)1102120A* | 23800 | 16.3 | 10.2 | 8.4 | 26200 | 20200 | 77.1% | 2.97 | 19100 | R-410A
213204879 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN0801716A* | 23600 | 17.5 | 10.3 | 8.5 | 25600 | 20000 | 78.12% | 3 | 18800 | R-410A
213204918 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0401410A* | 23800 | 15.2 | 10 | 8.5 | 26600 | 20600 | 77.44% | 2.84 | 19400 | R-410A
213204963 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *95ESN0601714A* | 23800 | 16.5 | 10.3 | 8.5 | 26000 | 20200 | 77.69% | 2.96 | 19000 | R-410A
213204972 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0801716A* | 23600 | 15.8 | 9.8 | 8.4 | 26200 | 20200 | 77.1% | 2.92 | 19100 | R-410A
213205018 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0601412A* | 23600 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213205045 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0801716A* | 23000 | 16.9 | 10.3 | 8.5 | 25600 | 19900 | 77.73% | 2.98 | 18700 | R-410A
216955376 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1C080M5PSC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216955377 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1C080M5PTC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216955429 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2B080D4PSB | 31200 | 15.5 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
215676315 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL1102120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215676345 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CMN0602120B* | 47500 | 18.5 | 10 | 9 | 50000 | 37000 | 74% | 1.98 | 46500 | R-454B
215676395 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *96CTN1202422B* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216957158 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X2C080M5PTC | 51500 | 15.5 | 11 | 8.1 | 50000 | 35400 | 70.8% | 2.85 | 34600 | R-454B
213752668 | 1.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M17**16 | 22600 | 17.4 | 10.3 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213752699 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M21**16 | 22800 | 17.4 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
213752766 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*B090V21**20 | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.92 | 19100 | R-410A
213752817 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC2E080M17**16 | 23200 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.86 | 19100 | R-410A
213752819 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2E080M17**16 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.86 | 19100 | R-410A
213752551 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SP6A100V21**20 | 23600 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213752566 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6C040V14**10 | 22600 | 15.4 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213204427 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0701712A* | 23400 | 17 | 10 | 8.5 | 25600 | 25200 | 98.44% | 2.55 | 24600 | R-410A
213204870 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92ESN0601714A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213204904 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92ESN1002120A* | 23800 | 17 | 10.3 | 8.5 | 26000 | 20200 | 77.69% | 3 | 19000 | R-410A
213204911 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *95ESN0261410A* | 23400 | 16.5 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
213205052 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0802120A* | 23400 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213205070 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN1002120A* | 22800 | 16.9 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.96 | 18600 | R-410A
216955374 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1B080M4PSC | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.94 | 20200 | R-454B
216955381 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1D120M5PTC | 32200 | 16.5 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.91 | 20000 | R-454B
216955399 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060U3VSA | 31800 | 16 | 11 | 8.1 | 29000 | 20400 | 70.34% | 2.9 | 20000 | R-454B
216955406 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B080U4PSC | 31600 | 16 | 11.7 | 8.1 | 28400 | 20600 | 72.54% | 2.92 | 20000 | R-454B
216955408 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C080U5PSC | 32200 | 16.5 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.94 | 20000 | R-454B
216957152 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X1C100M5PSC | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.82 | 35800 | R-454B
213204000 | 1.47 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *96VTN0401712A* | 17600 | 15.5 | 10.5 | 8.5 | 18500 | 13700 | 74.05% | 2.27 | 14200 | R-410A
213204107 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80ES(N,L)0902120A* | 23800 | 16 | 9.5 | 8.5 | 25800 | 27400 | 106.2% | 2.68 | 25400 | R-410A
216957135 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | L8V1C100U5VSB | 52500 | 15.5 | 11.7 | 8.1 | 50000 | 35000 | 70% | 3.06 | 34400 | R-454B
216957151 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X1C080M5PTC | 51500 | 15.5 | 11 | 8.1 | 50000 | 35400 | 70.8% | 2.85 | 34600 | R-454B
216955431 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2B080U4PSB | 31800 | 16 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.93 | 20000 | R-454B
216956810 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | S9X1B040D3PSB | 33000 | 16 | 12 | 8.1 | 29800 | 21000 | 70.47% | 2.92 | 20600 | R-454B
216956785 | 2.72 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 |  | 32600 | 15.5 | 11 | 8.1 | 29000 | 21000 | 72.41% | 2.91 | 20400 | R-454B
216955392 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2D120M5PTC | 32200 | 16.5 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.91 | 20000 | R-454B
216955412 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100D5PSC | 31800 | 16.5 | 12 | 8.1 | 29200 | 20600 | 70.55% | 2.92 | 20200 | R-454B
216955478 | 2.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2A040M3PTC | 30600 | 16 | 12 | 8.1 | 27800 | 20200 | 72.66% | 2.82 | 19700 | R-454B
216956815 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | S9X2B060D3PSB | 32800 | 16 | 12 | 8.1 | 29400 | 20800 | 70.75% | 2.93 | 20400 | R-454B
216955479 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B040U3PSB | 31600 | 16 | 11.7 | 8.1 | 28600 | 20200 | 70.63% | 2.91 | 19900 | R-454B
213753763 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC2E080M21**20 | 35000 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
216955380 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1D120M5PSC | 32200 | 16.5 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.91 | 20000 | R-454B
213205072 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN1002120A* | 23000 | 17 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.96 | 18600 | R-410A
213203991 | 1.43 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *95ESN0601412A* | 17200 | 16.4 | 10.8 | 8.5 | 18300 | 14100 | 77.05% | 2.33 | 14300 | R-410A
213204138 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92ESN0401712A* | 23800 | 15.2 | 9 | 8.1 | 25200 | 28600 | 113.5% | 2.64 | 26000 | R-410A
213204140 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92ESN0401712A* | 23800 | 15.2 | 9 | 8.1 | 25200 | 27200 | 107.9% | 2.63 | 25200 | R-410A
213204323 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0601714A* | 23600 | 15.5 | 9 | 8.1 | 25200 | 26000 | 103.2% | 2.76 | 25200 | R-410A
213204356 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0802120A* | 23800 | 16 | 9 | 8.1 | 24800 | 25800 | 104% | 2.76 | 25000 | R-410A
213204373 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN1002122A* | 23600 | 16.5 | 10 | 8.1 | 24800 | 27000 | 108.9% | 2.69 | 25800 | R-410A
213752852 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC6A026M14**10 | 23200 | 16.5 | 10 | 8.5 | 27000 | 20600 | 76.3% | 2.86 | 19500 | R-410A
213821554 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *96VTN1002122B* | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
216955382 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2B060M4PSC | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
216955398 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060D3VSB | 31400 | 16 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
216955414 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100U4VSB | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.9 | 20000 | R-454B
216955416 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100U5VSB | 32200 | 16.5 | 12 | 8.5 | 29000 | 20400 | 70.34% | 2.9 | 20000 | R-454B
216955423 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1C080U5PSB | 32000 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.95 | 20200 | R-454B
216955480 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B040U3VSA | 31600 | 16 | 11.7 | 8.1 | 28600 | 20200 | 70.63% | 2.91 | 19900 | R-454B
215654389 | 1.85 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | PE(S,T)284 |  | 22200 | 15.2 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.78 | 20000 | R-410A
213204093 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80ES(N,L)0901714A* | 23800 | 16 | 9 | 8.1 | 25600 | 27400 | 107% | 2.61 | 25400 | R-410A
216955487 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1D120U5PSB | 32000 | 16 | 12 | 8.1 | 28200 | 20400 | 72.34% | 3.03 | 19900 | R-454B
215654403 | 1.8 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PE(S,T)274 |  | 21600 | 15.2 | 9.8 | 8.5 | 26200 | 20200 | 77.1% | 2.71 | 19100 | R-410A
216957157 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X2C080M5PSC | 51500 | 15.5 | 11 | 8.1 | 50000 | 35400 | 70.8% | 2.85 | 34600 | R-454B
213204086 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80ES(N,L)0901714A* | 23800 | 16 | 9.5 | 8.1 | 25600 | 27400 | 107% | 2.61 | 25400 | R-410A
213204159 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92ESN0601714A* | 23800 | 16 | 9 | 8.1 | 25400 | 28000 | 110.2% | 2.79 | 25200 | R-410A
213612886 | 3.75 | Yes | No | GUARDIAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RHP15048B21 | L(E,G)M60A6 |  | 45000 | 15.5 | 11.8 | 8.1 | 45500 | 37800 | 83.08% | 3.7 | 34600 | R-410A
216957277 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5060A1 | 5PXFH009AZ3 | S9X1D120U5PSB | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.81 | 35800 | R-454B
216957279 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5060A1 | 5PXFH009AZ3 | S9X2D120U5PSB | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.81 | 35800 | R-454B
216955357 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B060M4PDA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
216955366 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C080M5PDA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
213204277 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *95ESN0802120A* | 23800 | 15.5 | 9.5 | 8.5 | 26000 | 25800 | 99.23% | 2.76 | 25000 | R-410A
213204311 | 1.88 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0601412A* | 22600 | 15.8 | 9.3 | 8.1 | 24400 | 24800 | 101.6% | 2.5 | 24000 | R-410A
213204359 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN1002120A* | 23600 | 16 | 9 | 8.1 | 25000 | 26000 | 104% | 2.73 | 25200 | R-410A
213204361 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN1002120A* | 23600 | 16 | 9 | 8.1 | 25000 | 26000 | 104% | 2.74 | 25200 | R-410A
213204370 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN1002122A* | 23600 | 16.5 | 10 | 8.1 | 24800 | 26800 | 108.1% | 2.7 | 25600 | R-410A
215439659 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96SC0805CUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
214238978 | 2.67 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | END4X42L17**+WALLCON | *80CTL0701716B* | 32000 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.9 | 31600 | R-410A
215439761 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A*+MBVK16CP1X00A* |  | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
213204417 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0701712A* | 23000 | 17 | 10 | 8.5 | 25600 | 25200 | 98.44% | 2.56 | 24600 | R-410A
213204453 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0901714A* | 23400 | 16.8 | 10.2 | 8.4 | 25800 | 26200 | 101.6% | 2.75 | 25200 | R-410A
213204860 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN0601714A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
214813279 | 1.85 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | RE(S,T)304 |  | 22200 | 16 | 10 | 8.5 | 26200 | 23400 | 89.31% | 1.92 | 19200 | R-410A
213203951 | 1.42 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *92ESN0401410A* | 17000 | 15.3 | 10.2 | 8.5 | 18400 | 13800 | 75% | 2.28 | 14200 | R-410A
213204862 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92ESN0601714A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213204928 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *95ESN0401410A* | 23800 | 15.2 | 10 | 8.5 | 26600 | 20600 | 77.44% | 2.84 | 19400 | R-410A
213204937 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0401712A* | 23800 | 15.2 | 9 | 8.5 | 26400 | 20400 | 77.27% | 2.82 | 19300 | R-410A
213204284 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *95ESN0802120A* | 23800 | 15.5 | 9.5 | 8.5 | 26000 | 26000 | 100% | 2.77 | 25200 | R-410A
213204318 | 1.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0601412A* | 22800 | 15.9 | 9.3 | 8.1 | 24400 | 27000 | 110.7% | 2.7 | 25800 | R-410A
216955351 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | *UHMB080CCV3 | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
216955367 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C080M5PDB | 32000 | 16.5 | 12 | 8.1 | 29000 | 20600 | 71.03% | 2.95 | 20200 | R-454B
213205028 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0601714A* | 23600 | 16.5 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.91 | 19100 | R-410A
215654401 | 1.85 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | PE(S,T)284 |  | 22200 | 15.2 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.78 | 20000 | R-410A
215654390 | 1.85 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | RE(S,T)244 |  | 22200 | 15.2 | 9 | 8.5 | 26200 | 24000 | 91.6% | 2.56 | 21200 | R-410A
213752985 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C040V14**10 | 23000 | 16 | 9.5 | 8.5 | 27000 | 20600 | 76.3% | 2.85 | 19500 | R-410A
214595160 | 1.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36A4 |  | 22800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
216955384 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2B080M4PSC | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.94 | 20200 | R-454B
216955401 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060U4PSB | 31600 | 16 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
215676215 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *80CTL1102120B* | 47000 | 19 | 10 | 9 | 50000 | 36200 | 72.4% | 2 | 45500 | R-454B
215676365 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CMN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216955360 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B080M4PCB | 31800 | 16 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.93 | 20000 | R-454B
216955362 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B080M4PDB | 31800 | 16 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.93 | 20000 | R-454B
216955379 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1C100M5PTC | 32000 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.95 | 20200 | R-454B
216955393 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B040D3PSC | 31400 | 16 | 11.7 | 8.1 | 29200 | 21000 | 71.92% | 2.79 | 20400 | R-454B
216955394 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B040D3VSB | 31400 | 16 | 11.7 | 8.1 | 29200 | 21000 | 71.92% | 2.79 | 20400 | R-454B
216955395 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B040U3PSC | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.95 | 20200 | R-454B
216955410 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C080U5VSB | 32200 | 16.5 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.94 | 20000 | R-454B
216955427 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2B060D3PSB | 31600 | 16 | 12 | 8.1 | 29200 | 21000 | 71.92% | 2.83 | 20400 | R-454B
216955476 | 2.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1A040M3PTC | 30600 | 16 | 12 | 8.1 | 27800 | 20200 | 72.66% | 2.82 | 19700 | R-454B
216956816 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | S9X2B080D4PSB | 32400 | 16 | 12 | 8.1 | 29200 | 21000 | 71.92% | 2.9 | 20400 | R-454B
216957255 | 4.29 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5060A1 | 5PXFH009AZ3 | S8X1C100M5PTC | 51500 | 15.5 | 9.8 | 8.1 | 50000 | 35400 | 70.8% | 2.7 | 34600 | R-454B
213204394 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0451712A* | 23800 | 17 | 10 | 8.5 | 26200 | 24800 | 94.66% | 2.54 | 24400 | R-410A
213204408 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0701412A* | 23800 | 17 | 10 | 8.5 | 26200 | 26400 | 100.8% | 2.81 | 25400 | R-410A
216732984 | 1.85 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2417AM* | 926SB48080V17*** | 22200 | 16 | 10.5 | 8.5 | 21200 | 19200 | 90.57% | 1.96 | 18100 | R-454B
213752598 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C080V21**20 | 23800 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213205986 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2D040E17**12 | 23800 | 15.2 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.88 | 20000 | R-410A
213206104 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC5B060E17**14 | 23600 | 15.3 | 9.3 | 8.4 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
216955373 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X1B060M4PTC | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
213204077 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80ES(N,L)0702116A* | 23800 | 16 | 9 | 8.1 | 25400 | 27800 | 109.4% | 2.58 | 25600 | R-410A
213204143 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92ESN0401712A* | 23800 | 15.2 | 9 | 8.1 | 25200 | 27000 | 107.1% | 2.63 | 25000 | R-410A
213204250 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *95ESN0601714A* | 23400 | 15.3 | 9.3 | 8.4 | 25400 | 27600 | 108.7% | 2.7 | 25000 | R-410A
216955405 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B080D4VSB | 31400 | 16 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
215654405 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | RE(S,T)304 |  | 22200 | 15.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.76 | 19100 | R-410A
213206187 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59TP6B080V17**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.88 | 20200 | R-410A
213206270 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A070E17**12 | 23400 | 17 | 10 | 8.1 | 25600 | 20000 | 78.12% | 2.87 | 18800 | R-410A
213206369 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*A090V17**16 | 23800 | 17 | 10 | 8.1 | 26000 | 20200 | 77.69% | 2.82 | 19000 | R-410A
213206371 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*A090V17**16 | 23800 | 17 | 10 | 8.1 | 26000 | 20200 | 77.69% | 2.82 | 19000 | R-410A
213206453 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2D080E17**16 | 23600 | 17.5 | 10.3 | 8.1 | 25600 | 20000 | 78.12% | 2.86 | 18800 | R-410A
216733252 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 83*SB36040M17*** | 23000 | 17 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
213204851 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92ESN0601412A* | 23200 | 17 | 10 | 8.5 | 25600 | 20000 | 78.12% | 2.87 | 18800 | R-410A
213204855 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN0601412A* | 23400 | 17 | 10 | 8.5 | 25600 | 20000 | 78.12% | 2.87 | 18800 | R-410A
213204935 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *95ESN0401712A* | 23800 | 15.2 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.82 | 19300 | R-410A
213204946 | 1.98 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *95ESN0601412A* | 23800 | 16 | 9.9 | 8.5 | 26000 | 20400 | 78.46% | 2.97 | 19100 | R-410A
213204960 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0601714A* | 23600 | 16.3 | 10.3 | 8.4 | 26000 | 20200 | 77.69% | 2.94 | 19000 | R-410A
215678215 | 1.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *97CTN0801716A* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215678265 | 1.93 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CSU0401712B* | 23200 | 17 | 10 | 8.5 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214505260 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*96VC0804CNA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
216960334 | 1.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A3J+TDR | S9V2B080U4PSC+LRP | 19000 | 20.5 | 11.2 | 9 | 22200 | 26200 | 118% | 2.78 | 21400 | R-454B
213296457 | 2 | Yes | No | SAMSUNG | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AC024BXUPCH | MSVT25***8U4DHX |  | 24000 | 16.5 | 10.1 | 8.1 | 25000 | 25600 | 102.4% | 1.8 | 30800 | R-410A
213613579 | 1.98 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24D4 |  | 23800 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
216957262 | 4.29 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5060A1 | 5PXFH009AZ3 | S8X2C100M5PTC | 51500 | 15.5 | 9.8 | 8.1 | 50000 | 35400 | 70.8% | 2.7 | 34600 | R-454B
215654404 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PE(S,T)284 |  | 22200 | 15.2 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.73 | 19100 | R-410A
216956881 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH009AZ3 | L8V1A040U3VSB | 31400 | 16 | 12 | 8.1 | 27400 | 20000 | 72.99% | 2.91 | 19500 | R-454B
213753668 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B070M21**16 | 35000 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.6 | 29400 | R-410A
213753671 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M17**14 | 35200 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
213753735 | 2.83 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58TP*B090V21**20 | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
213753804 | 2.8 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC6A100M21**22 | 33600 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.71 | 29000 | R-410A
213753836 | 2.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SP6A080V21**20 | 35400 | 16 | 9.5 | 8.1 | 39500 | 31600 | 80% | 2.51 | 29400 | R-410A
213753386 | 2.38 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)36B34+TDR | 59SC2E080M21**20 | 28600 | 15.3 | 8.8 | 8.4 | 33400 | 23800 | 71.26% | 2.76 | 23200 | R-410A
213613594 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M244+TDR |  | 23000 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.92 | 19000 | R-410A
213753829 | 2.8 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SP6A080V17**16 | 33600 | 15.9 | 9.8 | 8.1 | 38500 | 31400 | 81.56% | 2.71 | 29000 | R-410A
213753880 | 2.8 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59TP6C120V24**22 | 33600 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
213204876 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92ESN0801716A* | 23800 | 17.5 | 10.4 | 8.5 | 25600 | 20000 | 78.12% | 3 | 18800 | R-410A
213821218 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)1102120A* | 23400 | 17.5 | 10.3 | 8.5 | 25600 | 20000 | 78.12% | 3.01 | 18800 | R-410A
213821232 | 1.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80VTL0902120B* | 22800 | 16.7 | 10 | 8.4 | 25600 | 20200 | 78.91% | 2.96 | 18900 | R-410A
213821234 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80VTL0902120B* | 23200 | 16.9 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3.01 | 18900 | R-410A
213821250 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92MSN0601412A* | 23800 | 17 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.94 | 19200 | R-410A
215418106 | 3.5 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-4860A | HG86948+TD |  | 42000 | 15.2 | 11.7 | 8.6 | 41000 | 32000 | 78.05% | 1.9 | 36000 | R-410A
213821259 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92MSN0801716A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821277 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96MSN0401410A* | 22400 | 16.3 | 9.8 | 8.4 | 25400 | 20200 | 79.53% | 2.95 | 18800 | R-410A
213204895 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN1002120A* | 23600 | 16.8 | 10.2 | 8.4 | 26000 | 20200 | 77.69% | 2.98 | 19000 | R-410A
213204986 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *95ESN0802120A* | 23800 | 16.5 | 10.5 | 8.5 | 26600 | 20400 | 76.69% | 2.89 | 19300 | R-410A
216797134 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | L8V1B080U4VSB+LRP | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
216055335 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055352 | 3.46 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE130D20MP11 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35200 | 76.52% | 2 | 35400 | R-454B
215677208 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *96CTN1202422B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.1 | 55500 | R-454B
213821587 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0902420A* | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821671 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96VTN1002122B* | 35200 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213205536 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0902120A* | 35400 | 16 | 10 | 8.1 | 39500 | 31600 | 80% | 2.52 | 29400 | R-410A
213205618 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92ESN1202420A* | 35200 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
216955388 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2C100M5PSC | 32000 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.95 | 20200 | R-454B
216955472 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | *UHMC100CCV4 | 32000 | 16.5 | 12 | 8.1 | 28400 | 20200 | 71.13% | 2.88 | 19900 | R-454B
213204176 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92ESN0801716A* | 23800 | 16.5 | 9 | 8.1 | 25400 | 28600 | 112.6% | 2.61 | 26000 | R-410A
213204194 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92ESN1002120A* | 23800 | 16 | 9.5 | 8.5 | 26000 | 27400 | 105.4% | 2.68 | 25400 | R-410A
216957261 | 4.29 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5060A1 | 5PXFH009AZ3 | S8X2C100M5PSC | 51500 | 15.5 | 9.8 | 8.1 | 50000 | 35400 | 70.8% | 2.7 | 34600 | R-454B
216055369 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215399940 | 2.55 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR |  | 30600 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.56 | 27000 | R-454B
214093140 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.09 | 25800 | R-410A
214093141 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 45500 | 140.4% | 2.97 | 26200 | R-410A
214093142 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 46000 | 142% | 3.03 | 26400 | R-410A
214093143 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 45500 | 140.4% | 3 | 26200 | R-410A
214093126 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TP9C080C16MP13 | 31600 | 17.5 | 9.8 | 8.1 | 32400 | 44000 | 135.8% | 3.09 | 25400 | R-410A
213205082 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN1002122A* | 23600 | 17 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213205248 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *80ES(N,L)1102420A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.7 | 23400 | R-410A
213205318 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *92ESN0801716A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.67 | 23400 | R-410A
213753610 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 59TP6C100V21**20 | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
216055003 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | LP9C080C16MP13 | 31200 | 18 | 11 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
214093024 | 2.8 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 32400 | 46500 | 143.5% | 3.12 | 26800 | R-410A
214093026 | 2.8 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.2 | 32400 | 46500 | 143.5% | 3.17 | 26800 | R-410A
214093042 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.04 | 26000 | R-410A
214093106 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.3 | 32400 | 45000 | 138.9% | 3.11 | 26000 | R-410A
214093109 | 2.77 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.3 | 32400 | 45500 | 140.4% | 3.15 | 26200 | R-410A
214093124 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 46500 | 143.5% | 3.12 | 26600 | R-410A
214092924 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | LP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 46000 | 142% | 3.06 | 26400 | R-410A
214092940 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | LPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 45500 | 140.4% | 2.97 | 26200 | R-410A
214239178 | 2.68 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D,W)4X48L21**+WALLCON | *80CTL0701716B* | 32200 | 17 | 11.5 | 8.1 | 32800 | 24800 | 75.61% | 1.94 | 31600 | R-410A
216055281 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055333 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
216055347 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
213206204 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6B100V21**20 | 23600 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.98 | 20000 | R-410A
216957150 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X1C080M5PSC | 51500 | 15.5 | 11 | 8.1 | 50000 | 35400 | 70.8% | 2.85 | 34600 | R-454B
216957181 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S9X2C080U5PSB | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.85 | 35800 | R-454B
214264156 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214320589 | 2.67 | No | No | Frigidaire | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GXH24-36MSK4DH | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
216055349 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055358 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLV120C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055365 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055390 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055413 | 3.5 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES100C16SMPS1 | 42000 | 18 | 10.5 | 8.5 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
215031218 | 2.63 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CH48B34+TDR | D*80VC1005C*A* | 31600 | 19 | 11.9 | 8.1 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213204253 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *95ESN0601714A* | 23200 | 15.2 | 9.2 | 8.3 | 25200 | 27600 | 109.5% | 2.7 | 25000 | R-410A
216957162 | 4.42 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X2D120M5PSC | 53000 | 15.5 | 11.7 | 8.1 | 50500 | 35600 | 70.5% | 2.9 | 34800 | R-454B
213161300 | 1.92 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P149+AEFE4B* |  | 23000 | 21 | 13 | 8.55 | 20600 | 15700 | 76.21% | 2.24 | 13200 | R-410A
216764351 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S8X1B060M4PSC | 32200 | 17.1 | 11.7 | 8.7 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216764383 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | L8V1B080U4VSB | 33000 | 17.1 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216764451 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | S8X1D120M5PSC | 44000 | 17.1 | 12 | 9 | 44500 | 32400 | 72.81% | 2.2 | 29400 | R-454B
216764460 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TEMCD06AV41+TDR |  | 44000 | 17.1 | 12.7 | 9 | 43500 | 31800 | 73.1% | 2.2 | 29000 | R-454B
216955352 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | L8V1B080U4VSB | 31800 | 16 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.94 | 20000 | R-454B
216955353 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | L9X1B070U4VSA | 31200 | 15.5 | 11.5 | 8.1 | 28400 | 20600 | 72.54% | 2.8 | 20000 | R-454B
216955368 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2C100M5PCA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
216955417 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1B040D3PSB | 31800 | 16 | 11.7 | 8.1 | 29600 | 21000 | 70.95% | 2.86 | 20600 | R-454B
215850239 | 2.6 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | CP9C080C16MP13 | 31200 | 18 | 11 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850392 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 31000 | 18 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
215678325 | 1.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *97CTN0601716A* | 23000 | 16.5 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
213821192 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0701716A* | 22400 | 17.2 | 10 | 8.4 | 25200 | 20000 | 79.37% | 2.98 | 18700 | R-410A
213821199 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0702116A* | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
214826419 | 2.77 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9Y080B12MP11 | 33200 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
213821178 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0451412A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821181 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0701412A* | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.9 | 19000 | R-410A
215850473 | 2.57 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080B12MP11 | 30800 | 18 | 10.5 | 8.1 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
215850542 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850576 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
215850693 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 40000 | 16.5 | 11.2 | 8.1 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
215850707 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TL8E100C20UH11 | 42000 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
215850758 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215677888 | 4.54 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0701716B* | 54500 | 18 | 9 | 8.5 | 58500 | 41500 | 70.94% | 1.92 | 50500 | R-454B
212594777 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DD12936 | A97USMV070B12 | 23800 | 20 | 13.5 | 8.45 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215678425 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *97CTN1002122A* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
213821242 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92MSN0401712A* | 23000 | 16 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
216957156 | 4.42 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X1D120M5PTC | 53000 | 15.5 | 11.7 | 8.1 | 50500 | 35600 | 70.5% | 2.9 | 34800 | R-454B
215654388 | 1.8 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | PE(S,T)274 |  | 21600 | 15.2 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.75 | 20000 | R-410A
216733895 | 1.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 82*SB36070V14*** | 22400 | 16.5 | 11 | 8.5 | 21000 | 18800 | 89.52% | 1.96 | 17600 | R-454B
212437571 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213203998 | 1.47 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *96VTN0401712A* | 17600 | 15.5 | 10 | 8.5 | 18500 | 13900 | 75.14% | 2.27 | 14300 | R-410A
213204399 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0451712A* | 23800 | 17 | 10 | 8.5 | 26200 | 24600 | 93.89% | 2.52 | 24200 | R-410A
213204415 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0701412A* | 23800 | 17 | 10 | 8.5 | 26200 | 25200 | 96.18% | 2.56 | 24600 | R-410A
213204834 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92ESN0401410A* | 23600 | 15.5 | 9.9 | 8.5 | 26000 | 20400 | 78.46% | 2.94 | 19100 | R-410A
213204932 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *95ESN0401712A* | 23800 | 15.2 | 9 | 8.5 | 26400 | 20400 | 77.27% | 2.82 | 19300 | R-410A
213204951 | 1.98 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *95ESN0601412A* | 23800 | 16 | 9.9 | 8.5 | 26000 | 20400 | 78.46% | 2.97 | 19100 | R-410A
213204965 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0801716A* | 23600 | 15.8 | 9.7 | 8.4 | 26200 | 20200 | 77.1% | 2.92 | 19100 | R-410A
213204967 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *95ESN0801716A* | 23400 | 15.7 | 9 | 8.3 | 26000 | 20200 | 77.69% | 2.89 | 19000 | R-410A
213204981 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *95ESN0802120A* | 23800 | 16.5 | 10.5 | 8.5 | 26600 | 20400 | 76.69% | 2.89 | 19300 | R-410A
213204984 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0802120A* | 23800 | 16.5 | 10.5 | 8.5 | 26600 | 20400 | 76.69% | 2.89 | 19300 | R-410A
213205001 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0401712A* | 23000 | 16 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213821246 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92MSN0601412A* | 23600 | 17 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.94 | 19200 | R-410A
213821248 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92MSN0601412A* | 23800 | 17 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.94 | 19200 | R-410A
213821296 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96MSN0802120A* | 22400 | 17.3 | 9.7 | 8.4 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213821315 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0601412B* | 23600 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213205060 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0802120A* | 23600 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
216733913 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 82*SB48090V17*** | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
215850306 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C16MP11 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215850675 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
215850355 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8V080C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850589 | 2.62 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES120C16SMPS1 | 31400 | 18 | 11 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
213205016 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0601412A* | 23200 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213205033 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0601714A* | 23800 | 16.5 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.91 | 19100 | R-410A
215850709 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
215850840 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM8V120C20MP12 | 41500 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215850909 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9E100C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
215850974 | 3.29 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080C16MP11 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
215851244 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215851325 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES080C16SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
214802752 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0504A17UHU | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.63 | 21000 | R-410A
214802754 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0704A17UHU | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.62 | 21000 | R-410A
213821206 | 1.88 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0902116A* | 22600 | 17.3 | 10.2 | 8.4 | 25200 | 19900 | 78.97% | 2.96 | 18600 | R-410A
213821238 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80VTL1102122B* | 23000 | 17.5 | 10.3 | 8.5 | 25400 | 20200 | 79.53% | 2.99 | 18800 | R-410A
213821355 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0701412A* | 29000 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
213821287 | 1.88 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96MSN0601412A* | 22600 | 16.8 | 9.8 | 8.4 | 25200 | 20000 | 79.37% | 2.92 | 18700 | R-410A
213821289 | 1.9 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96MSN0601412A* | 22800 | 17 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213821306 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0401712B* | 23000 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213821323 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0801716B* | 23600 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.91 | 19000 | R-410A
214802749 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)30B34+TDR | R801V0504A17UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.63 | 21000 | R-410A
214802924 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D44+TDR | R801V1005A21UHN | 45500 | 15.5 | 10 | 8.4 | 46000 | 33800 | 73.48% | 3.1 | 36000 | R-410A
214802931 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60B44+TDR | R801V1005A21UHS | 45000 | 15.6 | 10.1 | 8.2 | 45500 | 33800 | 74.29% | 3.06 | 36400 | R-410A
216955490 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X2D120U5PSB | 32000 | 16 | 12 | 8.1 | 28200 | 20400 | 72.34% | 3.03 | 19900 | R-454B
213204420 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0701712A* | 23000 | 17 | 10 | 8.5 | 25600 | 26800 | 104.7% | 2.84 | 25600 | R-410A
214092958 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TL8E080C16UH11 | 31600 | 17.5 | 9.8 | 8.1 | 32400 | 44500 | 137.3% | 3.15 | 25600 | R-410A
214092992 | 2.77 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.3 | 32400 | 45500 | 140.4% | 3.15 | 26200 | R-410A
214093008 | 2.67 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8V100C20MP12 | 32000 | 16.5 | 8.9 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25200 | R-410A
216055385 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C16SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216055404 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
216797170 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2C100U4VSB+LRP | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.8 | 51500 | R-454B
216055020 | 2.62 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 31400 | 18 | 10.5 | 8.5 | 31600 | 25600 | 81.01% | 2 | 28000 | R-454B
216055069 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y080C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216055102 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V080B12MP12 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055152 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLV100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
213204434 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0701716A* | 23800 | 16.5 | 10.4 | 8.5 | 26000 | 24800 | 95.38% | 2.55 | 24400 | R-410A
213204436 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0701716A* | 23800 | 16.3 | 10.3 | 8.4 | 26000 | 25200 | 96.92% | 2.52 | 24600 | R-410A
213204445 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0702116A* | 23800 | 17 | 10.5 | 8.1 | 26200 | 27000 | 103.1% | 2.74 | 25800 | R-410A
213204450 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0702116A* | 23800 | 17 | 10.5 | 8.1 | 26200 | 25600 | 97.71% | 2.54 | 24800 | R-410A
213204820 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)1102120A* | 23800 | 16.3 | 10.3 | 8.4 | 26200 | 20200 | 77.1% | 2.97 | 19100 | R-410A
213204886 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92ESN0802120A* | 23400 | 16.7 | 10 | 8.3 | 25800 | 20000 | 77.52% | 2.95 | 18900 | R-410A
213204902 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN1002120A* | 23600 | 16.9 | 10.3 | 8.4 | 26000 | 20200 | 77.69% | 2.98 | 19000 | R-410A
213204970 | 1.98 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *95ESN0801716A* | 23800 | 16 | 9.9 | 8.5 | 26200 | 20200 | 77.1% | 2.94 | 19100 | R-410A
213821337 | 1.88 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN1002122B* | 22600 | 17.2 | 10 | 8.4 | 25200 | 19900 | 78.97% | 2.94 | 18600 | R-410A
213821340 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN1002122B* | 23200 | 17.5 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
215676255 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CMN0802120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215676305 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL0902120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215676465 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0901716B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 1.98 | 46500 | R-454B
215676715 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0701716B* | 48500 | 19 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215676815 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN1002122B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
213206221 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6B100V21**22 | 23800 | 16.5 | 10 | 8.1 | 24800 | 22200 | 89.52% | 2.89 | 19800 | R-410A
216497872 | 1.72 | No | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24A34+TDR | R962V0603A17M4S | 20600 | 16.5 | 9.8 | 9 | 22400 | 16800 | 75% | 2.55 | 18900 | R-410A
213204977 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0802120A* | 23800 | 16.5 | 10.5 | 8.5 | 26600 | 20400 | 76.69% | 2.89 | 19300 | R-410A
213204979 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *95ESN0802120A* | 23800 | 16.5 | 10 | 8.5 | 26600 | 20400 | 76.69% | 2.89 | 19300 | R-410A
213203993 | 1.45 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *96VTN0401410A* | 17400 | 16 | 10.5 | 8.5 | 18300 | 13700 | 74.86% | 2.26 | 14200 | R-410A
213820985 | 1.48 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *80VTL0451412B* | 17700 | 16.5 | 11 | 8.5 | 17900 | 12900 | 72.07% | 2.61 | 12500 | R-410A
216955239 | 2.53 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2A040M3PCB | 30400 | 16 | 11.7 | 8.1 | 27400 | 19900 | 72.63% | 2.8 | 19300 | R-454B
216955348 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | *DHMB080CCV3 | 31400 | 16 | 11.7 | 8.1 | 29200 | 21000 | 71.92% | 2.79 | 20400 | R-454B
215654400 | 1.8 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | PE(S,T)274 |  | 21600 | 15.2 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.75 | 20000 | R-410A
216764555 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S8X2B060M4PSC | 23000 | 17.1 | 12.5 | 9 | 21600 | 17100 | 79.17% | 2 | 15200 | R-454B
214802892 | 3.67 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R801V0755A21DZ | 44000 | 15.4 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.02 | 36400 | R-410A
214802897 | 3.83 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60D34+TDR | R801V0755A21DZ | 46000 | 15.5 | 10.2 | 8.4 | 46000 | 34000 | 73.91% | 3.14 | 36400 | R-410A
214802901 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60B44+TDR | R801V0755A21UH | 45000 | 15.6 | 10.1 | 8.2 | 46000 | 34200 | 74.35% | 3.07 | 36800 | R-410A
214802917 | 3.71 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D34+TDR | R801V1005A21DZ | 44500 | 15.5 | 10 | 8.2 | 45500 | 33600 | 73.85% | 3.03 | 36000 | R-410A
216955484 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100U4VSA | 31400 | 16.5 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.88 | 19900 | R-454B
216955355 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8V2B060M4PCA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
216955389 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S8X2C100M5PTC | 32000 | 16.5 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.95 | 20200 | R-454B
216955400 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B060U3VSB | 32000 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.91 | 20200 | R-454B
216955407 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B080U4VSB | 31600 | 16 | 11.7 | 8.1 | 28400 | 20600 | 72.54% | 2.92 | 20000 | R-454B
216955421 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9X1B080D4PSB | 31200 | 15.5 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
216955482 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2B080U4VSA | 31800 | 16 | 11.7 | 8.1 | 28600 | 20200 | 70.63% | 2.91 | 19900 | R-454B
213821197 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0702116A* | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213821212 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0902120A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
215850639 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
213821308 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0401712B* | 23400 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213821324 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0801716B* | 23400 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.91 | 19000 | R-410A
213770606 | 2.03 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CAP**2517AL*+UI | 88*TB48070C17*** | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
213770626 | 2.02 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CAP**2517AL*+UI | 935CB48060C17*** | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2.02 | 20600 | R-410A
216054751 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | LP9C060B12MP13 | 21200 | 16.5 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054752 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | LP9C060B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054786 | 1.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E060A12MP11 | 20200 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
216054802 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E100B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054818 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8Y080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216054834 | 1.67 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060A10MP12 | 20000 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18400 | R-454B
216054835 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E060A10MP12 | 19500 | 16 | 10 | 9 | 23000 | 18100 | 78.7% | 2 | 18600 | R-454B
216955415 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | S9V2C100U5PSC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.9 | 20000 | R-454B
214802731 | 1.87 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24B34+TDR | R801V1004A17UHN | 22400 | 16 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 3.03 | 17000 | R-410A
214802740 | 1.9 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24C34+TDR | R801V1004A17UHS | 22800 | 16 | 12 | 8.4 | 23000 | 16300 | 70.87% | 3.07 | 17000 | R-410A
215849807 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL8E060A12UH11 | 20600 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18200 | R-454B
215850023 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9Y060B12MP11 | 22200 | 17 | 11.7 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
215850071 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850124 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TPLC080B12MP13 | 22200 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
215850158 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES080B12SMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
214802734 | 1.9 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)30B34+TDR | R801V1004A17UHN | 22800 | 16 | 12 | 8.4 | 23000 | 16300 | 70.87% | 3.07 | 17000 | R-410A
213296453 | 4.75 | No | No | SAMSUNG | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AC060BXUPCH | MSVT60***9U7YHX |  | 57000 | 17.5 | 8.5 | 9 | 52000 | 47500 | 91.35% | 1.82 | 53500 | R-410A
214802899 | 3.71 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D34+TDR | R801V0755A21UH | 44500 | 15.5 | 10 | 8.2 | 45500 | 34000 | 74.73% | 3.05 | 36600 | R-410A
214802831 | 3.33 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | D(A,C,E)60D34+TDR | R801V1005A21DZ | 40000 | 15.5 | 10.2 | 8.4 | 40500 | 28800 | 71.11% | 3.05 | 30000 | R-410A
214802827 | 3.25 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | D(A,C,E)48D34+TDR | R801V1005A21DZ | 39000 | 15.5 | 10 | 8.2 | 40000 | 28600 | 71.5% | 2.99 | 30000 | R-410A
215849821 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL9E060B12UH11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849940 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9E060A10MP12 | 20800 | 16.5 | 10.5 | 9 | 22800 | 18100 | 79.39% | 2 | 18600 | R-454B
215849956 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
216955470 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | 5PXFH005AZ3 | *UHMB080ACV3 | 31400 | 16 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.88 | 19900 | R-454B
215399939 | 1.88 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.69 | 18700 | R-454B
215849867 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM8E100B12MP11 | 22400 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849919 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E026A08MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 17600 | 77.19% | 2 | 17800 | R-454B
214802729 | 1.83 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R801V1004A17UHN | 22000 | 16.3 | 11.8 | 8.1 | 22800 | 16200 | 71.05% | 2.96 | 16900 | R-410A
216054849 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E080B12MP12 | 22600 | 17 | 11.7 | 8.5 | 22600 | 18700 | 82.74% | 2 | 18800 | R-454B
216054883 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y080B12MP11 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18600 | R-454B
216054884 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9Y080B12MP11 | 22000 | 17 | 11.7 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18500 | R-454B
216054933 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES040A12SMPS1 | 21000 | 18 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216054985 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES060B12SMPS1 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18600 | 81.58% | 2 | 18700 | R-454B
214813278 | 1.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | RE(S,T)244 |  | 22200 | 16 | 9.8 | 8.2 | 27200 | 23400 | 86.03% | 1.92 | 19200 | R-410A
216497871 | 1.72 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24A34+TDR | R962V0403A17M4S | 20600 | 16.5 | 11 | 9 | 22400 | 16800 | 75% | 2.55 | 18900 | R-410A
215654402 | 1.85 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | RE(S,T)244 |  | 22200 | 15.2 | 9 | 8.5 | 26200 | 24000 | 91.6% | 2.56 | 21200 | R-410A
213821382 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0902116A* | 29000 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213821229 | 1.88 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80VTL0701716B* | 22600 | 17.4 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213821231 | 1.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80VTL0902120B* | 23000 | 16.8 | 10.2 | 8.4 | 25600 | 20200 | 78.91% | 2.99 | 18900 | R-410A
213296456 | 3 | Yes | No | SAMSUNG | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AC036BXUPCH | MSVT36***8U4YHX |  | 36000 | 18.5 | 10.5 | 8.4 | 33600 | 34400 | 102.4% | 1.92 | 40500 | R-410A
216957254 | 4.29 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5060A1 | 5PXFH009AZ3 | S8X1C100M5PSC | 51500 | 15.5 | 9.8 | 8.1 | 50000 | 35400 | 70.8% | 2.7 | 34600 | R-454B
213821183 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0701412A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.9 | 19000 | R-410A
213821383 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0902116A* | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213821187 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0701712A* | 23200 | 17.5 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.9 | 19000 | R-410A
213821205 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0901714A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821185 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0701412A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.9 | 19000 | R-410A
213821190 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0701712A* | 23600 | 17.5 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.9 | 19000 | R-410A
216497875 | 1.72 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24A34+TDR | R98MV0703A17UPS | 20600 | 16.5 | 11 | 9 | 22400 | 16800 | 75% | 2.55 | 18900 | R-410A
216797160 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2B080U4PSC+LRP | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
213821219 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)1102120A* | 23200 | 17.4 | 10.3 | 8.5 | 25600 | 20000 | 78.12% | 3.01 | 18800 | R-410A
213821244 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92MSN0401712A* | 23200 | 16 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
213821194 | 1.88 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0701716A* | 22600 | 17.4 | 10.3 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213821208 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0902116A* | 23000 | 17.5 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
213821210 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0902116A* | 23000 | 17.5 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
213821217 | 1.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)1102120A* | 22800 | 17.2 | 10 | 8.4 | 25600 | 20000 | 78.12% | 2.96 | 18800 | R-410A
213821233 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80VTL0902120B* | 23400 | 17 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3.01 | 18900 | R-410A
215869107 | 2.65 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X36A1 | 5TXCC005AS3 | S9V2C080U5VSB+LRP | 31800 | 18.1 | 10 | 8.5 | 32800 | 25400 | 77.44% | 2.1 | 31000 | R-454B
211176466 | 3.71 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | MCG60T(C,D)2M | GUH96T090C3M | 44500 | 15.3 | 12.4 | 8.2 | 45000 | 32000 | 71.11% | 2.86 | 13500 | R-410A
211176427 | 3.75 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | (M,V)CG60P(C,D)1M+TXV | GUH96C110C5M | 45000 | 15.3 | 12.3 | 8.1 | 45000 | 31600 | 70.22% | 2.76 | 13700 | R-410A
216957153 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S8X1C100M5PTC | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.82 | 35800 | R-454B
215850176 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z8ES100B12SMPS1 | 20800 | 18.9 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
215850185 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ET080B12LMPS1 | 22200 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
216957178 | 4.38 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | 5PXFH009AZ3 | S9X1C080U5PSB | 52500 | 15.5 | 9.8 | 8.1 | 52000 | 36400 | 70% | 2.85 | 35800 | R-454B
213821249 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92MSN0601412A* | 23800 | 17 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.94 | 19200 | R-410A
213821267 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92MSN1002120A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.93 | 19100 | R-410A
213821269 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92MSN1002120A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.93 | 19100 | R-410A
213821274 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96MSN0261410A* | 23200 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213821301 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0401410B* | 23000 | 16 | 10 | 8.5 | 26200 | 20400 | 77.86% | 2.85 | 19200 | R-410A
213821333 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN1002120B* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821335 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN1002120B* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821186 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0701712A* | 23200 | 17.5 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.9 | 19000 | R-410A
213821189 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0701712A* | 23400 | 17.5 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.9 | 19000 | R-410A
213821247 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92MSN0601412A* | 23600 | 17 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.94 | 19200 | R-410A
213821265 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92MSN0802120A* | 23400 | 17.5 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3 | 18900 | R-410A
213821028 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0701712A* | 23600 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
213821080 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80VTL1102122B* | 23800 | 16 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213821097 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92MSN0801716A* | 23400 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821112 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96MSN0261410A* | 23200 | 15.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.83 | 19800 | R-410A
213821113 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96MSN0261410A* | 23600 | 15.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.83 | 19800 | R-410A
213821144 | 1.88 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0401410B* | 22600 | 15.4 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213204098 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80ES(N,L)0902120A* | 23800 | 16 | 9 | 8.5 | 25800 | 28600 | 110.9% | 2.66 | 26000 | R-410A
213204182 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92ESN0802120A* | 23800 | 16 | 9.5 | 8.5 | 26000 | 28200 | 108.5% | 2.63 | 25800 | R-410A
213204347 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0802120A* | 23400 | 16 | 9 | 8.1 | 24800 | 23600 | 95.16% | 2.47 | 23200 | R-410A
213821036 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0702116A* | 23600 | 16.5 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213821037 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0702116A* | 23600 | 16.5 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213821039 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0702116A* | 23800 | 16.5 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213204133 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92ESN0401712A* | 23400 | 15.2 | 9 | 8.1 | 25200 | 28000 | 111.1% | 2.57 | 25800 | R-410A
213204178 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92ESN0801716A* | 23800 | 16.5 | 9.5 | 8.1 | 25400 | 27400 | 107.9% | 2.61 | 25400 | R-410A
213204201 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92ESN1002120A* | 23800 | 16 | 9.5 | 8.5 | 26000 | 29400 | 113.1% | 2.63 | 26400 | R-410A
213204342 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0801716A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 27000 | 106.3% | 2.68 | 25800 | R-410A
213821018 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0451412A* | 23400 | 16.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213821073 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80VTL0902120B* | 23800 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213821084 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92MSN0401712A* | 23400 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
213821102 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92MSN0802120A* | 23400 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821045 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0901714A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821046 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0902116A* | 23200 | 16.5 | 9.5 | 8.1 | 24600 | 22000 | 89.43% | 2.86 | 19700 | R-410A
213821081 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92MSN0401712A* | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
213821094 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92MSN0601714A* | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821111 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96MSN0261410A* | 23200 | 15.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.83 | 19800 | R-410A
213821128 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96MSN0601412A* | 23200 | 16 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.9 | 19700 | R-410A
213821253 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92MSN0601714A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821255 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92MSN0601714A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821288 | 1.93 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96MSN0601412A* | 23200 | 17 | 9.9 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213821290 | 1.93 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96MSN0601412A* | 23200 | 17 | 9.9 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213821469 | 2.38 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *92MSN0802120A* | 28600 | 15.3 | 8.8 | 8.4 | 33400 | 23800 | 71.26% | 2.76 | 23200 | R-410A
213821024 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0701412A* | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821033 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0701716A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821042 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0901714A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821085 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92MSN0401712A* | 23600 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
213821110 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92MSN1002120A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821115 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96MSN0261410A* | 23600 | 15.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.83 | 19800 | R-410A
213821133 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96MSN0801716A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.9 | 20000 | R-410A
213821055 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0902120A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821070 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80VTL0701716B* | 23800 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821072 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80VTL0902120B* | 23400 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213821089 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92MSN0601412A* | 23800 | 16 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213821104 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92MSN0802120A* | 23600 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821106 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92MSN1002120A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821123 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96MSN0401712A* | 23600 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213821138 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96MSN0802120A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213204185 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92ESN0802120A* | 23800 | 16 | 9.5 | 8.5 | 26000 | 27400 | 105.4% | 2.61 | 25400 | R-410A
213821184 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0701412A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.9 | 19000 | R-410A
213821202 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0901714A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821207 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0902116A* | 22400 | 17.2 | 10 | 8.4 | 25200 | 19900 | 78.97% | 2.94 | 18600 | R-410A
213821227 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80VTL0701716B* | 22400 | 17.2 | 9 | 8.4 | 25200 | 20000 | 79.37% | 2.98 | 18700 | R-410A
213821252 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92MSN0601714A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821286 | 1.88 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96MSN0601412A* | 22600 | 16.9 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213821022 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0701412A* | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821038 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0702116A* | 23800 | 16.5 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213821053 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0902120A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821056 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)1102120A* | 23400 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821120 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96MSN0401410A* | 23200 | 15.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
213821136 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96MSN0802120A* | 23600 | 16 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213821204 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0901714A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821237 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80VTL1102122B* | 22400 | 17.2 | 10 | 8.4 | 25400 | 20200 | 79.53% | 2.95 | 18800 | R-410A
213821239 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80VTL1102122B* | 22800 | 17.4 | 10.3 | 8.5 | 25400 | 20200 | 79.53% | 2.99 | 18800 | R-410A
214092994 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.04 | 25800 | R-410A
214092996 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.09 | 25800 | R-410A
214093044 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.09 | 26000 | R-410A
214093055 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9V060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 32400 | 44500 | 137.3% | 3.07 | 25600 | R-410A
214093078 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9Y080C16MP11 | 31600 | 18.4 | 9.3 | 8.1 | 32400 | 44500 | 137.3% | 3.12 | 25600 | R-410A
213821201 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0901714A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821226 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80VTL0701716B* | 22400 | 17.3 | 9.7 | 8.4 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213821235 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80VTL0902120B* | 23400 | 17 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3.01 | 18900 | R-410A
213821283 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96MSN0401712A* | 23400 | 16 | 9 | 8.5 | 26200 | 20400 | 77.86% | 2.86 | 19200 | R-410A
213821317 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0601716B* | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.93 | 19400 | R-410A
214093112 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLV060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.09 | 26000 | R-410A
214093144 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TPLC080C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092978 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8E060A12MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 44000 | 135.8% | 3.09 | 25400 | R-410A
214093014 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 44000 | 135.8% | 3.09 | 25200 | R-410A
214093053 | 2.68 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 32400 | 44000 | 135.8% | 3.06 | 25200 | R-410A
214092946 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | LPLC100C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092921 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | LP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 44500 | 137.3% | 3.07 | 25600 | R-410A
214092928 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | LP9C100C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
213204328 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0601714A* | 23800 | 15.5 | 9.5 | 8.1 | 25200 | 26800 | 106.3% | 2.7 | 25600 | R-410A
213204378 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN1002122A* | 23800 | 16.5 | 10 | 8.1 | 24800 | 26400 | 106.5% | 2.77 | 25400 | R-410A
215472299 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X36A1 | D(A,C,E)48C34+TDR | S9V2B060U4PSB+RP | 32800 | 18 | 11.7 | 8.2 | 31000 | 25800 | 83.23% | 2.39 | 29800 | R-410A
216057051 | 1.88 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.72 | 18700 | R-454B
215851260 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055218 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
216055234 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
216055236 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
216055250 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055253 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
213821109 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92MSN1002120A* | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821132 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96MSN0801716A* | 23600 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.9 | 20000 | R-410A
213821134 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96MSN0801716A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.9 | 20000 | R-410A
213821150 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0401712B* | 23600 | 15.5 | 9 | 8.1 | 24600 | 22400 | 91.06% | 2.85 | 19900 | R-410A
213821159 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0801716B* | 23400 | 16 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
213821168 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN1002120B* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
216055172 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC080C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055174 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TPLC080C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850512 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
213821177 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0451412A* | 23400 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821182 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80MS(N,L)0701412A* | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.9 | 19000 | R-410A
213821200 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0702116A* | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213821216 | 1.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)1102120A* | 22800 | 17.3 | 10.2 | 8.4 | 25600 | 20000 | 78.12% | 2.98 | 18800 | R-410A
213821020 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0451412A* | 23400 | 16.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213821054 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0902120A* | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821069 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80VTL0701716B* | 23600 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821086 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92MSN0601412A* | 23600 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213821088 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92MSN0601412A* | 23800 | 16 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213204075 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80ES(N,L)0702116A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 27400 | 107.9% | 2.68 | 25400 | R-410A
213204091 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80ES(N,L)0901714A* | 23800 | 16 | 9.5 | 8.1 | 25600 | 28200 | 110.2% | 2.63 | 25800 | R-410A
213204100 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80ES(N,L)0902120A* | 23800 | 16 | 9.5 | 8.5 | 25800 | 28200 | 109.3% | 2.61 | 25800 | R-410A
213204161 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92ESN0601714A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 29400 | 115.7% | 2.6 | 26400 | R-410A
213204243 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *95ESN0601412A* | 23800 | 15.2 | 9.4 | 8.1 | 25400 | 29000 | 114.2% | 2.59 | 26200 | R-410A
213204352 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0802120A* | 23800 | 16 | 9 | 8.1 | 24800 | 26400 | 106.5% | 2.71 | 25400 | R-410A
213204375 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN1002122A* | 23800 | 16.5 | 10 | 8.1 | 24800 | 27000 | 108.9% | 2.74 | 25800 | R-410A
213821035 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0701716A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821040 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0702116A* | 23800 | 16.5 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213821051 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0902120A* | 23400 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821060 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)1102120A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821083 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92MSN0401712A* | 23600 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
213821151 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0601412B* | 23200 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
214802939 | 3.83 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60D34+TDR | R801V1005A21UHU | 46000 | 15.5 | 10.2 | 8.4 | 46000 | 34000 | 73.91% | 3.15 | 36400 | R-410A
214802766 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V1004A17UHN | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20000 | 70.42% | 2.62 | 20800 | R-410A
214802730 | 1.87 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A44+TDR | R801V1004A17UHN | 22400 | 16.4 | 11.8 | 8.2 | 23000 | 16300 | 70.87% | 3.01 | 17000 | R-410A
213821307 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0401712B* | 23000 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213821309 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0401712B* | 23200 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213821386 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0902116A* | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
214802921 | 3.83 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60D34+TDR | R801V1005A21DZ | 46000 | 15.5 | 10.2 | 8.4 | 46000 | 33800 | 73.48% | 3.13 | 36000 | R-410A
214802937 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60B44+TDR | R801V1005A21UHU | 45000 | 15.6 | 10.1 | 8.2 | 46000 | 34000 | 73.91% | 3.06 | 36400 | R-410A
213821257 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92MSN0801716A* | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821384 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *80MS(N,L)0902116A* | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213821179 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0451412A* | 23600 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821180 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0451412A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821211 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0902120A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821215 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0902120A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821245 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92MSN0401712A* | 23400 | 16 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
213821261 | 1.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92MSN0802120A* | 23000 | 17.3 | 10.2 | 8.4 | 25600 | 20200 | 78.91% | 2.98 | 18900 | R-410A
213821366 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *80MS(N,L)0701716A* | 29400 | 15.2 | 8.9 | 8.5 | 33600 | 23800 | 70.83% | 2.79 | 23200 | R-410A
213821334 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN1002120B* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821191 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0701716A* | 22400 | 17.3 | 10 | 8.4 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213821266 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92MSN1002120A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.93 | 19100 | R-410A
213821268 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92MSN1002120A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.93 | 19100 | R-410A
213821275 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96MSN0261410A* | 23400 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213821282 | 1.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96MSN0401712A* | 23000 | 16 | 9.5 | 8.5 | 26200 | 20400 | 77.86% | 2.86 | 19200 | R-410A
213821121 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96MSN0401712A* | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213821256 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92MSN0801716A* | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821271 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96MSN0261410A* | 23000 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213821272 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96MSN0261410A* | 23000 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213821273 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96MSN0261410A* | 23400 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213821320 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0601716B* | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.93 | 19400 | R-410A
213821322 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0801716B* | 23200 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.91 | 19000 | R-410A
213821385 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0902116A* | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213205013 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0601412A* | 23200 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213821176 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0451412A* | 23400 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821251 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92MSN0601714A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821302 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0401410B* | 23000 | 16 | 10 | 8.5 | 26200 | 20400 | 77.86% | 2.85 | 19200 | R-410A
213821311 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0601412B* | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213821318 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0601716B* | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.93 | 19400 | R-410A
213821327 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0802120B* | 23600 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213821461 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *92MSN0801716A* | 29000 | 15.5 | 8.9 | 8.1 | 33200 | 24000 | 72.29% | 2.79 | 23200 | R-410A
216055004 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | LP9C080C16MP13 | 30800 | 18 | 11 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
214092930 | 2.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | LP9C100C16MP13 | 32600 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092333 | 2.8 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.3 | 32400 | 47000 | 145.1% | 3.23 | 27000 | R-410A
214092376 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9V100C20MP12 | 32600 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.16 | 26000 | R-410A
214092437 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TP9C100C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092442 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TP9C100C20MP13 | 32600 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.16 | 26000 | R-410A
214092228 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | LP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 32400 | 44500 | 137.3% | 3.07 | 25600 | R-410A
214092278 | 2.78 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.1 | 32400 | 45500 | 140.4% | 3.12 | 26200 | R-410A
214092292 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.2 | 32400 | 45000 | 138.9% | 3.11 | 25800 | R-410A
213821155 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0601412B* | 23600 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
213821171 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN1002122B* | 23800 | 16.5 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
216764619 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD04AS3 | S8X2B080M4PTC | 32600 | 17.1 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.9 | 21600 | R-454B
216764671 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S8X1C100M5PTC | 34200 | 17.1 | 12 | 9 | 33000 | 24400 | 73.94% | 2.2 | 21600 | R-454B
213821067 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80VTL0701716B* | 23400 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821092 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92MSN0601714A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821142 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0401410B* | 22400 | 15.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213821149 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0401712B* | 23400 | 15.5 | 9.5 | 8.1 | 24600 | 22400 | 91.06% | 2.85 | 19900 | R-410A
213821264 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92MSN0802120A* | 23200 | 17.4 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3 | 18900 | R-410A
213821279 | 1.88 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96MSN0401410A* | 22600 | 16.4 | 9.8 | 8.5 | 25400 | 20200 | 79.53% | 2.94 | 18800 | R-410A
213821280 | 1.92 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96MSN0401410A* | 23000 | 16.5 | 9.9 | 8.5 | 25400 | 20200 | 79.53% | 2.94 | 18800 | R-410A
213821281 | 1.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96MSN0401712A* | 23000 | 16 | 9.5 | 8.5 | 26200 | 20400 | 77.86% | 2.86 | 19200 | R-410A
213821297 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96MSN0802120A* | 22400 | 17.2 | 9 | 8.4 | 25200 | 20000 | 79.37% | 2.96 | 18700 | R-410A
213821365 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0701716A* | 29000 | 15.2 | 8.9 | 8.5 | 33600 | 23800 | 70.83% | 2.79 | 23200 | R-410A
213821314 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0601412B* | 23400 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213821276 | 1.87 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96MSN0401410A* | 22400 | 16.3 | 9.8 | 8.5 | 25400 | 20200 | 79.53% | 2.94 | 18800 | R-410A
213821285 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96MSN0401712A* | 23400 | 16 | 9 | 8.5 | 26200 | 20400 | 77.86% | 2.86 | 19200 | R-410A
216055014 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | LPLC080C16MP13 | 31200 | 18 | 11 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055116 | 2.57 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080B12MP11 | 30800 | 18 | 10.5 | 8.1 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
216055123 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9Y100C16MP11 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
216055130 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055139 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
213821456 | 2.43 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *92MSN0601714A* | 29200 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.77 | 23200 | R-410A
213821471 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)42B34+TDR | *92MSN0802120A* | 29000 | 15.4 | 8.8 | 8.3 | 33200 | 24000 | 72.29% | 2.76 | 23200 | R-410A
216055009 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | LP9C100C20MP13 | 31600 | 18 | 10 | 8.5 | 32200 | 26000 | 80.75% | 2 | 28400 | R-454B
216055075 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y100C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055077 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 31000 | 18 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
214093009 | 2.58 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8V120C20MP12 | 31000 | 16.3 | 8.8 | 8.5 | 32400 | 43500 | 134.3% | 3.13 | 25000 | R-410A
214092389 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.04 | 25800 | R-410A
214092407 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.06 | 25800 | R-410A
214092424 | 2.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TMLV100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092441 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.16 | 26000 | R-410A
214092455 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TPLC100C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092456 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092255 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | LPLC100C16MP13 | 32400 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
213821135 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96MSN0801716A* | 23800 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.9 | 20000 | R-410A
213821165 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0802120B* | 23800 | 16 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
216055023 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL8E100C20UH11 | 31200 | 17 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055030 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL9E100C20UH11 | 31200 | 17 | 10.5 | 8.5 | 31600 | 25400 | 80.38% | 2 | 27800 | R-454B
216055064 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
216055066 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
216055073 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y100C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055107 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055121 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y100C16MP11 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
216055132 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055146 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C16MP11 | 30800 | 18 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055198 | 2.62 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES120C16SMPS1 | 31400 | 18 | 11 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055367 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
213821195 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0701716A* | 22800 | 17.5 | 10.3 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
216055187 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
214437568 | 2.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9E080B12MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
215850242 | 2.57 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | CP9C100C16MP13 | 30800 | 17.5 | 10.5 | 8.1 | 31400 | 25200 | 80.25% | 2 | 27200 | R-454B
215850325 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C16MP11 | 31400 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
215850358 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
213821258 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92MSN0801716A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821260 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92MSN0801716A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213821299 | 1.88 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96MSN0802120A* | 22600 | 17.4 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213821310 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0401712B* | 23400 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213204084 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80ES(N,L)0702116A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 28600 | 112.6% | 2.61 | 26000 | R-410A
213204166 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92ESN0601714A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 27800 | 109.4% | 2.65 | 25600 | R-410A
213204168 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92ESN0801716A* | 23800 | 16.5 | 9.5 | 8.1 | 25400 | 28200 | 111% | 2.61 | 25800 | R-410A
213204345 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0801716A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 26000 | 102.4% | 2.72 | 25200 | R-410A
213204368 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN1002120A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 26000 | 104% | 2.76 | 25200 | R-410A
213821058 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)1102120A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821074 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80VTL0902120B* | 23600 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213821076 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80VTL1102122B* | 23800 | 16 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213821090 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92MSN0601412A* | 23800 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213821140 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96MSN0802120A* | 23800 | 16 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
215849793 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | CPLC080B12MP13 | 22400 | 17 | 12 | 9 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215849818 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TL9E060B12UH11 | 22400 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849895 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y060A12MP11 | 20600 | 17.5 | 10.5 | 8.5 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
215849943 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060A10MP12 | 20600 | 16.5 | 10.5 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18500 | R-454B
215850054 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE040A12MP11 | 20800 | 16.5 | 11.7 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
215850068 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE060A12MP11 | 20800 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
215850077 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TMLE080B12MP11 | 22400 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850229 | 2.55 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | CP9C080B12MP13 | 30600 | 17.5 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055006 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | LP9C100C16MP13 | 31200 | 18 | 11 | 8.5 | 31400 | 25200 | 80.25% | 2 | 27200 | R-454B
216055024 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL8E100C20UH11 | 31000 | 17 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055065 | 2.57 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080B12MP11 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
216055115 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
216055138 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE100B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055147 | 2.53 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055163 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
213821129 | 1.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96MSN0601412A* | 22800 | 15.9 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.9 | 19700 | R-410A
213821147 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0401712B* | 23200 | 15.5 | 9.5 | 8.1 | 24600 | 22400 | 91.06% | 2.85 | 19900 | R-410A
214802770 | 2.77 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R801V1004A17UHN | 33200 | 15.4 | 11.7 | 8.1 | 34200 | 24800 | 72.51% | 2.77 | 26200 | R-410A
215850607 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C20SMPS1 | 31400 | 18 | 10.5 | 8.1 | 31800 | 24200 | 76.1% | 2 | 26200 | R-454B
216055001 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | LP9C080B12MP13 | 30600 | 18 | 11 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
215850695 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
215850697 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TL8E080C16UH11 | 41500 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
215850711 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TL8E100C20UH11 | 42000 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
215850747 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM8E080C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850820 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM8V100C16MP12 | 41000 | 17 | 11.5 | 8.5 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850152 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z8ES060A12SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215850170 | 1.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES100B12SMPS1 | 20000 | 18.5 | 11.2 | 9 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850538 | 2.57 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080B12MP13 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
213821303 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0401410B* | 23400 | 16 | 10 | 8.5 | 26200 | 20400 | 77.86% | 2.85 | 19200 | R-410A
213821305 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0401410B* | 23400 | 16 | 10 | 8.5 | 26200 | 20400 | 77.86% | 2.85 | 19200 | R-410A
213821356 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0701412A* | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
216055178 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES080B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216055194 | 2.65 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C20SMPS1 | 31800 | 18 | 10.5 | 8.5 | 31600 | 25400 | 80.38% | 2 | 27600 | R-454B
216055159 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C080B12MP13 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
213821329 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0802120B* | 23800 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
216055002 | 2.57 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | LP9C080C16MP13 | 30800 | 17.5 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055018 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | LPLC100C16MP13 | 31000 | 18 | 11 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055033 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055051 | 2.53 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055067 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y080C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216055162 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055041 | 2.58 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055045 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055058 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055060 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055076 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y120C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055078 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y120C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055128 | 2.58 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055118 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y080C16MP11 | 31200 | 18 | 10.5 | 8.5 | 32000 | 25800 | 80.62% | 2 | 28200 | R-454B
216055151 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLV100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055168 | 2.63 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C100C20MP13 | 31600 | 18 | 9.8 | 8.5 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
216055183 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES080C16SMPS1 | 31000 | 18 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055203 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ET080B12LMPS1 | 30800 | 19 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
213821468 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *92MSN0802120A* | 29400 | 15.5 | 8.9 | 8.5 | 33400 | 23800 | 71.26% | 2.79 | 23200 | R-410A
213821300 | 1.9 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96MSN0802120A* | 22800 | 17.5 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213821325 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0801716B* | 23600 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.91 | 19000 | R-410A
213821016 | 1.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0451412A* | 22800 | 16.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213821050 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0902116A* | 23600 | 16.5 | 9 | 8.1 | 24600 | 22000 | 89.43% | 2.86 | 19700 | R-410A
213821082 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92MSN0401712A* | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
216055007 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | LP9C100C16MP13 | 30800 | 18 | 11 | 8.5 | 31400 | 25200 | 80.25% | 2 | 27200 | R-454B
216055032 | 2.58 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055091 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9E100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055141 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055182 | 2.62 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C16SMPS1 | 31400 | 18 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
213821030 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0701712A* | 23600 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
213821031 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0701716A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821078 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80VTL1102122B* | 23800 | 16 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213821095 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92MSN0601714A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
216055013 | 2.58 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | LPLC080C16MP13 | 31000 | 17.5 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055029 | 2.62 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL9E100C20UH11 | 31400 | 17 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
216055040 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055074 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C20MP11 | 31000 | 18 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055104 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055197 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
213821048 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0902116A* | 23600 | 16.5 | 9 | 8.1 | 24600 | 22000 | 89.43% | 2.86 | 19700 | R-410A
213821057 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)1102120A* | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
215850374 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080C16MP11 | 31000 | 18 | 11.2 | 8.1 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
215850439 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V080B12MP12 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
215850508 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE100B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
215850540 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850556 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC080C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
213205693 | 2.82 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *96VTN1202422A* | 33800 | 15.9 | 9.8 | 8.5 | 38500 | 31400 | 81.56% | 2.74 | 29000 | R-410A
213925633 | 2.9 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48C4 |  | 34800 | 18 | 9 | 8.2 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
213821029 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0701712A* | 23400 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
216055101 | 2.57 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080B12MP12 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055119 | 2.62 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080C16MP11 | 31400 | 18 | 10.5 | 8.5 | 31800 | 25800 | 81.13% | 2 | 28000 | R-454B
216055136 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE100B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055137 | 2.58 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055153 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLV100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055186 | 2.67 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES080C20SMPS1 | 32000 | 19 | 10.5 | 8.5 | 32200 | 25800 | 80.12% | 2 | 28200 | R-454B
213821032 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0701716A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821043 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0901714A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821091 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92MSN0601714A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821125 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96MSN0401712A* | 23600 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213821059 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)1102120A* | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821077 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80VTL1102122B* | 23800 | 16 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213821093 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92MSN0601714A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821100 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92MSN0801716A* | 23800 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821141 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0401410B* | 22400 | 15.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213821152 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0601412B* | 23200 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
216054840 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060B12MP12 | 21600 | 17 | 11 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216054922 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C080B12MP13 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
213204336 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0801716A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 26400 | 103.9% | 2.77 | 25400 | R-410A
213821026 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0701712A* | 23200 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
216054940 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES060A12SMPS1 | 20800 | 17.5 | 11.7 | 8.5 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216054963 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ET080B12LMPS1 | 22600 | 18 | 12 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
216054970 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES026A08SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
216054979 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES060A10SMPS1 | 19600 | 17 | 11.2 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216055388 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C20SMPS1 | 40000 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055233 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
216055256 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216054792 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054809 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8V080B12MP12 | 22600 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054844 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
216054894 | 1.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE060A12MP11 | 20200 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
216054908 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE100B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054927 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216054928 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
213821158 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0801716B* | 23600 | 16 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
213821160 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0801716B* | 23600 | 16 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
216054789 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216054805 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8V080B12MP12 | 21200 | 17 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216054830 | 1.72 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E040A10MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216054864 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9V080B12MP12 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216054880 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y060B12MP11 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216054882 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9Y080B12MP11 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
216054958 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ET060A12LMPS1 | 20800 | 18.8 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18000 | R-454B
216054993 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z9ES080B12SMPS1 | 22600 | 17 | 12 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
216055225 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
216055261 | 3.5 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C20MP11 | 42000 | 17 | 10.5 | 8.1 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
216055262 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055276 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055359 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLV120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
213821049 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0902116A* | 23400 | 16.5 | 9.5 | 8.1 | 24600 | 22000 | 89.43% | 2.86 | 19700 | R-410A
216054887 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9Y080B12MP11 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18600 | R-454B
216054907 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE100B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054932 | 1.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES040A12SMPS1 | 20400 | 17.5 | 11.2 | 9.5 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216054937 | 1.64 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES060A12SMPS1 | 19700 | 17 | 11.2 | 9 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055214 | 3.29 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | LP9C080C16MP13 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33600 | 76.36% | 2 | 32600 | R-454B
216055230 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LPLC100C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055271 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V080C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055093 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9E100C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055145 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE120C16MP11 | 30600 | 18 | 11 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055210 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z9ES080C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 32000 | 24200 | 75.62% | 2 | 26200 | R-454B
216054774 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TL9E060B12UH11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054775 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TL9E060B12UH11 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054808 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8V080B12MP12 | 22400 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
213821099 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92MSN0801716A* | 23600 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821101 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92MSN0802120A* | 23400 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821108 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92MSN1002120A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821124 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96MSN0401712A* | 23400 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213821126 | 1.88 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96MSN0601412A* | 22600 | 15.8 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.9 | 19700 | R-410A
213821167 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN1002120B* | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821169 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN1002120B* | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
216054843 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E060B12MP12 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18600 | R-454B
216054860 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9V060B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054874 | 1.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.1 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216054893 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TMLE040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054924 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TPLC080B12MP13 | 21600 | 17 | 11.7 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054926 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TPLC080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054976 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES040A10SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17800 | 78.07% | 2 | 18200 | R-454B
216054978 | 1.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES060A10SMPS1 | 20200 | 17.5 | 11.2 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18000 | R-454B
216055105 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V080C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055164 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055173 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055180 | 2.53 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES080B12SMPS1 | 30400 | 18 | 11.2 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216055189 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
216055207 | 2.45 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z9ES080C16SMPS1 | 29400 | 17.5 | 10.5 | 8.5 | 30400 | 23400 | 76.97% | 2 | 25600 | R-454B
216054762 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | LPLC080B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
213821096 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92MSN0801716A* | 23400 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821098 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92MSN0801716A* | 23800 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821130 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96MSN0601412A* | 23200 | 16 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.9 | 19700 | R-410A
213821131 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96MSN0801716A* | 23600 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.9 | 20000 | R-410A
213821146 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0401712B* | 23200 | 15.5 | 9.5 | 8.1 | 24600 | 22400 | 91.06% | 2.85 | 19900 | R-410A
214802900 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D44+TDR | R801V0755A21UH | 45500 | 15.5 | 10.2 | 8.4 | 46000 | 34200 | 74.35% | 3.14 | 36800 | R-410A
216055391 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C16SMPS1 | 40000 | 16.5 | 11.7 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055400 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C20SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
216764476 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCD008AS3 | S8X1C100M5PSC | 43500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 2.1 | 30200 | R-454B
216055005 | 2.57 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | LP9C100C16MP13 | 30800 | 17.5 | 10.5 | 8.1 | 31400 | 25200 | 80.25% | 2 | 27200 | R-454B
216055021 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL8E080C16UH11 | 31200 | 18 | 10.5 | 8.5 | 31800 | 25600 | 80.5% | 2 | 28000 | R-454B
216055062 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216054862 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V060B12MP12 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054778 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL9E060B12UH11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054798 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054814 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y060A12MP11 | 20600 | 17.5 | 10.5 | 8.5 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216054832 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E040A10MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
216054848 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E080B12MP12 | 22000 | 17 | 11.7 | 8.5 | 22400 | 18700 | 83.48% | 2 | 18700 | R-454B
216054853 | 1.64 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V040A10MP12 | 19700 | 16 | 10 | 9 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216054857 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9V040A10MP12 | 21200 | 17 | 10.5 | 8.5 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216054878 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9Y060B12MP11 | 22000 | 17 | 11.7 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216055000 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | LP9C080B12MP13 | 30800 | 18 | 11 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055034 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055050 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C16MP11 | 30800 | 18 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055068 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080C16MP11 | 31000 | 18 | 11.2 | 8.1 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216055117 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
216055120 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9Y080C16MP11 | 31200 | 18 | 10.5 | 8.5 | 32000 | 25800 | 80.62% | 2 | 28200 | R-454B
216054782 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E040A12MP11 | 20600 | 16.5 | 11.2 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216054867 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9V080B12MP12 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054999 | 2.55 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | LP9C080B12MP13 | 30600 | 17.5 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055072 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y100C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216055106 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055129 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216054945 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES080B12SMPS1 | 22600 | 18 | 12 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
216054889 | 1.65 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE040A12MP11 | 19800 | 16 | 11.2 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054930 | 1.67 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES040A12SMPS1 | 20000 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216054939 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES060A12SMPS1 | 21000 | 17.5 | 11.7 | 9 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055405 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
216055416 | 3.5 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES100C20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
216055232 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | LPLC100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
215850236 | 2.57 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | CP9C080C16MP13 | 30800 | 17.5 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850279 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TL8E100C20UH11 | 31000 | 17 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
215850470 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
215850479 | 2.62 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080C16MP11 | 31400 | 18 | 10.5 | 8.5 | 31800 | 25800 | 81.13% | 2 | 28000 | R-454B
215850493 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850536 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080B12MP13 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216054773 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TL8E060A12UH11 | 21000 | 17.5 | 11.2 | 9 | 22800 | 17900 | 78.51% | 2 | 18300 | R-454B
216054796 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E080B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055376 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055393 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
214802745 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)30B34+TDR | R801V0503A14DZ | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.63 | 21000 | R-410A
214802746 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0503A14DZ | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.63 | 21000 | R-410A
214802894 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D44+TDR | R801V0755A21DZ | 45500 | 15.5 | 10.2 | 8.4 | 46000 | 34000 | 73.91% | 3.12 | 36400 | R-410A
214802930 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D44+TDR | R801V1005A21UHS | 45500 | 15.5 | 10 | 8.4 | 46000 | 33800 | 73.48% | 3.1 | 36000 | R-410A
216054992 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES080B12SMPS1 | 22000 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216055227 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LPLC080C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055244 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL9E080C16UH11 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055278 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055279 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055295 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216055310 | 3.29 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080C16MP12 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216054812 | 1.7 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8Y060A12MP11 | 20400 | 17.5 | 9.8 | 9 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216054823 | 1.64 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E026A08MP12 | 19700 | 16 | 10 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216054846 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E080B12MP12 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
216054898 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE060A12MP11 | 20800 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216054912 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TP9C060B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054914 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TP9C060B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054948 | 1.67 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES100B12SMPS1 | 20000 | 18.5 | 11.2 | 9 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054971 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES026A08SMPS1 | 21200 | 17.5 | 11.7 | 8.1 | 23000 | 17300 | 75.22% | 2 | 17700 | R-454B
216055239 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216054957 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ET060A12LMPS1 | 21000 | 19 | 11.7 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
216054964 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ET080B12LMPS1 | 22200 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
216054973 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES040A10SMPS1 | 19500 | 17 | 11.2 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18400 | R-454B
216055226 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | LPLC080C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055228 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LPLC080C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055242 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
216055293 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y120C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055329 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
216055360 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLV120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216054956 | 1.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ET060A12LMPS1 | 20400 | 18.7 | 11 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18000 | R-454B
216054761 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | LP9C080B12MP13 | 22600 | 17 | 12 | 9 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054781 | 1.65 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E040A12MP11 | 19800 | 16 | 11.2 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054795 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E080B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054813 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8Y060A12MP11 | 21000 | 18 | 10.5 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216054815 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8Y060A12MP11 | 21000 | 17.5 | 10.5 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216054820 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y080B12MP11 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216054829 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E040A10MP12 | 19500 | 16 | 10 | 9 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
216054896 | 1.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE060A12MP11 | 20400 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216054921 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TP9C080B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054955 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ET060A12LMPS1 | 19500 | 18 | 11.2 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
216054982 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES060A10SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
216055221 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
216055257 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055341 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055346 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216054980 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES060A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
216054755 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | LP9C060B12MP13 | 22600 | 17 | 12 | 9 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054764 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | LPLC080B12MP13 | 22000 | 17 | 12 | 9 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055241 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E100C20UH11 | 40500 | 17.5 | 11.2 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
216055289 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216054771 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TL8E060A12UH11 | 21000 | 18 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
216054828 | 1.68 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E040A10MP12 | 20200 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216055071 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 31000 | 18 | 11.2 | 8.1 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216054868 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V080B12MP12 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216054899 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TMLE060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216054900 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054916 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C060B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055235 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | LPLC120C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
216055251 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055371 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216054754 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | LP9C060B12MP13 | 22400 | 17 | 12 | 9 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054765 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | LPLC080B12MP13 | 22400 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216054779 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TL9E060B12UH11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054788 | 1.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E060A12MP11 | 20400 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216054806 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8V080B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054854 | 1.72 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9V040A10MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 17500 | 76.75% | 2 | 17700 | R-454B
216054879 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y060B12MP11 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216054750 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | LP9C060B12MP13 | 21600 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054783 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054785 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054800 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E100B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054816 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8Y080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216054819 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8Y080B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054850 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E080B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
216054903 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE080B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055389 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055414 | 3.5 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES100C16SMPS1 | 42000 | 18 | 10.5 | 8.5 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
216055216 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32600 | R-454B
216055246 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055248 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL9E100C20UH11 | 41000 | 17 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055264 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055280 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V120C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055321 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215851342 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES100C16SMPS1 | 42000 | 18 | 10.5 | 8.5 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
216055334 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055368 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055420 | 3.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES120D20SMPS1 | 43000 | 17.5 | 11.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
215850074 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TMLE080B12MP11 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054919 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TP9C080B12MP13 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054934 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES040A12SMPS1 | 20600 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216055379 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055394 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C20SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216054776 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TL9E060B12UH11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054810 | 1.67 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8Y060A12MP11 | 20000 | 17.5 | 9.8 | 8.5 | 22600 | 18400 | 81.42% | 2 | 18500 | R-454B
216054811 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8Y060A12MP11 | 19500 | 17 | 10 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216054826 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E026A08MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 17600 | 77.19% | 2 | 17800 | R-454B
216054827 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E026A08MP12 | 21200 | 17 | 10.5 | 8.5 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216054858 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9V060B12MP12 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850189 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES026A08SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
215850192 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z9ES040A10SMPS1 | 20800 | 17.5 | 11.7 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18300 | R-454B
216055403 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES130D20SMPS1 | 40500 | 17.5 | 11.7 | 8.5 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215850643 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CP9C120D20MP13 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
215850673 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CPLC100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
215850790 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM8E120C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850826 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM8V100C20MP12 | 41500 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216054935 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ES040A12SMPS1 | 21000 | 17.5 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216054950 | 1.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES100B12SMPS1 | 20400 | 18.7 | 11.2 | 9.5 | 22600 | 18000 | 79.65% | 2 | 18300 | R-454B
216054952 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES100B12SMPS1 | 20600 | 18.8 | 11.2 | 9 | 22600 | 18000 | 79.65% | 2 | 18300 | R-454B
216054969 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z9ES026A08SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17300 | 75.22% | 2 | 17700 | R-454B
216054983 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES060A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216054767 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | LPLC080B12MP13 | 22600 | 17 | 12 | 9 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054817 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8Y080B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054833 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18400 | R-454B
215849916 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9E026A08MP12 | 21000 | 16.5 | 10.5 | 8.5 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216055348 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055357 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLV100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055380 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055382 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC120C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215849766 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | CP9C060B12MP13 | 22400 | 17 | 12 | 9 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849770 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | CP9C080B12MP13 | 21600 | 17 | 12 | 8.5 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
215849843 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM8E060A12MP11 | 20800 | 17.5 | 11.2 | 9 | 22800 | 17900 | 78.51% | 2 | 18200 | R-454B
215849952 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9E060B12MP12 | 22400 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054897 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216054954 | 1.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ET060A12LMPS1 | 20200 | 18.5 | 11.2 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055222 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
216055229 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | LPLC100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055263 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055274 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055313 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216054968 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES026A08SMPS1 | 20600 | 17.5 | 11.2 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
216054986 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES060B12SMPS1 | 22000 | 17 | 11.7 | 8.5 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
215850792 | 3.46 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E130D20MP11 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35200 | 76.52% | 2 | 35400 | R-454B
216055401 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
216055417 | 3.5 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES100C20SMPS1 | 42000 | 17.5 | 11.5 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
216055418 | 3.5 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES120D20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
216055219 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LP9C100C16MP13 | 40500 | 16.5 | 11.2 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
216055285 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y080C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216054836 | 1.7 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E060A10MP12 | 20400 | 16.5 | 9.8 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18500 | R-454B
216054866 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9V080B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216054902 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055237 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
216055252 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055284 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y080C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055286 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055287 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
214092358 | 2.72 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9E100C20MP12 | 32600 | 15.5 | 10 | 8.1 | 32400 | 43500 | 134.3% | 3.1 | 25000 | R-410A
214092372 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092373 | 2.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9V100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092321 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y060A12MP11 | 32400 | 18 | 9.9 | 8.1 | 32400 | 44000 | 135.8% | 3.09 | 25200 | R-410A
214092322 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 44000 | 135.8% | 3.09 | 25200 | R-410A
214092324 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y080B12MP11 | 32600 | 18 | 9.9 | 8.1 | 32400 | 44000 | 135.8% | 3.11 | 25200 | R-410A
214813298 | 1.4 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | RE(S,T)184 |  | 16800 | 15.2 | 10 | 8.2 | 19100 | 18300 | 95.81% | 2.2 | 12800 | R-410A
214813275 | 1.4 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | RE(S,T)244 |  | 16800 | 15.2 | 10 | 8.2 | 19100 | 18300 | 95.81% | 2.2 | 12800 | R-410A
216055296 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216055298 | 3.46 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C20MP12 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055314 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055323 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055325 | 3.29 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055330 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
216055374 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055381 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055383 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055415 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES100C20SMPS1 | 41000 | 17.5 | 11.2 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
216054972 | 1.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES040A10SMPS1 | 20200 | 17.5 | 11.2 | 8.1 | 22600 | 17800 | 78.76% | 2 | 18200 | R-454B
216055366 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055398 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES120C16SMPS1 | 41000 | 18 | 11.7 | 8.5 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
216054989 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES060B12SMPS1 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18600 | 81.58% | 2 | 18700 | R-454B
216055384 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055386 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216055402 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
215851241 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C20SMPS1 | 40000 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215851310 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | Z8ES130D20SMPS1 | 42000 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215851010 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
213821107 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92MSN1002120A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
215679535 | 2.82 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0802120A* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215679635 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0801716A* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.92 | 30000 | R-454B
216054831 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
216054838 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060A10MP12 | 20600 | 16.5 | 10.5 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18500 | R-454B
216054865 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V080B12MP12 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054890 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE040A12MP11 | 20600 | 16.5 | 11.2 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216054938 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES060A12SMPS1 | 20600 | 17.5 | 11.2 | 8.5 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
215849776 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | CP9C080B12MP13 | 22400 | 17 | 12 | 9 | 22800 | 18300 | 80.26% | 2 | 18400 | R-454B
216054946 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES080B12SMPS1 | 22200 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
215849861 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849959 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E080B12MP12 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
215850011 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9Y040A10MP11 | 20800 | 16.5 | 10.5 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215850020 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9Y060B12MP11 | 21600 | 17 | 11 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18500 | R-454B
215850095 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TP9C060B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850120 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TPLC080B12MP13 | 21600 | 17 | 11.7 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215850161 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z8ES080B12SMPS1 | 22200 | 18 | 12 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
215849975 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9V040A10MP12 | 20800 | 16.5 | 10.5 | 9 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
215850136 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z8ES040A12SMPS1 | 20600 | 17.5 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
215679795 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU0401712B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
216054891 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054925 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TPLC080B12MP13 | 21200 | 17 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216054942 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES080B12SMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
216054944 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES080B12SMPS1 | 22000 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
216055272 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V080C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055297 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216055324 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055331 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y120D20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
215850570 | 2.62 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C16SMPS1 | 31400 | 18 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
215850586 | 2.65 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C20SMPS1 | 31800 | 18 | 10.5 | 8.5 | 31600 | 25400 | 80.38% | 2 | 27600 | R-454B
215850613 | 3.29 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CP9C080C16MP13 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33600 | 76.36% | 2 | 32600 | R-454B
215850629 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CP9C100C16MP13 | 40500 | 16.5 | 11.2 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215850645 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CP9C120D20MP13 | 41000 | 17.5 | 11.2 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
215850679 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
216055196 | 2.62 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES120C16SMPS1 | 31400 | 18 | 11 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
215850245 | 2.6 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | CP9C100C16MP13 | 31200 | 18 | 11 | 8.5 | 31400 | 25200 | 80.25% | 2 | 27200 | R-454B
215439635 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96TC0804CNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215850252 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | CP9C100C20MP13 | 31600 | 18 | 10 | 8.5 | 32200 | 26000 | 80.75% | 2 | 28400 | R-454B
215850386 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C20MP11 | 31000 | 18 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
215439644 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96TC0403BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215849803 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TL8E060A12UH11 | 20800 | 17.5 | 11.2 | 9 | 22800 | 17900 | 78.51% | 2 | 18300 | R-454B
215849828 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8E040A12MP11 | 20800 | 16.5 | 11 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215850303 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215850321 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
215849858 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E080B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849969 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E080B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
215849987 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9V060B12MP12 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215850101 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TP9C060B12MP13 | 22400 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850727 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TL9E100C20UH11 | 41500 | 17 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850729 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E100C20UH11 | 41000 | 17 | 11 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850752 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215850754 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055301 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055303 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9E100C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055304 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C20MP12 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215851057 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
215851075 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TMLE120C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
216055200 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
215439647 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80TC0804C*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215675478 | 3.92 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *96CTN0802120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215678138 | 4.63 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0802120B* | 55500 | 17 | 8.5 | 8.5 | 60000 | 42000 | 70% | 1.9 | 51500 | R-454B
215850893 | 3.46 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C20MP12 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215850940 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V080C16MP12 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215851094 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLV100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
214336720 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R802V0755A21UHS | 45500 | 15.2 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.18 | 32400 | R-410A
216766048 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S8V2B080M4PCB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216054917 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TP9C060B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216766068 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD04AS3 | S8V2B060M4PDB | 32600 | 16 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.98 | 21600 | R-454B
216766168 | 2.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S9X2C100U5PSB | 33600 | 15.2 | 12 | 9 | 32600 | 24200 | 74.23% | 2.19 | 21400 | R-454B
213355380 | 2.92 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M36E6 |  | 35000 | 18 | 9 | 8.1 | 35400 | 26000 | 73.45% | 2.82 | 25000 | R-410A
214802927 | 3.83 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60D34+TDR | R801V1005A21UHN | 46000 | 15.5 | 10.2 | 8.4 | 46000 | 33800 | 73.48% | 3.09 | 36000 | R-410A
215850193 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES040A10SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17800 | 78.07% | 2 | 18200 | R-454B
215850770 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM8E100C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850913 | 3.42 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C20MP12 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216766202 | 2.73 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD05AS3 | S9X1C100D5PSB | 32800 | 15.2 | 12 | 8.2 | 33400 | 24400 | 73.05% | 1.99 | 21600 | R-454B
216766284 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S9X2B060U4PSB | 32400 | 16 | 11.7 | 8.7 | 32600 | 24200 | 74.23% | 2.12 | 21400 | R-454B
216055042 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E100B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
215439638 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96TC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215849946 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060B12MP12 | 21600 | 17 | 11 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216734236 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 926TC30040V14*** | 22000 | 15.5 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
215679275 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0802120B* | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215676308 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL0902120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215850530 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLV100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216734118 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 916SA48060M17*** | 22000 | 15.5 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.9 | 17600 | R-454B
213821213 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0902120A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821214 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0902120A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213821262 | 1.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92MSN0802120A* | 22800 | 17.2 | 10 | 8.4 | 25600 | 20200 | 78.91% | 2.96 | 18900 | R-410A
213821263 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92MSN0802120A* | 23400 | 17.5 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3 | 18900 | R-410A
213821278 | 1.92 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96MSN0401410A* | 23000 | 16.5 | 9.9 | 8.5 | 25400 | 20200 | 79.53% | 2.94 | 18800 | R-410A
214802926 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60C34+TDR | R801V1005A21UHN | 45000 | 15.6 | 10.1 | 8.1 | 45500 | 33600 | 73.85% | 2.99 | 36000 | R-410A
216055165 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C100C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215439643 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96TC0403BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215679785 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0802120B* | 34000 | 16 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.76 | 30600 | R-454B
215679885 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0601716B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215678308 | 1.93 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0401712B* | 23200 | 17 | 10 | 8.5 | 23400 | 16500 | 70.51% | 2 | 19900 | R-454B
216055356 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLV100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850844 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y080C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
215679305 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CTN0601716A* | 34200 | 17.5 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.88 | 30600 | R-454B
215679555 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN0802120B* | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215675728 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0901716B* | 48000 | 19 | 10 | 9 | 50000 | 37000 | 74% | 1.98 | 46500 | R-454B
216054951 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES100B12SMPS1 | 21000 | 19 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
215849773 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | CP9C080B12MP13 | 22200 | 17 | 12 | 9 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
215849787 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | CPLC080B12MP13 | 22200 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
215849840 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8E060A12MP11 | 20600 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
215676455 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0702120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676555 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
215849796 | 1.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TL8E060A12UH11 | 20000 | 17.5 | 11.2 | 9 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
215849913 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9E026A08MP12 | 20800 | 16.5 | 10.5 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
215850653 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CPLC080C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850655 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CPLC080C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850669 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CPLC100C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850578 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100B12SMPS1 | 31000 | 18 | 11.2 | 8.1 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
215850605 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z9ES080C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 32000 | 24200 | 75.62% | 2 | 26200 | R-454B
215850778 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
215850830 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM8V100C20MP12 | 41500 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
213821298 | 1.92 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96MSN0802120A* | 23000 | 17.5 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213821312 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0601412B* | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213821313 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0601412B* | 23600 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213821330 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0802120B* | 23800 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213821331 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN1002120B* | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
215849889 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8Y060A12MP11 | 20600 | 17.5 | 10.5 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
215849904 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM8Y080B12MP11 | 22400 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18400 | R-454B
215849923 | 1.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E040A10MP12 | 20200 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
215675818 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215675918 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *95CSU1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.02 | 46000 | R-454B
213781201 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *80CTL1102120B* | 33000 | 17 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 1.98 | 31600 | R-410A
213781281 | 2.67 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L21A*+WALLCON | *80CTL0451712B* | 32000 | 16.5 | 10.5 | 8.1 | 32800 | 25200 | 76.83% | 1.92 | 31800 | R-410A
215677508 | 4.63 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN0602120B* | 55500 | 17.5 | 8.5 | 8.5 | 64000 | 45500 | 71.09% | 1.94 | 57000 | R-454B
215677558 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN1202422B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
214092285 | 2.72 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E060A12MP11 | 32600 | 18 | 10 | 8.1 | 32400 | 44000 | 135.8% | 3.09 | 25400 | R-410A
213205623 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *92ESN1202420A* | 35400 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
214093371 | 2.88 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B36+TDR | Z8ES080C20SMPS1 | 34600 | 17 | 9 | 8.1 | 32400 | 44000 | 135.8% | 3.24 | 25400 | R-410A
215935530 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X30M17A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
215935630 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *80CTL0701716B* | 34200 | 20.5 | 11.5 | 8.5 | 39000 | 28400 | 72.82% | 2.02 | 32400 | R-454B
215679865 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN0802120B* | 34200 | 16 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215850264 | 2.6 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | CPLC080C16MP13 | 31200 | 18 | 11 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850631 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | CP9C100C16MP13 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215850649 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
215850683 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CPLC120C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
215850735 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
213206639 | 1.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6B100V21**20 | 22800 | 16.9 | 10.3 | 8.1 | 25200 | 19900 | 78.97% | 2.7 | 18600 | R-410A
215439654 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80TC0604B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439661 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96SC0603BUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
214336678 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V1255A24UHN | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
215676818 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN1002122B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
215935710 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27000 | 71.05% | 2 | 30600 | R-454B
215935730 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *97CMN0801714B* | 34200 | 20.5 | 11.5 | 8.5 | 39000 | 28600 | 73.33% | 2.02 | 32600 | R-454B
213781701 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X61L24A*+WALLCON | *97CMN1202422B* | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 1.98 | 31200 | R-410A
215850848 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y080C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055215 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32600 | R-454B
216055224 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | LP9C120D20MP13 | 41000 | 17.5 | 11.2 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
216055265 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055283 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055290 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055322 | 3.29 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080C16MP11 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
213203979 | 1.41 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *95ESN0401410A* | 16900 | 15.8 | 10.2 | 8.5 | 18200 | 13500 | 74.18% | 2.21 | 14200 | R-410A
213204382 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0451412A* | 23600 | 16.4 | 10.3 | 8.4 | 26000 | 26200 | 100.8% | 2.75 | 25200 | R-410A
213204413 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0701412A* | 23800 | 17 | 10 | 8.5 | 26200 | 25600 | 97.71% | 2.52 | 24800 | R-410A
213204815 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)1102120A* | 23600 | 16.2 | 10 | 8.3 | 26000 | 20200 | 77.69% | 2.94 | 19000 | R-410A
213204867 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN0601714A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213204897 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92ESN1002120A* | 23400 | 16.7 | 10 | 8.3 | 25800 | 20000 | 77.52% | 2.92 | 18900 | R-410A
213205050 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0802120A* | 23400 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
215849981 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V040A10MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 17500 | 76.75% | 2 | 17700 | R-454B
215850065 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TMLE060A12MP11 | 20800 | 17.5 | 11.2 | 9 | 22800 | 17900 | 78.51% | 2 | 18200 | R-454B
215850098 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TP9C060B12MP13 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215850133 | 1.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES040A12SMPS1 | 20000 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216055340 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055363 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055372 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
213820984 | 1.48 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *80VTL0451412B* | 17700 | 16.5 | 11 | 8.5 | 17900 | 12900 | 72.07% | 2.61 | 12500 | R-410A
216055188 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100B12SMPS1 | 31000 | 18 | 11.2 | 8.1 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
216055204 | 2.53 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ET080B12LMPS1 | 30400 | 19 | 11.2 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
215849990 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9V060B12MP12 | 22400 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850005 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V080B12MP12 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
215850139 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z8ES040A12SMPS1 | 20800 | 17.5 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
215850591 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
214595143 | 1.5 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M364+TDR |  | 18000 | 15.2 | 9.8 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
215850033 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9Y080B12MP11 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
215850080 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE080B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850164 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z8ES080B12SMPS1 | 22400 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
215850180 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z8ET060A12LMPS1 | 20800 | 18.9 | 11.7 | 9 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
215850181 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ET060A12LMPS1 | 20800 | 18.8 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18000 | R-454B
216055326 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055328 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C20MP11 | 40000 | 16.5 | 10.5 | 8.1 | 45500 | 34800 | 76.48% | 2 | 34400 | R-454B
216055361 | 3.29 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055377 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC100C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055410 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
215850214 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z9ES080B12SMPS1 | 22200 | 17 | 12 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
215850751 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM8E080C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850768 | 3.5 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C20MP11 | 42000 | 17 | 10.5 | 8.1 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850832 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V120C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851169 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TP9C120D20MP13 | 41500 | 18 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215676588 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CSU0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.12 | 46000 | R-454B
215679245 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *80CSU0601716B* | 34000 | 17 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.86 | 30600 | R-454B
216055302 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E100C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055336 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055337 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055370 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C120D20MP13 | 40000 | 17.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
212160177 | 1.97 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE32936 | A97US2V060B12X | 23600 | 20 | 13 | 8.45 | 22000 | 15400 | 70% | 1.88 | 13700 | R-410A
212160195 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P159 | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
215439649 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80TC0803B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439663 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80SC0805CUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216766466 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*CD09AS3 | S9X2C100D5PSB | 43500 | 16 | 12 | 8.5 | 44000 | 32400 | 73.64% | 2.16 | 29400 | R-454B
214336686 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R921V0705A21M4S | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214802934 | 3.67 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R801V1005A21UHU | 44000 | 15.4 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.03 | 36400 | R-410A
211752356 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE34936 | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215439648 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80TC0804C*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215677015 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL1102120B* | 57000 | 18.5 | 9.5 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
215849757 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | CP9C060B12MP13 | 21600 | 17 | 12 | 8.5 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
214505262 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*96SC0805CUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214505264 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*96VC1005CNA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214320590 | 2.67 | No | No | Frigidaire | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GXH24-36MSK4DH | C(A,C,E)37C24+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
213821588 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80MS(N,L)0902420A* | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821589 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)1102120A* | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
213821590 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)1102120A* | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
215031253 | 2.63 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CH48B34+TDR | D*96VC1005CNA* | 31600 | 19 | 11.9 | 8.1 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213779040 | 2.73 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X37L21A*+WALLCON | *96CTN0801714B* | 32800 | 17 | 11 | 8.5 | 33000 | 25200 | 76.36% | 1.96 | 31800 | R-410A
214802896 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60C34+TDR | R801V0755A21DZ | 45000 | 15.6 | 10.1 | 8.1 | 45500 | 33800 | 74.29% | 3 | 36400 | R-410A
216055396 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215850633 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CP9C100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
212159491 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P149 | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
215676928 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN1002122B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
214336661 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V0755A21DZ | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214336665 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V1005A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
215850595 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
215439642 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*96TC0403BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216055157 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080B12MP13 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055291 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y100C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055355 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLV100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
213780751 | 2.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X36L21A*+WALLCON | *80CTL0901716B* | 31600 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.84 | 31000 | R-410A
214336691 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R951V0855A21M4S | 51500 | 17 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214336675 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V1005A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336676 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V1005A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
215679355 | 2.77 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0401712B* | 33200 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.86 | 30800 | R-454B
213780451 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X60AAL+WALLCON | *96CTN1202422B* | 33000 | 16.5 | 11.5 | 8.1 | 32200 | 24800 | 77.02% | 2 | 31200 | R-410A
212969811 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *80VSL0451412B* | 23400 | 17 | 10 | 8.5 | 27000 | 25000 | 92.59% | 2.08 | 19500 | R-410A
215675888 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *80CTL1102120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215676538 | 3.96 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0801714B* | 47500 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 1.98 | 47000 | R-454B
215850367 | 2.57 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080B12MP11 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
215850451 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215850566 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080B12SMPS1 | 30800 | 18 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
215850599 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ET080B12LMPS1 | 30800 | 19 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
215851183 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055362 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215849907 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y080B12MP11 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
215850058 | 1.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE060A12MP11 | 20200 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
215850173 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z8ES100B12SMPS1 | 20600 | 18.8 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
215850188 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z9ES026A08SMPS1 | 21000 | 17.5 | 11.7 | 8.1 | 23000 | 17300 | 75.22% | 2 | 17700 | R-454B
215851228 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C16SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
215850623 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CP9C100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215850625 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215850659 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CPLC080C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215849837 | 1.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E060A12MP11 | 20200 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
215676628 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CTL1102120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215850928 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM9E120D20MP12 | 42000 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35000 | R-454B
215850946 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215676528 | 3.96 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0602120B* | 47500 | 18.5 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215676578 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *96CTN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
214725836 | 3.5 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9Y100C16MP11 | 42000 | 15.9 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.12 | 30400 | R-410A
215869141 | 4.42 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X60A1 | 5TXCC007AS3 | S9V2C100U5VSB+LRP | 53000 | 18.1 | 10 | 8.5 | 56000 | 40000 | 71.43% | 2 | 49500 | R-454B
212159758 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE34936 | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216055378 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC100C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055411 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
216733033 | 1.83 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2417AM* | 986TD42080C17*** | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 18000 | R-454B
216733301 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 88*TB48090C17*** | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
214389295 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4821AL*+UI | 987MC66100C21*** | 33800 | 19.5 | 12.5 | 9 | 36600 | 26000 | 71.04% | 2.04 | 31200 | R-410A
215850183 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z8ET080B12LMPS1 | 22200 | 18 | 12 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
214336717 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R801V1005A21UHS | 45500 | 16 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.17 | 32400 | R-410A
215679285 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *80CSU0401712B* | 34600 | 17.5 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215679335 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CTN1002122A* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215850725 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL9E100C20UH11 | 41000 | 17 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850743 | 3.42 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215439667 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80SC0604BUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215850609 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z9ES100C16SMPS1 | 32000 | 17.5 | 10.5 | 8.1 | 32400 | 24600 | 75.93% | 2 | 26400 | R-454B
215850190 | 1.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES040A10SMPS1 | 20200 | 17.5 | 11.2 | 8.1 | 22600 | 17800 | 78.76% | 2 | 18200 | R-454B
215850207 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES060B12SMPS1 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
215850964 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V120D20MP12 | 40000 | 17.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215851107 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLV120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851137 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215851162 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
213821316 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0601716B* | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.93 | 19400 | R-410A
213779611 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X60L24A*+WALLCON | *96CTN1002122B* | 32800 | 17.5 | 11.5 | 8.1 | 31800 | 24600 | 77.36% | 1.98 | 30800 | R-410A
213779761 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L24A*+WALLCON | *80CTL1102120B* | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31000 | R-410A
213779811 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L24A*+WALLCON | *96CTN1202422B* | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31000 | R-410A
214802919 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60B44+TDR | R801V1005A21DZ | 45000 | 15.6 | 10.1 | 8.2 | 46000 | 33800 | 73.48% | 3.04 | 36000 | R-410A
214638553 | 3.29 | Yes | Yes | GUARDIAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RHP15042B21 | AE(D,N,U)+CM60A34+TDR |  | 39500 | 16.2 | 12 | 8.2 | 40000 | 29200 | 73% | 3.27 | 28200 | R-410A
215677338 | 4.58 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0701716B* | 55000 | 18 | 9.5 | 9 | 59500 | 43500 | 73.11% | 2.1 | 54000 | R-454B
216054990 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES080B12SMPS1 | 21600 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
215849810 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TL9E060B12UH11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216766474 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*CD09AS3 | S9V2C100D5VSB | 43000 | 16 | 12 | 8.5 | 44000 | 32200 | 73.18% | 2.15 | 29200 | R-454B
216766526 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S9X2D120U5PSB | 44000 | 16 | 12 | 9 | 44000 | 32400 | 73.64% | 2.24 | 29400 | R-454B
216766544 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3+P0V0C000M50SD |  | 43500 | 16 | 12 | 8.7 | 44500 | 32400 | 72.81% | 2.21 | 29400 | R-454B
216766578 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8V2C080M5PDB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
216766592 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8V2D120M5PCB | 43000 | 16.5 | 12 | 9 | 44500 | 32400 | 72.81% | 2.23 | 29400 | R-454B
216055211 | 2.67 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z9ES100C16SMPS1 | 32000 | 17.5 | 10.5 | 8.1 | 32400 | 24600 | 75.93% | 2 | 26400 | R-454B
215439639 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*96TC0603BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215675938 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CMN1202422B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216054758 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | LP9C080B12MP13 | 22000 | 17 | 12 | 8.5 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216054759 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | LP9C080B12MP13 | 22600 | 17 | 12 | 9 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
214389313 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4824AL*+UI | 986TD66100C21*** | 33800 | 19.5 | 12.5 | 9 | 36600 | 26000 | 71.04% | 2.04 | 31200 | R-410A
214389394 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*3621AL*+UI | 987MC42060C17*** | 32400 | 18 | 11 | 9 | 39000 | 27400 | 70.26% | 1.9 | 33000 | R-410A
216057050 | 1.83 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR |  | 22000 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.67 | 18600 | R-454B
216054757 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | LP9C080B12MP13 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054807 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8V080B12MP12 | 22400 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216054824 | 1.72 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E026A08MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 17600 | 77.19% | 2 | 17800 | R-454B
216054841 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E060B12MP12 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18600 | R-454B
215679575 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1002122A* | 34400 | 18.5 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215679595 | 2.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0802120B* | 34800 | 18 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215850685 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
215850766 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM8E100C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850816 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM8V100C16MP12 | 41000 | 17 | 11.5 | 8.5 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850852 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
215850885 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
215851016 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215851034 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215851036 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215676335 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *95CSU1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.02 | 46000 | R-454B
211176460 | 3.79 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | MCG48T(C,D)2M | GUH96T090C3M | 45500 | 15.2 | 12.3 | 8.1 | 45000 | 31600 | 70.22% | 2.8 | 13500 | R-410A
215679455 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CTN0801716A* | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
213613574 | 1.5 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M36D4 |  | 18000 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
216764617 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD04AS3 | S8X2B060M4PTC | 32600 | 17.1 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.9 | 21600 | R-454B
216764701 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD09AS3 | S8X2C080M5PSC | 34200 | 17.1 | 12.5 | 9 | 32200 | 24000 | 74.53% | 2.1 | 21200 | R-454B
216764719 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S8X2B080M4PSC | 32600 | 17.1 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
212969581 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *80VSL0451412B* | 17700 | 16.5 | 11 | 8.5 | 18700 | 19100 | 102.1% | 2.3 | 12500 | R-410A
212970431 | 3 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *80VSL0701716B* | 36000 | 16 | 10 | 8.5 | 38500 | 34800 | 90.39% | 2.02 | 29000 | R-410A
214336671 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V0755A21DZ | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
215679485 | 2.82 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0802120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215439636 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*96TC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216055015 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | LPLC080C16MP13 | 31000 | 18 | 11 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055022 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TL8E100C20UH11 | 31000 | 17 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
215849926 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9E040A10MP12 | 20600 | 16.5 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
215849962 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9E080B12MP12 | 22200 | 17 | 11.7 | 8.5 | 22800 | 18700 | 82.02% | 2 | 18800 | R-454B
215850017 | 1.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.1 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
215850051 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TMLE040A12MP11 | 21000 | 16.5 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215850167 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES080B12SMPS1 | 22200 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
215850178 | 1.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ET060A12LMPS1 | 20200 | 18.5 | 11.2 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216766694 | 4.21 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8V2C080M5PCB | 50500 | 15.2 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.17 | 34000 | R-454B
215439655 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80TC0603B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439657 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80TC0603B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216766728 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S9V2C080U5VSB | 51000 | 15.2 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34200 | R-454B
215679665 | 2.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN0802120B* | 34800 | 18 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215676515 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *95CSU1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
215676415 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2.12 | 46000 | R-454B
213821114 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96MSN0261410A* | 23400 | 15.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.83 | 19800 | R-410A
213821163 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0802120B* | 23800 | 16 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
216766016 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S9V2B060U4VSB | 32200 | 16 | 12 | 8.7 | 32200 | 24000 | 74.53% | 2.11 | 21200 | R-454B
216766032 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S8V2B060M4PDB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216766050 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S8V2B060M4PCB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216054875 | 1.77 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9Y040A10MP11 | 21200 | 17 | 10.5 | 8.1 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216054909 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE100B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054941 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ES060A12SMPS1 | 21200 | 17.5 | 11.7 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216054959 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ET060A12LMPS1 | 21000 | 19 | 11.7 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
216054961 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ET080B12LMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
216055044 | 2.62 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C16MP11 | 31400 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055061 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055111 | 2.63 | No | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V100C20MP12 | 31600 | 18 | 9.8 | 8.5 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
214336715 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R801V0755A21UHS | 45500 | 15.2 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.18 | 32400 | R-410A
214336722 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R802V1005A21UHS | 45500 | 16 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.17 | 32400 | R-410A
216055407 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES080C16SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
215850772 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
212160144 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H210P299 | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214092691 | 2.88 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B34+TDR | Z8ES100C20SMPS1 | 34600 | 16.5 | 9 | 8.1 | 32400 | 44500 | 137.3% | 3.25 | 25600 | R-410A
216765968 | 1.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3 | S9X2B040D3PSB | 22400 | 16.5 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2.01 | 15100 | R-454B
216765998 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3 | S9X1B060U4PSB | 23800 | 17.1 | 12.5 | 9 | 21800 | 17400 | 79.82% | 2.08 | 15400 | R-454B
216766316 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S8V2B060M4PCB | 33200 | 16.5 | 12 | 8.7 | 32600 | 24000 | 73.62% | 2.16 | 21200 | R-454B
213770474 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X24L14A*+WALLCON | *80CTL0701412B* | 23400 | 16.5 | 10.5 | 8.1 | 22000 | 16800 | 76.36% | 1.9 | 21000 | R-410A
213770524 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X24L17A*+WALLCON | *80CTL0901716B* | 23400 | 16.5 | 10.5 | 8.1 | 21800 | 16800 | 77.06% | 1.9 | 21000 | R-410A
216055031 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055240 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216055258 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055288 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055315 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216054988 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES060B12SMPS1 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
216055122 | 2.58 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 31000 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
215679655 | 2.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN1002122A* | 34800 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215679775 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CTN1202422A* | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215869159 | 4.25 | No | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X60A1 | 5TXCD010AS3 | S9V2C100D5VSB+LRP | 51000 | 18 | 9.8 | 8.5 | 53000 | 38500 | 72.64% | 1.9 | 47000 | R-454B
216055127 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055294 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y120C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055311 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V080C16MP12 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055327 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y100C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055342 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055161 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055175 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055343 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
211260040 | 1.57 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | OMV098J12* | 18800 | 16 | 11 | 8.5 | 18800 | 17500 | 93.09% | 2.12 | 12600 | R-410A
211260133 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L14A* | *95ESN0401410A* | 17700 | 15.5 | 10.5 | 8.5 | 18700 | 19000 | 101.6% | 2.28 | 12500 | R-410A
215850954 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215588127 | 4.17 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6124AM*+UI | 59CU5B080C21**20 | 50000 | 19 | 11 | 10.5 | 53000 | 52500 | 99.06% | 1.94 | 51000 | R-454B
215588141 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*4812AM*+UI | 59CU5B080C21**20 | 48500 | 17.5 | 10.5 | 10.5 | 52500 | 52000 | 99.05% | 1.92 | 50500 | R-454B
213771426 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CAP**4224AL*+UI | 986TD66120C24*** | 23800 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
216055140 | 2.62 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C16MP11 | 31400 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055179 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080B12SMPS1 | 30800 | 18 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216055181 | 2.6 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES080C16SMPS1 | 31200 | 18 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216054770 | 1.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TL8E060A12UH11 | 20400 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18200 | R-454B
216054772 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL8E060A12UH11 | 20600 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18200 | R-454B
216054790 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E060A12MP11 | 20800 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216054863 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9V060B12MP12 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054872 | 1.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9Y040A10MP11 | 20600 | 16.5 | 9.8 | 8.1 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
215850804 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V080C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850854 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
215850897 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM9E080C20MP12 | 43000 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215851154 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215851256 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215851315 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | Z8ES130D20SMPS1 | 42000 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215851331 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
215850627 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | CP9C100C16MP13 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215851253 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C16SMPS1 | 40000 | 16.5 | 11.7 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215851266 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C20SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215851268 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215850990 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y100C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
215851020 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215851070 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TMLE120C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215851213 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC120C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851312 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215850689 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33600 | R-454B
213770674 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X25L17A*+WALLCON | *96CTN0601714B* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
213770824 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X36L17A*+WALLCON | *80CTL0701412B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.94 | 20800 | R-410A
213771024 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X36L21A*+WALLCON | *96CTN1002122B* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
216054904 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE080B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054906 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054920 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TP9C080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
214389299 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4821AL*+UI | 986TD42080C17*** | 33400 | 19 | 12 | 9 | 36800 | 26200 | 71.2% | 2.02 | 31400 | R-410A
214389317 | 2.83 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*6024AL*+UI | 88*TB60090C21*** | 34000 | 20 | 12.5 | 9 | 36200 | 25400 | 70.17% | 2.02 | 30600 | R-410A
215676095 | 3.92 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M21A*+WALLCON | *80CSU0601716A* | 47000 | 18 | 9.5 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
213204422 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0701712A* | 23400 | 17 | 10 | 8.5 | 25600 | 26800 | 104.7% | 2.84 | 25600 | R-410A
215850986 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216766446 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S8V2C100M5PCB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.21 | 29200 | R-454B
216766480 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S8V2C080M5PDB | 43500 | 16 | 12 | 8.7 | 45000 | 32800 | 72.89% | 2.21 | 30000 | R-454B
216766496 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S8V2C100M5PCB | 43000 | 16 | 12 | 8.7 | 44500 | 32600 | 73.26% | 2.22 | 29800 | R-454B
216766596 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8V2C080M5PCB | 43500 | 16 | 12 | 8.7 | 45000 | 32800 | 72.89% | 2.21 | 30000 | R-454B
216766362 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 | S8V2C080M5PDB | 32600 | 16 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.13 | 21400 | R-454B
216766378 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | S9V2C100D5VSB | 31800 | 15.2 | 11.7 | 8.7 | 31600 | 23600 | 74.68% | 2.16 | 21000 | R-454B
216055176 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055193 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
216055195 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
216055209 | 2.62 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C20SMPS1 | 31400 | 18 | 10.5 | 8.1 | 31800 | 24200 | 76.1% | 2 | 26200 | R-454B
216054929 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TPLC080B12MP13 | 22600 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054931 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES040A12SMPS1 | 19500 | 17 | 11 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216054974 | 1.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES040A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17800 | 78.07% | 2 | 18300 | R-454B
216054981 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z9ES060A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
214389406 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4221AL*+UI | 88*TB36045C17*** | 32800 | 18 | 11 | 9 | 38000 | 26800 | 70.53% | 1.94 | 32400 | R-410A
216055397 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C16SMPS1 | 40000 | 17.5 | 11.5 | 8.1 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
213204458 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0901714A* | 23800 | 17 | 10.4 | 8.5 | 25800 | 26000 | 100.8% | 2.76 | 25200 | R-410A
213204805 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0902120A* | 23800 | 17 | 10.4 | 8.5 | 25800 | 20000 | 77.52% | 2.98 | 18900 | R-410A
213204872 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN0801716A* | 23400 | 17.4 | 10.3 | 8.5 | 25600 | 20000 | 78.12% | 3 | 18800 | R-410A
213204070 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80ES(N,L)0701716A* | 23800 | 15.5 | 9 | 8.5 | 26200 | 28600 | 109.2% | 2.63 | 26000 | R-410A
213204157 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92ESN0601714A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 28200 | 111% | 2.69 | 25800 | R-410A
215439665 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80SC0604BUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215679915 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1002122A* | 34200 | 16.5 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
216766792 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S9X2B040U3PSB | 23200 | 16.5 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2.01 | 15400 | R-454B
215677058 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN0802120B* | 56500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.06 | 56500 | R-454B
215439640 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96TC0603BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216733053 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2417AM* | 926TC36040V17*** | 22000 | 15.5 | 10 | 8.5 | 21200 | 19300 | 91.04% | 1.98 | 18100 | R-454B
216054760 | 1.85 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | LP9C080B12MP13 | 22200 | 17 | 12 | 9 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
215850260 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | CPLC080C16MP13 | 31000 | 17.5 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850294 | 2.62 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL9E100C20UH11 | 31400 | 17 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
215850562 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216732948 | 1.82 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2417AM* | 926SB30040V14*** | 21800 | 15.5 | 10 | 8.5 | 21200 | 19200 | 90.57% | 1.96 | 18100 | R-454B
215850774 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
215850958 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM9V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
213204112 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80ES(N,L)1102120A* | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 27600 | 105.3% | 2.7 | 25000 | R-410A
213204164 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92ESN0601714A* | 23800 | 16 | 9 | 8.1 | 25400 | 28000 | 110.2% | 2.59 | 25800 | R-410A
213204180 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92ESN0802120A* | 23800 | 16 | 9 | 8.5 | 26000 | 28000 | 107.7% | 2.62 | 25800 | R-410A
213204199 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92ESN1002120A* | 23800 | 16 | 9 | 8.5 | 26000 | 27800 | 106.9% | 2.6 | 25600 | R-410A
213204279 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *95ESN0802120A* | 23800 | 15.5 | 9.5 | 8.5 | 26000 | 26000 | 100% | 2.73 | 25200 | R-410A
213204366 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN1002120A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 26200 | 104.8% | 2.75 | 25200 | R-410A
214093051 | 2.58 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9V040A10MP12 | 31000 | 16.9 | 9.3 | 8.1 | 32400 | 44000 | 135.8% | 3.04 | 25200 | R-410A
212159483 | 1.93 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE32936 | A80UH1E045A12 | 23200 | 20 | 13 | 8.45 | 21200 | 14900 | 70.28% | 1.84 | 13200 | R-410A
212159684 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P159 | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
212160119 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H210P299 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212160169 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE34936 | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212160186 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P149 | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
215849898 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8Y080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
215849932 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E040A10MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
215849999 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9V080B12MP12 | 22200 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
215850149 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z8ES060A12SMPS1 | 20800 | 17.5 | 11 | 9 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215850198 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES060B12SMPS1 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18600 | 83.04% | 2 | 18500 | R-454B
214336716 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R801V1005A21UHN | 45500 | 16 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.17 | 32400 | R-410A
216055412 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES100C16SMPS1 | 41000 | 17.5 | 10.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
215850615 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32600 | R-454B
214389279 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4821AL*+UI | 88*TB36045C17*** | 33200 | 18.5 | 11.7 | 9 | 37000 | 26200 | 70.81% | 2 | 31600 | R-410A
216733334 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 82*TB48090V17*** | 23200 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216733469 | 1.9 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 926SB30040V14*** | 22800 | 15.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
215679505 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716B* | 33800 | 18 | 9.5 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
214802916 | 3.67 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R801V1005A21DZ | 44000 | 15.4 | 10 | 8.1 | 45500 | 33600 | 73.85% | 3.01 | 36000 | R-410A
214573153 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X42AAL+WALLCON | *95CSU1002122B* | 32600 | 17 | 11 | 8.5 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
212976668 | 1.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *96VTN1002120B* | 23600 | 17.5 | 10 | 8.5 | 26200 | 23800 | 90.84% | 1.98 | 19000 | R-410A
214093082 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.09 | 26000 | R-410A
214093085 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y100C20MP11 | 32400 | 15.5 | 9.5 | 8.1 | 32400 | 44500 | 137.3% | 3.05 | 25600 | R-410A
214093101 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.2 | 32400 | 45000 | 138.9% | 3.11 | 25800 | R-410A
214093118 | 2.65 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLV120C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25200 | R-410A
215439656 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80TC0603B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439673 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*97MC0603BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216054837 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E060A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18600 | R-454B
215849834 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E040A12MP11 | 20800 | 16.5 | 11.7 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
215849852 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8E080B12MP11 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215849870 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E100B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849886 | 1.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8Y060A12MP11 | 20000 | 17.5 | 9.8 | 8.5 | 22600 | 18400 | 81.42% | 2 | 18500 | R-454B
216766084 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD04AS3 | S9V2B040D3VSB | 32600 | 16 | 11.7 | 8.2 | 33600 | 24600 | 73.21% | 1.98 | 21800 | R-454B
213753627 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)36B34+TDR | 59TP6C100V21**22 | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
213821462 | 2.43 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *92MSN0801716A* | 29200 | 15.5 | 8.9 | 8.1 | 33200 | 24000 | 72.29% | 2.79 | 23200 | R-410A
213821464 | 2.4 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *92MSN0801716A* | 28800 | 15.4 | 8.8 | 8.1 | 33200 | 24000 | 72.29% | 2.79 | 23200 | R-410A
215849984 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9V060B12MP12 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850029 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y060B12MP11 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
215850061 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TMLE060A12MP11 | 20600 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
215850086 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TMLE100B12MP11 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215850104 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C060B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850177 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES100B12SMPS1 | 20600 | 18.8 | 11.2 | 9 | 22600 | 18000 | 79.65% | 2 | 18300 | R-454B
215851082 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TMLE130D20MP11 | 43000 | 17 | 11 | 8.5 | 46500 | 35200 | 75.7% | 2 | 35600 | R-454B
215851134 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215851185 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC100C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850651 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | CP9C120D20MP13 | 41500 | 17.5 | 11.5 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
215850715 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
215850733 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216733536 | 1.9 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 986TD30040C14*** | 22800 | 15.5 | 10.5 | 8.5 | 20800 | 18600 | 89.42% | 1.96 | 17700 | R-454B
216733805 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 83*CA36040C17*** | 22800 | 17 | 11 | 8.5 | 21200 | 19000 | 89.62% | 1.94 | 17900 | R-454B
214389382 | 2.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*3621AL*+UI | 88*TB36045C17*** | 32000 | 18 | 11 | 9 | 39000 | 27400 | 70.26% | 1.9 | 33000 | R-410A
214389400 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*3621AL*+UI | 986TD42060C17*** | 32400 | 18 | 11 | 9 | 39000 | 27400 | 70.26% | 1.9 | 33000 | R-410A
215849761 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | CP9C060B12MP13 | 22200 | 17 | 12 | 9 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215487439 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*80VC0804C*A* | 45500 | 16.5 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
213821607 | 2.8 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80VTL0902120B* | 33600 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
213821640 | 2.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *96MSN0802120A* | 35200 | 16 | 9.5 | 8.1 | 39000 | 32200 | 82.56% | 2.52 | 29600 | R-410A
213821540 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *96VTN0802120B* | 29400 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.8 | 23200 | R-410A
215439634 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96TC0804CNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439652 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80TC0604B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439668 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*97MC0804CNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216733514 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 935SB36040M17*** | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
212159688 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE34936 | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
212160133 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | V,A,D36H175D149 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213821174 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN1002122B* | 23800 | 16.5 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
215850647 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | CP9C120D20MP13 | 41500 | 17.5 | 11.5 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
213821467 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *92MSN0802120A* | 29000 | 15.5 | 8.9 | 8.5 | 33400 | 23800 | 71.26% | 2.79 | 23200 | R-410A
215850731 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TL9E100C20UH11 | 41500 | 17 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850637 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | CP9C100C20MP13 | 41000 | 18 | 11 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
215850739 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215850814 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850864 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215850889 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
215850923 | 3.38 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E120D20MP12 | 40500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215851014 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215851146 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215851173 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055406 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C16SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
216055408 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES080C16SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
215850705 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
215850828 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851198 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216764785 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S8X2C100M5PSC | 43500 | 17.1 | 11.7 | 9 | 45000 | 33000 | 73.33% | 2.2 | 30200 | R-454B
216764801 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S8X2D120M5PSC | 44000 | 17.1 | 12 | 9 | 44500 | 32400 | 72.81% | 2.2 | 29400 | R-454B
215851004 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y120D20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
215851040 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
215851065 | 3.42 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215439666 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80SC0604BUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
213925634 | 2.93 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48D4 |  | 35200 | 18 | 9 | 8.2 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
213205527 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0902116A* | 35200 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213205541 | 2.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0902420A* | 35000 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213205560 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80ES(N,L)1102420A* | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
216699817 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*97MC0804CNA* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
216699800 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A*+MBVK16CP1X00A* |  | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
213771576 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CAP**4821AL*+UI | 88*TB48090C17*** | 24200 | 17 | 11 | 8.1 | 20800 | 16500 | 79.33% | 2.02 | 20400 | R-410A
215850663 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | CPLC100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850420 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9E100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
215850445 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V080C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850786 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM8E120C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850822 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215850836 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM8V120C20MP12 | 41500 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215850872 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215850936 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V080C16MP12 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215851104 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLV120C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851249 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215851329 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C20SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
215851347 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES100C16SMPS1 | 42000 | 18 | 10.5 | 8.5 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
215851372 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES120D20SMPS1 | 43000 | 17.5 | 11.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
216733654 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3014AM* | 8(0,1)*SB36045M14*** | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216733685 | 1.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3014AM* | 82*SB36070V14*** | 22400 | 16.5 | 11 | 8.5 | 20800 | 18800 | 90.38% | 1.96 | 17600 | R-454B
215850834 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215850883 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216765884 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD04AS3 | S9V2B040D3VSB | 23400 | 17.1 | 12.5 | 8.1 | 22200 | 17200 | 77.48% | 1.84 | 15400 | R-454B
216765934 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3 | S9X2B040D3PSB | 21600 | 15.2 | 11.7 | 8.5 | 21200 | 16800 | 79.25% | 1.93 | 15000 | R-454B
215439674 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*97MC0603BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215679515 | 2.78 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0601716A* | 33400 | 17.5 | 9.5 | 9 | 35200 | 25400 | 72.16% | 1.88 | 30600 | R-454B
215851318 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C16SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
207699009 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30U-30HFN1-MR0(X) | MVC-30HWFN1-M |  | 30000 | 16.2 | 10 | 8.9 | 33000 | 24000 | 72.73% | 1.8 | 21000 | R-410A
214606338 | 2.85 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B36T21 | AE(D,N,U)+CM48C3G+TDR |  | 34200 | 15.5 | 12.1 | 8.1 | 33800 | 25000 | 73.96% | 3.16 | 24000 | R-410A
215850921 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM9E100C20MP12 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850980 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
215851028 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TMLE080C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215851053 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TMLE100C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215851055 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
215851280 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C16SMPS1 | 40000 | 17.5 | 11.5 | 8.1 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
215851321 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES080C16SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
215850249 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | CP9C100C20MP13 | 31600 | 17.5 | 9.8 | 8.1 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
215850267 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | CPLC100C16MP13 | 31000 | 17.5 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850297 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850364 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
215487454 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA4830*3A* | D*96VC1205DNA* | 45500 | 16.5 | 10 | 8.5 | 46000 | 33600 | 73.04% | 2 | 28400 | R-32
214243060 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D,W)4X42L21**+WALLCON | *96CTN0801714B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
213779140 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X42L21A*+WALLCON | *97CMN1002122B* | 31800 | 17 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.88 | 31200 | R-410A
213779390 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X48L21A*+WALLCON | *80CTL0901716B* | 32400 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.96 | 31400 | R-410A
214243160 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D,W)4X48L21**+WALLCON | *97CMN1002122B* | 24200 | 17 | 11.5 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
216055387 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
215850808 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V080C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850842 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
215850858 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
215850976 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
215850994 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C20MP11 | 40000 | 16.5 | 10.5 | 8.1 | 45500 | 34800 | 76.48% | 2 | 34400 | R-454B
215851061 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
215851092 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLV100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215851141 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215851192 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC100C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850782 | 3.42 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215850802 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V080C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850868 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y100C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215850901 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM9E080C20MP12 | 43000 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850917 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TM9E100C20MP12 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215850932 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TM9E120D20MP12 | 42000 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35000 | R-454B
215850984 | 3.29 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
215851099 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLV100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850233 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | CP9C080B12MP13 | 30800 | 18 | 11 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
215850282 | 2.6 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL8E100C20UH11 | 31200 | 17 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
215850300 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850315 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
215850514 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C16MP11 | 31400 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216766744 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S8V2D120M5PDB | 51000 | 15.2 | 11.2 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34000 | R-454B
216766760 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3+P0V0C000M50SD |  | 52500 | 16 | 11.5 | 9 | 51000 | 38500 | 75.49% | 2.24 | 33800 | R-454B
214573967 | 2.7 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH837GKA2* | EA*4X48L21A*+WALLCON | *96CTN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32400 | 24800 | 76.54% | 2 | 31400 | R-410A
216055320 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215683667 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3717AM*+UI | 58CU*A060C17**16 | 23800 | 17 | 10 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
215439653 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80TC0604B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215850454 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
212400414 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C44+JMET12BS2N1+TDR |  | 34000 | 18 | 8.5 | 8.1 | 36000 | 25400 | 70.56% | 2.64 | 24800 | R-410A
215850211 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES080B12SMPS1 | 21600 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216764817 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8X1C080M5PTC | 43000 | 17.1 | 11.7 | 9 | 44500 | 32600 | 73.26% | 2.1 | 29800 | R-454B
216764833 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S8X2C080M5PSC | 44000 | 17.1 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29400 | R-454B
214802739 | 1.87 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24B34+TDR | R801V1004A17UHS | 22400 | 16 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 3.03 | 17000 | R-410A
216764919 | 1.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8X2B080M4PTC | 22600 | 17.5 | 12 | 8.7 | 21600 | 17000 | 78.7% | 1.9 | 15100 | R-454B
215850838 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215850956 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215850970 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215851006 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
215851122 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215683883 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3717AM*+UI | 59MN7C080C17**14 | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215683917 | 2.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 59MN7C060C21**20 | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215684017 | 2.8 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 58TN*B070C17**16 | 33600 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.78 | 31000 | R-454B
212986132 | 1.93 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L14A* | *96MSN0401410A* | 23200 | 16 | 9.5 | 8.5 | 27000 | 26600 | 98.52% | 2.22 | 19500 | R-410A
212986216 | 1.93 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L14** | *96MSN0401410A* | 23200 | 16 | 10 | 8.5 | 27000 | 25200 | 93.33% | 2.1 | 19500 | R-410A
214242860 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | END4X42L17**+WALLCON | *80CTL0451712B* | 23800 | 16 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
214242960 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D,W)4X42L21**+WALLCON | *80CTL0451712B* | 23600 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.94 | 20800 | R-410A
216737345 | 1.87 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80VTL0701716B* | 22400 | 15.5 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.85 | 17700 | R-454B
216054753 | 1.88 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | LP9C060B12MP13 | 22600 | 17 | 12 | 9 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054787 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E060A12MP11 | 19500 | 17 | 11 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216054839 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E060A10MP12 | 21000 | 17 | 10.5 | 9 | 22800 | 18100 | 79.39% | 2 | 18600 | R-454B
216054855 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9V040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216054871 | 1.66 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y040A10MP11 | 19900 | 16 | 10 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216054873 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216054962 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ET080B12LMPS1 | 22000 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
215851113 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLV120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216737562 | 1.87 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *96MSN0801716A* | 22400 | 15.2 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.9 | 17700 | R-454B
216737696 | 1.87 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *95MSU0401712A* | 22400 | 15.5 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
216738132 | 1.9 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *80MS(N,L)1552420A* | 22800 | 15.5 | 10.5 | 8.1 | 20800 | 18500 | 88.94% | 1.85 | 17600 | R-454B
216738167 | 1.88 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *80VSL0901716B* | 22600 | 15.5 | 10.5 | 8.1 | 20600 | 18400 | 89.32% | 1.85 | 17500 | R-454B
216738718 | 1.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *95MSU0802120A* | 22600 | 16 | 11 | 8.1 | 20800 | 18400 | 88.46% | 1.85 | 17500 | R-454B
216738833 | 1.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *96VTN0601716B* | 22600 | 16 | 11 | 8.1 | 20800 | 18500 | 88.94% | 1.85 | 17600 | R-454B
216738917 | 1.9 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *97VTN0802120A* | 22800 | 16 | 11 | 8.1 | 21000 | 18600 | 88.57% | 1.85 | 17700 | R-454B
216766380 | 2.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | S9X1C100U5PSB | 33600 | 15.2 | 12 | 9 | 32800 | 24200 | 73.78% | 2.19 | 21400 | R-454B
215683705 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 59MN7C060C17**14 | 24000 | 17 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215851222 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851231 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
215851274 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055273 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V080C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055282 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055307 | 3.38 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E120D20MP12 | 40500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055316 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055332 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
207803596 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-17HFN1-MT0W | MVC-18HWFN1-MW(GA) |  | 18000 | 17.6 | 11.7 | 9.6 | 19000 | 17000 | 89.47% | 2 | 15400 | R-410A
216055364 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055373 | 3.29 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC080C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055375 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215679325 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CTN0802120A* | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
216733703 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3014AM* | 82*TB36045V14*** | 22000 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
215850568 | 2.6 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES080C16SMPS1 | 31200 | 18 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
215679475 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CTN1002122A* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215679625 | 2.87 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0601716A* | 34400 | 17.5 | 9.5 | 9 | 34600 | 25200 | 72.83% | 1.9 | 30200 | R-454B
215679645 | 2.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0802120A* | 34800 | 18 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215679675 | 2.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN0802120A* | 34800 | 18 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215679695 | 2.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN1202422A* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215439664 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80SC0805CUA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216733994 | 1.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 82*TB48070V17*** | 22400 | 16 | 10.5 | 8.5 | 21000 | 18800 | 89.52% | 1.96 | 17600 | R-454B
215679745 | 2.78 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CTN0801716A* | 33400 | 16 | 9 | 8.5 | 36000 | 25600 | 71.11% | 1.76 | 31000 | R-454B
215679995 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1002122A* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.82 | 30000 | R-454B
216055191 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31400 | 25200 | 80.25% | 2 | 27600 | R-454B
215831777 | 2.65 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | LP9C100C16MP13 | 31800 | 17.5 | 9.9 | 8.3 | 33800 | 24000 | 71.01% | 2.1 | 25400 | R-410A
215850582 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31400 | 25200 | 80.25% | 2 | 27600 | R-454B
215850584 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
215849779 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | CP9C080B12MP13 | 22200 | 17 | 12 | 9 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
215849831 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM8E040A12MP11 | 21000 | 16.5 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215849996 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9V080B12MP12 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
215850014 | 1.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.1 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215850083 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850182 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ET080B12LMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
212438128 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213771626 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CAP**4821AL*+UI | 987MC42080C17*** | 24000 | 16.5 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
216699836 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*80TC0804C*A* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
211708425 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TL9E100C20UH11 | 45500 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.08 | 30600 | R-410A
211708436 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM8E100C20MP11 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
211708468 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9E080C20MP12 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
211708504 | 3.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TMLE100C16MP11 | 45000 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
216764735 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S8X1B080M4PTC | 33400 | 17.1 | 12 | 9 | 32800 | 24200 | 73.78% | 2.1 | 21400 | R-454B
215679425 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CSU0401712B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215676778 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *95CSU0802120B* | 48500 | 18.5 | 10 | 9 | 50000 | 37000 | 74% | 2 | 47000 | R-454B
216766430 | 2.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCD010AS3 | S8V2D120M5PCB | 34600 | 17.1 | 12.5 | 9 | 32400 | 24000 | 74.07% | 2.24 | 21200 | R-454B
215940123 | 2.82 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0601716B* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.92 | 30400 | R-454B
213821148 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0401712B* | 23600 | 15.5 | 9 | 8.1 | 24600 | 22400 | 91.06% | 2.85 | 19900 | R-410A
216738414 | 1.88 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *97CMN0801714B* | 22600 | 15.2 | 10.5 | 8.1 | 20600 | 18400 | 89.32% | 1.85 | 17500 | R-454B
215677795 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1352422B* | 55500 | 18.5 | 9 | 9 | 59000 | 41500 | 70.34% | 2.02 | 50500 | R-454B
216055399 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES120C16SMPS1 | 41000 | 18 | 11.7 | 8.5 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
215850862 | 3.33 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215850996 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
215851078 | 3.46 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE130D20MP11 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35200 | 76.52% | 2 | 35400 | R-454B
215851089 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TMLE130D20MP11 | 43000 | 17 | 11 | 8.5 | 46500 | 35200 | 75.7% | 2 | 35600 | R-454B
215851164 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TP9C120D20MP13 | 41500 | 18 | 11.5 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215849783 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | CPLC080B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215849876 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8V080B12MP12 | 22200 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
215849935 | 1.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060A10MP12 | 20000 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18400 | R-454B
215849978 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9V040A10MP12 | 21000 | 16.5 | 10.5 | 8.5 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
215850042 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y080B12MP11 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18500 | 81.86% | 2 | 18500 | R-454B
215850092 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE100B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215850142 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES040A12SMPS1 | 20600 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
215850597 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ET080B12LMPS1 | 30600 | 19 | 11 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216764935 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8X1B060M4PTC | 32200 | 17.1 | 11.7 | 8.7 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216764942 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S8X2B080M4PTC | 32800 | 17.5 | 12 | 8.7 | 32200 | 24000 | 74.53% | 2.1 | 21200 | R-454B
216765003 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S8X2B080M4PSC | 32800 | 17.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
214336663 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V0755A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
215850522 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C16MP11 | 30800 | 18 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
207699007 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430U-18HFN1-M | MVC-18HWFN1-M |  | 18000 | 18 | 12.4 | 9.3 | 19000 | 16500 | 86.84% | 2.04 | 13500 | R-410A
215850197 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES060A10SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
215850217 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z9ES080B12SMPS1 | 22400 | 17 | 12 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216734187 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 935SB36040M17*** | 22200 | 16 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
215850499 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
212590801 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DD14936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215679705 | 2.8 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0802120B* | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215679755 | 2.8 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CTN0802120A* | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
216733605 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 927TA48060V17*** | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17500 | R-454B
216733784 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3014AM* | 926TC30040V14*** | 22000 | 15.5 | 10.5 | 8.1 | 20800 | 18900 | 90.87% | 1.9 | 17700 | R-454B
215940223 | 2.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0801716A* | 34000 | 19 | 11 | 9 | 34800 | 26400 | 75.86% | 1.92 | 30400 | R-454B
215940293 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CTN0601716A* | 35200 | 21 | 11.7 | 8.5 | 38500 | 29400 | 76.36% | 2 | 33400 | R-454B
215940443 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *97CTN0801716A* | 35400 | 21 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33200 | R-454B
215681315 | 3.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716B* | 44000 | 17 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.04 | 42500 | R-454B
214336690 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R951V0705A21M4S | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214336697 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R962V1005A21M4S | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215487472 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96VC0403BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215942635 | 2.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN0802120A* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
215932239 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CTL0702120B* | 32600 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
215932289 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CMN0601714B* | 32400 | 19 | 10.5 | 9.5 | 34400 | 26400 | 76.74% | 2.04 | 30200 | R-454B
214092347 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9E080B12MP12 | 31600 | 17.5 | 9.8 | 8.1 | 32400 | 44000 | 135.8% | 3.06 | 25400 | R-410A
214092965 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 32400 | 44500 | 137.3% | 3.05 | 25600 | R-410A
214092983 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.3 | 32400 | 45000 | 138.9% | 3.11 | 26000 | R-410A
214093065 | 2.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092230 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | LP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 46000 | 142% | 3.03 | 26400 | R-410A
214092265 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL8E060A12UH11 | 32800 | 18 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.04 | 26000 | R-410A
214092281 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E040A12MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.01 | 26000 | R-410A
215850201 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z9ES060B12SMPS1 | 22200 | 17 | 11.7 | 8.5 | 22800 | 18600 | 81.58% | 2 | 18800 | R-454B
215439670 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*97MC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215850269 | 2.6 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | CPLC100C16MP13 | 31200 | 18 | 11 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850337 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C16MP11 | 30800 | 18 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
215850485 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 31000 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
215850496 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215850510 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
214336704 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R98MV1155A24UPS | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214336679 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V1255A24UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336662 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V0755A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214336673 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V0755A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
216766598 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3+P0V0D000M50SD |  | 43500 | 17 | 12.5 | 9 | 44000 | 32200 | 73.18% | 2.24 | 29200 | R-454B
214092296 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.06 | 25800 | R-410A
215849800 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TL8E060A12UH11 | 20600 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
215849993 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V060B12MP12 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215588159 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 58TN*B070C17**16 | 48500 | 18 | 11.5 | 9.5 | 52000 | 51000 | 98.08% | 1.9 | 50000 | R-454B
215588345 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6021XMA*+UI | 59MN7C080C21**20 | 52000 | 19 | 11.5 | 8.1 | 53500 | 45500 | 85.05% | 1.9 | 48500 | R-454B
215850002 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9V080B12MP12 | 22400 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18400 | R-454B
215850036 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9Y080B12MP11 | 22200 | 17 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18700 | R-454B
215850111 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TP9C080B12MP13 | 22200 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
215850544 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215850560 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215681375 | 3.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN0802120B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215850127 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215850318 | 2.58 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
215850352 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850361 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850370 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y080C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
215850377 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y100C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
215850520 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE120C16MP11 | 30600 | 18 | 11 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
215848361 | 1.85 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR |  | 22200 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.76 | 18700 | R-454B
215849846 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E060A12MP11 | 20800 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216733436 | 1.92 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 916SA36060M14*** | 23000 | 15.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
216733854 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 8(0,1)*SB36070M17*** | 22200 | 16.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
216733904 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 82*SB48070V17*** | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216733554 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**2517AM* | 986TD42080C17*** | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216681009 | 2.9 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3621AL* | 927TA60080V21*** | 34800 | 16 | 9.8 | 8.5 | 38500 | 34800 | 90.39% | 1.75 | 29400 | R-410A
214336666 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V1005A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336667 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V1005A21UHU | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
211708482 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9V100C20MP12 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
215676635 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *95CSU0802120B* | 47500 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
215851354 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES100C20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
216734007 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 935CB48060C17*** | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
212624013 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLE080B12MP11 | 30200 | 17.5 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624018 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TMLE080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624038 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TMLE080B12MP11 | 30200 | 17.5 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624186 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9Y100C20MP11 | 33000 | 15.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624195 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624222 | 2.63 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLE040A12MP11 | 31600 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624270 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624327 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8E120C16MP11 | 32800 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624388 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624397 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624404 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM9Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624479 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624486 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624504 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | CPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213821455 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *92MSN0601714A* | 29000 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.77 | 23200 | R-410A
212624511 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624529 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624629 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8V100C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624638 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8Y100C16MP11 | 31600 | 18.4 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624688 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624695 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624697 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624745 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TPLC100C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
214336684 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802VA125524M | 52000 | 18.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50000 | R-410A
214336700 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R97MV1005A21DHS | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
212624765 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624788 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TL8E080C16UH11 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624838 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TL9E080C16UH11 | 32800 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624847 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TL9E080C16UH11 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624865 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TP9C100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 34000 | 27000 | 79.41% | 2.48 | 25200 | R-410A
212624879 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624904 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM8Y080C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624913 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624938 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625022 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8Y100C16MP11 | 33200 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625029 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM9V100C16MP12 | 29200 | 16.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625038 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625113 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627871 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TL8E080C16UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627880 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TL8E080C16UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
215932339 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *96CTN0601714B* | 32400 | 19.5 | 10.5 | 9.5 | 34200 | 26400 | 77.19% | 2.02 | 30200 | R-454B
215932459 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0601716B* | 33200 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
215931739 | 4.67 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0602120B* | 56000 | 18 | 10.5 | 8.5 | 61000 | 47500 | 77.87% | 2 | 49000 | R-454B
212989158 | 1.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *95MSU0601716A* | 23600 | 17 | 10 | 8.5 | 26400 | 24600 | 93.18% | 2.04 | 19100 | R-410A
212989206 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *95MSU0601716A* | 24200 | 17.5 | 10.5 | 8.5 | 25200 | 21600 | 85.71% | 1.82 | 18700 | R-410A
215932189 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0401712A* | 32600 | 20 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2 | 30800 | R-454B
216765948 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3 | S8V2B080M4PCB | 23200 | 17.1 | 12.5 | 8.7 | 21800 | 17200 | 78.9% | 2.02 | 15300 | R-454B
216765966 | 1.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3 | S9X2B060D3PSB | 22200 | 16 | 12 | 8.7 | 21200 | 16900 | 79.72% | 2.02 | 15000 | R-454B
216766100 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S9X1B080D4PSB | 32400 | 16 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.05 | 21400 | R-454B
216766102 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S9X1B060D3PSB | 33200 | 17 | 12 | 8.5 | 33400 | 24400 | 73.05% | 2.09 | 21600 | R-454B
215851178 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216766118 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S8V2B080M4PDB | 33000 | 16.5 | 12 | 8.5 | 33200 | 24400 | 73.49% | 2.09 | 21400 | R-454B
212627905 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.4 | 34000 | 30200 | 88.82% | 2.83 | 27000 | R-410A
212627912 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627955 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8Y100C16MP11 | 29200 | 17.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627987 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627996 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628007 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628023 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TL9E100C20UH11 | 32400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
216766582 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S9X1D120U5PSB | 43500 | 16 | 12 | 9 | 44500 | 32600 | 73.26% | 2.23 | 29800 | R-454B
216766814 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S9V2B060U4VSB | 23800 | 17.5 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2.07 | 15500 | R-454B
216766848 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S9X1B040U3PSB | 23200 | 16.5 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2.01 | 15300 | R-454B
216679867 | 3.03 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4321AL* | 927TA48080V17*** | 36400 | 15.5 | 10 | 9 | 38500 | 34400 | 89.35% | 1.96 | 29200 | R-410A
212628032 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8Y100C20MP11 | 32600 | 18 | 9 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628037 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628046 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TL8E100C20UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625165 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TL9E100C20UH11 | 32800 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625256 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TL8E100C20UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625258 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TL8E100C20UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625338 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625349 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
216766166 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S9X2C080U5PSB | 34200 | 17.1 | 12 | 9 | 33000 | 24400 | 73.94% | 2.21 | 21600 | R-454B
216766266 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*DD10AS3 | S8V2D120M5PCB | 34000 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.21 | 21200 | R-454B
216766318 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S8V2A040M3PCB | 32800 | 16 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.14 | 21400 | R-454B
216766332 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9X1B060U4PSB | 33600 | 16.5 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.18 | 21400 | R-454B
216766336 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9X2B060D3PSB | 31400 | 16 | 11.2 | 8.7 | 31600 | 23600 | 74.68% | 2.14 | 21000 | R-454B
216766350 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 | S9V2C100U5VSB | 32200 | 16 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.12 | 21000 | R-454B
216766368 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | S9X2C080U5PSB | 34200 | 17.1 | 12 | 9 | 33000 | 24400 | 73.94% | 2.2 | 21600 | R-454B
215588443 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*4812AM*+UI | 58CU*B060C17**16 | 48500 | 18 | 11.5 | 11.5 | 51500 | 50500 | 98.06% | 1.96 | 49500 | R-454B
215588493 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6024XMA*+UI | 59TN7A120C24**22 | 52000 | 19 | 12 | 8.1 | 52500 | 46500 | 88.57% | 1.9 | 48000 | R-454B
212625399 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625440 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625608 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TPLC120C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625622 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9V120D20MP12 | 29800 | 16.4 | 9 | 8.5 | 32200 | 28000 | 86.96% | 2.79 | 25200 | R-410A
212625672 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625676 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CPLC100C20MP13 | 32600 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625701 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625708 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8V100C20MP12 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625756 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TMLV120C20MP12 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625767 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625783 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TPLC120C20MP13 | 32400 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625824 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CP9C120D20MP13 | 29800 | 16.4 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.52 | 25200 | R-410A
212625826 | 2.4 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9V120D20MP12 | 28800 | 16.1 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.79 | 25200 | R-410A
212625831 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TP9C120D20MP13 | 29800 | 16.4 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.52 | 25200 | R-410A
215932659 | 2.87 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712A* | 34400 | 20.5 | 11.7 | 9 | 34600 | 26200 | 75.72% | 1.94 | 30200 | R-454B
212625833 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625915 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V040A10MP12 | 32000 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625926 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625958 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9E100C20MP12 | 32800 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626033 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626035 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626042 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626049 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8Y060A12MP11 | 33400 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
216766896 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3+P0V0A000M30SD |  | 31800 | 15.5 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.08 | 21200 | R-454B
216766900 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S9X2B040U3PSB | 33800 | 17 | 11.7 | 8.7 | 33000 | 24600 | 74.55% | 2.16 | 21800 | R-454B
212626051 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8Y080B12MP11 | 30600 | 17.6 | 9 | 8.4 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
212626201 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.64 | 26400 | R-410A
212626233 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.63 | 26400 | R-410A
212626326 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.1 | 33600 | 29000 | 86.31% | 2.72 | 26200 | R-410A
212626353 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM9Y080C16MP11 | 31200 | 18.3 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.6 | 25600 | R-410A
212626376 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM8Y080C16MP11 | 29800 | 17.8 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.63 | 25200 | R-410A
212626408 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8Y120C20MP11 | 32200 | 18 | 9.5 | 8.3 | 33600 | 30000 | 89.29% | 2.81 | 26800 | R-410A
212626533 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.2 | 33800 | 29200 | 86.39% | 2.65 | 26400 | R-410A
212626669 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9E060A10MP12 | 32200 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626676 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9E060A10MP12 | 33000 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626687 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.68 | 25800 | R-410A
212626726 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM9E080B12MP12 | 29400 | 16.7 | 9.4 | 8.4 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
212626787 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8E100C16MP11 | 30800 | 17.9 | 9.8 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626803 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8E120C16MP11 | 32000 | 18 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626812 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8Y080C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
212626969 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLE100B12MP11 | 32800 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626978 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212626985 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.2 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212627085 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627087 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627121 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9Y080C16MP11 | 32200 | 18.5 | 9.4 | 8.5 | 33800 | 28200 | 83.43% | 2.67 | 25800 | R-410A
212627126 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TL9E100C20UH11 | 32400 | 17 | 10 | 8.4 | 33800 | 28800 | 85.21% | 2.79 | 26200 | R-410A
212627128 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TL8E100C20UH11 | 31800 | 17.5 | 9.9 | 8.4 | 33800 | 27200 | 80.47% | 2.64 | 25200 | R-410A
212627130 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.4 | 33800 | 27200 | 80.47% | 2.64 | 25200 | R-410A
215681405 | 3.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN0802120A* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215681675 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
212627146 | 2.63 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TL8E080C16UH11 | 31600 | 17.5 | 9.8 | 8.5 | 33800 | 27800 | 82.25% | 2.68 | 25600 | R-410A
212627171 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | CP9C100C20MP13 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
212627246 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TL9E060B12UH11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627255 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TL9E060B12UH11 | 33000 | 18 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627285 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9E060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627287 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627312 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627321 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
213205065 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN1002120A* | 22400 | 16.7 | 10 | 8.4 | 25200 | 19900 | 78.97% | 2.91 | 18600 | R-410A
214092382 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9Y060B12MP11 | 32600 | 17.5 | 9.5 | 8.1 | 32400 | 46000 | 142% | 3.01 | 26400 | R-410A
212626864 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626866 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8E120C16MP11 | 31000 | 17.9 | 9.8 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626949 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TMLE060A12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626967 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TMLE100B12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
214243999 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CNPV*3017AL*+UI | 59TN6C040C14**10 | 22800 | 17.5 | 12 | 9.5 | 27000 | 20600 | 76.3% | 2.28 | 25600 | R-410A
212977022 | 2.53 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X37L21A* | *96VTN1002122B* | 30400 | 15.2 | 9 | 8.1 | 33400 | 26400 | 79.04% | 1.84 | 23200 | R-410A
215932489 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0801714B* | 33200 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30800 | R-454B
215932589 | 2.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU1002122B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.04 | 29600 | R-454B
215932809 | 2.87 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN1002122B* | 34400 | 20.5 | 12 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 30000 | R-454B
215933109 | 2.78 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0902120B* | 33400 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215933609 | 2.8 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU0601716B* | 33600 | 19 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 30800 | R-454B
215934079 | 3.54 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0801714B* | 42500 | 20 | 11 | 9 | 48500 | 35200 | 72.58% | 2 | 35800 | R-454B
215681305 | 3.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0401712B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.04 | 42500 | R-454B
215681355 | 3.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0802120A* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.06 | 42500 | R-454B
212626980 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212626998 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM8V100C16MP12 | 31800 | 17.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212627014 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM9Y080C16MP11 | 31800 | 18.5 | 9.4 | 8.4 | 33800 | 27800 | 82.25% | 2.64 | 25600 | R-410A
212627033 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | CP9C080C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627034 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627047 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CP9C080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627067 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9V080C16MP12 | 30400 | 17 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627080 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627328 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | CP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627369 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627405 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TL8E060A12UH11 | 32800 | 18 | 9.5 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212627430 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8E080B12MP11 | 32400 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627462 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9Y080B12MP11 | 33600 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627464 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TMLE080B12MP11 | 29200 | 17.2 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627478 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TMLE080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627494 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8V060A12MP12 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
211708498 | 3.75 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TMLE080C16MP11 | 45000 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.11 | 30200 | R-410A
216766825 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD04AS3 | S9X1B060D3PSB | 23400 | 17.1 | 12.5 | 8.1 | 22200 | 17200 | 77.48% | 1.84 | 15400 | R-454B
212627521 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212627544 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y100C20MP11 | 32800 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627553 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9Y100C20MP11 | 30800 | 15.2 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627589 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212627594 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9E080C16MP12 | 32200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212627596 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212627619 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8V080C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627648 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216764739 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S8X2B060M4PSC | 33600 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
213355429 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E6 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
216764937 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S8X2B060M4PSC | 33600 | 17.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216764970 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S8X2C100M5PTC | 33400 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216765087 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | S8X2C080M5PTC | 51500 | 16 | 11 | 9 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
216765104 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*DD10AS3 | S8X2C100M5PSC | 51000 | 16 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.1 | 34000 | R-454B
216765122 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TXCD010AS3 | S8X1C100M5PTC | 52500 | 16.5 | 11 | 9 | 51000 | 38500 | 75.49% | 2.1 | 34200 | R-454B
212627083 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627100 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TL9E100C20UH11 | 32000 | 17 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.77 | 26200 | R-410A
212627117 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TL9E080C16UH11 | 31800 | 17.5 | 9.4 | 8.4 | 33800 | 27800 | 82.25% | 2.63 | 25600 | R-410A
212627132 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9V100C16MP12 | 30200 | 17 | 9 | 8.4 | 33800 | 27200 | 80.47% | 2.64 | 25200 | R-410A
212627233 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212627282 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9E060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627315 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | CP9C060B12MP13 | 29800 | 16.9 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627317 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627655 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y080C16MP11 | 32800 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627662 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9Y080C16MP11 | 32600 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627671 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TMLE120C16MP11 | 32400 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212627687 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM9V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627696 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | CPLC080C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627703 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627728 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627730 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
215935760 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *96CTN0601714B* | 34000 | 20.5 | 11 | 8.1 | 38000 | 27000 | 71.05% | 1.95 | 30400 | R-454B
215931500 | 2.87 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | FCMA5B48L0C*+WALLCON |  | 34400 | 21.5 | 12.5 | 9.5 | 34200 | 25800 | 75.44% | 2.06 | 29800 | R-454B
215932159 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X37M17A*+WALLCON | *96CTN0601714B* | 33200 | 19 | 10.5 | 9.5 | 34400 | 26400 | 76.74% | 2.06 | 30400 | R-454B
215933579 | 2.8 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0901716B* | 33600 | 19.5 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215933699 | 2.78 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN0601714B* | 33400 | 19 | 11 | 9 | 34200 | 26000 | 76.02% | 1.94 | 30000 | R-454B
215933849 | 2.85 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU1002122B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 25800 | 75.44% | 1.96 | 29800 | R-454B
215934649 | 2.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X30M17A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
212627351 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9V060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627367 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627368 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627381 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8E080B12MP11 | 32200 | 18 | 9.4 | 8.4 | 34000 | 28000 | 82.35% | 2.6 | 25800 | R-410A
212627418 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8E080B12MP11 | 29200 | 17.2 | 8.9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627431 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8E080B12MP11 | 30200 | 17.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627449 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9Y080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627451 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627762 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8V080C16MP12 | 33400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627780 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8V100C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627823 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627830 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TPLC080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627832 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627846 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627853 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TPLC100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
216766883 | 1.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9X1B040D3PSB | 22400 | 16 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2 | 15100 | R-454B
212627482 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TMLE080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627518 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | CP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212627550 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9Y100C20MP11 | 32600 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627582 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212627583 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212627651 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627665 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9Y080C16MP11 | 30800 | 18.2 | 9.2 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627666 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9Y080C16MP11 | 33400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627685 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8Y100C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627818 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627819 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627834 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TPLC080C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627850 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627869 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TL8E080C16UH11 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627899 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL9E080C16UH11 | 32600 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627901 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TL9E080C16UH11 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
215681965 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *97CTN1002122A* | 48000 | 19 | 10.5 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215682335 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU1002120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
215682385 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CSU0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36200 | 72.4% | 2.12 | 46000 | R-454B
215682485 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN0801716A* | 48000 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 2 | 47000 | R-454B
212628002 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628020 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TP9C100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628120 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628133 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212623991 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9Y080B12MP11 | 33000 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624009 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TMLE080B12MP11 | 29200 | 17.2 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624122 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624157 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TP9C080B12MP13 | 31800 | 17 | 9 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624176 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9Y100C20MP11 | 30800 | 15.2 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624189 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9Y100C20MP11 | 33000 | 15.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624208 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8E080C16MP11 | 32600 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212624275 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM8E120C16MP11 | 31400 | 18 | 9.9 | 8.4 | 34000 | 28800 | 84.71% | 2.77 | 26200 | R-410A
212624309 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.76 | 26000 | R-410A
212624390 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9Y080C16MP11 | 30600 | 18.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624391 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM9Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624407 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624426 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8E120C16MP11 | 32400 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624442 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212624473 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | CPLC080C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624477 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624493 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624509 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624540 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | CPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624575 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8V080C16MP12 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624608 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624641 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9V100C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624643 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624726 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624825 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TL9E080C16UH11 | 30000 | 17 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624860 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM8Y080C16MP11 | 29800 | 17.8 | 9.5 | 8.5 | 34000 | 27000 | 79.41% | 2.66 | 25200 | R-410A
212624878 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | CP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624909 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624910 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624926 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8Y080C16MP11 | 33000 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624928 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624976 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625010 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625043 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625058 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625059 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM9V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625175 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TL9E100C20UH11 | 32800 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625177 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625192 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8Y100C20MP11 | 32600 | 18 | 9 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625210 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8Y120C20MP11 | 32200 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625261 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TL8E100C20UH11 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625376 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625396 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9V100C20MP12 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625445 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
216770089 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*CD07AS3 | *DHMC100CCV4 | 23400 | 17.1 | 12.7 | 8.5 | 22000 | 17100 | 77.73% | 1.92 | 15300 | R-454B
212627864 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TL8E080C16UH11 | 29600 | 16.9 | 9.5 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
216766890 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S9X2B040U3PSB | 32200 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216766940 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9X2B040D3PSB | 32800 | 16.5 | 11.7 | 8.5 | 33200 | 24400 | 73.49% | 2.06 | 21600 | R-454B
216766963 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S9V2C100D5VSB | 31400 | 15.2 | 11.2 | 8.7 | 31600 | 23600 | 74.68% | 2.15 | 21000 | R-454B
216766990 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3+P0V0C000M50SD |  | 34200 | 17.1 | 12 | 8.7 | 33400 | 24400 | 73.05% | 2.14 | 21600 | R-454B
216766999 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8V2C080M5PCB | 34200 | 17 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
212625593 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TMLV120C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625612 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM9V120D20MP12 | 31400 | 16.9 | 9.3 | 8.4 | 32200 | 28000 | 86.96% | 2.77 | 25200 | R-410A
212625613 | 2.4 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM9Y120D20MP11 | 28800 | 15.6 | 8.9 | 8.5 | 32200 | 28000 | 86.96% | 2.77 | 25200 | R-410A
212625643 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8V100C20MP12 | 28600 | 15.6 | 8.4 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625660 | 2.42 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TPLC120C20MP13 | 29000 | 15.8 | 8.5 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625662 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TPLC120C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625678 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | CPLC100C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625680 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | CPLC100C20MP13 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
215934629 | 2.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X25M17A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
215934729 | 2.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X36M17A*+WALLCON | *96CTN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
216738983 | 1.92 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | FCMA5B36L0C*+WALLCON |  | 23000 | 16.5 | 11 | 8.5 | 21000 | 18800 | 89.52% | 1.96 | 17700 | R-454B
216734490 | 1.85 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80CTL0701412B* | 22200 | 16.5 | 11 | 8.1 | 20800 | 18600 | 89.42% | 1.85 | 17500 | R-454B
216734773 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96CTN0801714B* | 22200 | 16.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
216735023 | 1.9 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80CTL0451712B* | 22800 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216735641 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80CTL1102120B* | 23600 | 15.5 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.96 | 17700 | R-454B
215439651 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80TC0803B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
208101909 | 1.5 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430U-18HFN1-M | MAC-24HWDN1-MN0 |  | 18000 | 16.1 | 11.7 | 9.5 | 19000 | 15000 | 78.95% | 2.2 | 14700 | R-410A
212628063 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TL8E100C20UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628081 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628088 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628097 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212627920 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627929 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | CP9C100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625727 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8V120C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625729 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V120C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625810 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y120D20MP11 | 32400 | 16.5 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625811 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y120D20MP11 | 32000 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625830 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TP9C120D20MP13 | 29800 | 16.4 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.52 | 25200 | R-410A
212625860 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9V120D20MP12 | 32000 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
216735709 | 1.9 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *97CMN0601714B* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
216736144 | 1.92 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80CSU1002120A* | 23000 | 15.2 | 10 | 8.5 | 21800 | 19500 | 89.45% | 1.96 | 18400 | R-454B
216734372 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0451714A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734804 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VTN0601412B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734923 | 1.9 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80MS(N,L)0701412A* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17500 | R-454B
216735673 | 1.93 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80VTL1102122B* | 23200 | 16 | 11 | 8.5 | 20600 | 18500 | 89.81% | 1.96 | 17500 | R-454B
216737013 | 1.87 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MS(N,L)0451412A* | 22400 | 15.2 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.9 | 17700 | R-454B
212627963 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8Y100C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627979 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628004 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628013 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628031 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TL8E100C20UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
212628040 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628054 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TL8E100C20UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628056 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL8E100C20UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625864 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9V120D20MP12 | 32400 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625913 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V040A10MP12 | 31600 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625945 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212625947 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9E100C20MP12 | 32400 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212625964 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9E100C20MP12 | 31000 | 15.2 | 9.7 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626061 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8Y100C20MP11 | 31200 | 17.9 | 9.3 | 8.1 | 33400 | 29800 | 89.22% | 2.75 | 26600 | R-410A
212626328 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9V080C16MP12 | 29800 | 16.9 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.6 | 25200 | R-410A
212626346 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM9V080C16MP12 | 31800 | 17.5 | 9.9 | 8.3 | 33600 | 27600 | 82.14% | 2.63 | 25400 | R-410A
216767008 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*D008AS3 | S8V2D120M5PCB | 34200 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.21 | 21400 | R-454B
216767024 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S9X1B040U3PSB | 32200 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
212628055 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TL8E100C20UH11 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628082 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628096 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628112 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9V100C20MP12 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628130 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628132 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212624010 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624012 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TMLE080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624080 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8V060A12MP12 | 31600 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624146 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9V080B12MP12 | 31800 | 17 | 9 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624155 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TP9C080B12MP13 | 31400 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624187 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9Y100C20MP11 | 32600 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624246 | 2.65 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8E080C16MP11 | 31800 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212624280 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.77 | 26200 | R-410A
212626362 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9E100C16MP12 | 32400 | 18 | 9.9 | 8.4 | 33600 | 27200 | 80.95% | 2.64 | 25200 | R-410A
212626397 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9E100C16MP12 | 33200 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626398 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E100C16MP12 | 32800 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626549 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8E080B12MP11 | 31400 | 17.8 | 9.3 | 8.2 | 33800 | 27800 | 82.25% | 2.56 | 25600 | R-410A
212626649 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.3 | 33800 | 29600 | 87.57% | 2.7 | 26600 | R-410A
212626665 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9E060A10MP12 | 32200 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626680 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM8E080B12MP11 | 31800 | 17.9 | 9.4 | 8.3 | 33800 | 28200 | 83.43% | 2.59 | 25800 | R-410A
212626731 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8E080C16MP11 | 30800 | 17.9 | 9.8 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
215934669 | 2.9 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X31M17A*+WALLCON | *97CMN0601714B* | 34800 | 20.5 | 11.5 | 8.5 | 38000 | 28000 | 73.68% | 2.08 | 31800 | R-454B
215931659 | 4.67 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0701716B* | 56000 | 18 | 11 | 8.5 | 61000 | 45500 | 74.59% | 2.1 | 46500 | R-454B
215931709 | 4.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1102120B* | 57000 | 19 | 11.5 | 8.5 | 60500 | 46500 | 76.86% | 2.02 | 47500 | R-454B
215679825 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN0801716A* | 33800 | 16 | 9 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215679875 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0401712B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
213821161 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0802120B* | 23800 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
212624310 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.76 | 26000 | R-410A
212624380 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TL8E080C16UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27800 | 81.76% | 2.66 | 25600 | R-410A
212624389 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624419 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9Y080C16MP11 | 30600 | 18.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624480 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | CPLC080C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624496 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | CPLC080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624562 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8V080C16MP12 | 29200 | 16.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624578 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8V080C16MP12 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624598 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8V080C16MP12 | 33400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624605 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624621 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8V100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624623 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624696 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624698 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624739 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624837 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
215677685 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN0602120B* | 56500 | 18 | 8.5 | 9 | 65000 | 46000 | 70.77% | 2.06 | 57000 | R-454B
215677885 | 4.54 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0701716B* | 54500 | 18 | 9 | 8.5 | 58500 | 41500 | 70.94% | 1.92 | 50500 | R-454B
216766860 | 1.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S9X1B060D3PSB | 21800 | 15.5 | 11.5 | 8.5 | 21200 | 16900 | 79.72% | 1.95 | 15100 | R-454B
211599531 | 3.25 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B42T21 | LEM48C4 |  | 39000 | 16 | 12.5 | 8.1 | 40500 | 29000 | 71.6% | 3.33 | 28200 | R-410A
216733971 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 88*TB48090C17*** | 22000 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17500 | R-454B
216766909 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S8V2A040M3PCB | 32800 | 16 | 11.7 | 8.7 | 32400 | 24200 | 74.69% | 2.13 | 21200 | R-454B
216766911 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S8V2B080M4PDB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
212624846 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TL9E080C16UH11 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624887 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624946 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM8Y080C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624948 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8Y080C16MP11 | 33200 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625046 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM9V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625089 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TP9C100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625130 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625157 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TL9E100C20UH11 | 32000 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
216766927 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S9X2B060D3PSB | 32800 | 16 | 11.2 | 8.1 | 33600 | 24800 | 73.81% | 1.98 | 21800 | R-454B
216766929 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S9X1B080D4PSB | 32400 | 16 | 11.5 | 8.1 | 33400 | 24600 | 73.65% | 1.96 | 21600 | R-454B
216766960 | 2.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S9X2C100U5PSB | 33600 | 15.2 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216766961 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S8V2C080M5PCB | 33800 | 16.5 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.18 | 21400 | R-454B
216767026 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S8V2B080M4PCB | 32000 | 16 | 11.7 | 8.5 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216767059 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3 | S8V2C080M5PCB | 32400 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.11 | 21200 | R-454B
216767060 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3+P0V0C000M50SD |  | 32800 | 16.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
212625223 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8Y120C20MP11 | 33000 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625300 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212625339 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | CP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625350 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | CP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625432 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TP9C100C20MP13 | 29600 | 16.9 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625516 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8V120C20MP12 | 28600 | 15.6 | 8.4 | 8.5 | 32000 | 27600 | 86.25% | 2.71 | 25000 | R-410A
212625598 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TPLC100C20MP13 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625625 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TP9C120D20MP13 | 29800 | 16.4 | 9 | 8.1 | 32200 | 28000 | 86.96% | 2.51 | 25200 | R-410A
212625648 | 2.42 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8V120C20MP12 | 29000 | 15.8 | 8.5 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
212625682 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625725 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8V120C20MP12 | 31400 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625739 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625759 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625782 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625809 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9Y120D20MP11 | 29800 | 15.9 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625825 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | CP9C120D20MP13 | 29800 | 16.4 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.52 | 25200 | R-410A
212625832 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625857 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9V120D20MP12 | 31600 | 17 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625875 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625909 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8Y080B12MP11 | 31600 | 17.8 | 9.8 | 8.2 | 33200 | 27000 | 81.33% | 2.57 | 25000 | R-410A
212625923 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9V040A10MP12 | 31800 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625943 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626032 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8Y060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626043 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8Y060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626050 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8Y080B12MP11 | 29600 | 17.3 | 9.4 | 8.4 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
212626216 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8E080C16MP11 | 30800 | 17.9 | 9.8 | 8.1 | 33600 | 28200 | 83.93% | 2.65 | 25800 | R-410A
212626266 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626309 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM9V080C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33600 | 27200 | 80.95% | 2.58 | 25200 | R-410A
212626316 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9E080B12MP12 | 30400 | 17 | 9 | 8.4 | 33600 | 27600 | 82.14% | 2.61 | 25400 | R-410A
212626336 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626377 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM8Y100C16MP11 | 29800 | 17.8 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.63 | 25200 | R-410A
212626650 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.3 | 33800 | 29600 | 87.57% | 2.7 | 26600 | R-410A
212626659 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9E060A10MP12 | 29600 | 16.9 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626677 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9E060A10MP12 | 31000 | 17.3 | 9.2 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626770 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8V080C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.62 | 25200 | R-410A
212626802 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8E120C16MP11 | 32000 | 18 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626809 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9V080B12MP12 | 31000 | 17 | 9.4 | 8.4 | 33800 | 29600 | 87.57% | 2.74 | 26600 | R-410A
212626820 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8E100B12MP11 | 32400 | 18 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212626884 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626902 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8E060A12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626918 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626945 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE060A12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626963 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE100B12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626970 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TMLE100B12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212627102 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30200 | 89.35% | 2.82 | 27000 | R-410A
212627120 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9Y080C16MP11 | 30200 | 17.9 | 9 | 8.4 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
212627222 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CPLC080B12MP13 | 31600 | 17 | 9 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212627270 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9E060B12MP12 | 29400 | 16.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627277 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9E060B12MP12 | 33000 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627279 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9E060B12MP12 | 30400 | 17 | 9.1 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627322 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627352 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V060B12MP12 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627395 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9Y100C16MP11 | 31200 | 18 | 9.9 | 8.4 | 34000 | 28400 | 83.53% | 2.72 | 26000 | R-410A
212627429 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E080B12MP11 | 32400 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627436 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8E080B12MP11 | 30600 | 17.7 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627456 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9Y080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
216766787 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S8V2A040M3PDB | 23200 | 16.5 | 12 | 8.7 | 21800 | 17300 | 79.36% | 2.01 | 15400 | R-454B
216734247 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 926TC36040V17*** | 22000 | 15.5 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.9 | 17600 | R-454B
212219659 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-17HFN1-MT0W-L | MVC-18HWFN1-MW(GA) |  | 18000 | 17.6 | 11.7 | 9.6 | 19000 | 17000 | 89.47% | 2 | 15400 | R-410A
216766803 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S8V2A040M3PDB | 23800 | 17.5 | 12.7 | 9 | 22000 | 17500 | 79.55% | 2.06 | 15600 | R-454B
216766885 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S8V2B060M4PDB | 23600 | 17.1 | 12.7 | 8.7 | 21800 | 17300 | 79.36% | 2.03 | 15400 | R-454B
216766886 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S9X1B060U4PSB | 32000 | 16 | 11.7 | 8.5 | 32200 | 23800 | 73.91% | 2.09 | 21000 | R-454B
216766887 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S9X1B080U4PSB | 32200 | 16 | 11.7 | 8.5 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
212627479 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TMLE080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627497 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212627502 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TMLV060A12MP12 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212627504 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLV060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212627545 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y100C20MP11 | 32400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627561 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212627581 | 2.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8E080C16MP11 | 32200 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212627586 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TMLE080C16MP11 | 32200 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
216765026 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCD008AS3 | S8X2D120M5PSC | 33000 | 17.5 | 12 | 9 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216765035 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*CD09AS3 | S8X1C080M5PTC | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.1 | 29200 | R-454B
216765076 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCD010AS3 | S8X2C080M5PTC | 44000 | 17 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29400 | R-454B
216737113 | 1.9 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MS(N,L)1102120A* | 22800 | 15.2 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.9 | 17800 | R-454B
216737248 | 1.87 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MSU1002120A* | 22400 | 15.5 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17800 | R-454B
215934479 | 3.71 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL1352422B* | 44500 | 20.5 | 11 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
212977591 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X25L17A* | *80MS(N,L)0451412A* | 24200 | 17 | 10 | 8.5 | 25200 | 21800 | 86.51% | 1.82 | 18700 | R-410A
212627595 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212627620 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8V080C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627636 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8V080C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.68 | 25400 | R-410A
212627661 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9Y080C16MP11 | 33200 | 18.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627686 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627697 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627722 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | CPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627745 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8V080C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212626732 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626733 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626780 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM9E080B12MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212626782 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9E080B12MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212626797 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8E080C16MP11 | 32200 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.73 | 26000 | R-410A
212626814 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM9V100C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
212626833 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9E080B12MP12 | 29400 | 16.7 | 9.4 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626847 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9E080B12MP12 | 33000 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
216765101 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*DD10AS3 | S8X2D120M5PTC | 51000 | 16 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.1 | 34000 | R-454B
215681815 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215681865 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN0801716A* | 47500 | 18.5 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215681365 | 3.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN1002122A* | 44000 | 18 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.04 | 42500 | R-454B
215681415 | 3.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1002122A* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 41500 | R-454B
213815137 | 2.82 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CSCF3642N6D*+MBVK12BP1X00A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213815138 | 2.82 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CSCF3642N6D*+MBVK16CP1X00A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214572763 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X43L21A*+WALLCON | *96CTN0802120B* | 33000 | 18.5 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 2 | 31600 | R-410A
214572833 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X48L24A*+WALLCON | *80CTL0702120B* | 32400 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214572963 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L21A*+WALLCON | *95CSU0802120B* | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 25000 | 78.12% | 2 | 31200 | R-410A
214572983 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L21A*+WALLCON | *97CMN0602120B* | 33000 | 17.5 | 11 | 8.5 | 32200 | 25000 | 77.64% | 1.98 | 31400 | R-410A
214573063 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L24A*+WALLCON | *96CTN0802120B* | 33200 | 18.5 | 11.5 | 8.5 | 31800 | 24800 | 77.99% | 2.02 | 31200 | R-410A
212627772 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627779 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627831 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627847 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627865 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TL8E080C16UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627872 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TL8E080C16UH11 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
216766791 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S9X2B040D3PSB | 21600 | 15.5 | 11.5 | 8.5 | 21200 | 16800 | 79.25% | 1.92 | 15000 | R-454B
216766830 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S9X1B080D4PSB | 23600 | 16.5 | 12.7 | 8.5 | 22200 | 17300 | 77.93% | 1.95 | 15400 | R-454B
215681915 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0601716B* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215682015 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN1002122A* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
215682065 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *97CTN0802120A* | 48500 | 19 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
215682085 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *97CTN1202422A* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
207825914 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430U-24HFN1-MR0 | MVC-24HWFN1-M |  | 24000 | 17 | 10.5 | 9.2 | 26000 | 19400 | 74.62% | 2.1 | 21000 | R-410A
215682115 | 3.92 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M21A*+WALLCON | *80CSU0601716B* | 47000 | 18 | 9.5 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
212627890 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TL9E080C16UH11 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212623694 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TL9E060B12UH11 | 33400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623762 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9E060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623819 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | CP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623837 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | CP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623921 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM9Y100C16MP11 | 31200 | 18 | 9.9 | 8.4 | 34000 | 28400 | 83.53% | 2.72 | 26000 | R-410A
212623937 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TL8E060A12UH11 | 32800 | 18 | 9.5 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212623676 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
215865884 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBC-36HWFPN10-MC3E |  | 36000 | 17.4 | 11.7 | 10.3 | 37000 | 39000 | 105.4% | 1.9 | 31800 | R-454B
209960481 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE31U-36HFN1-MR0 | MVC-36HWFN1-MR0 |  | 36000 | 16 | 10 | 9.5 | 40000 | 34600 | 86.5% | 1.95 | 30400 | R-410A
213351327 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | PE(S,T)354 |  | 23000 | 15.3 | 9.3 | 8.5 | 25400 | 22600 | 88.98% | 2.82 | 20200 | R-410A
213479413 | 2.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN1-M3X | MVC-36HWFN1-M |  | 35000 | 16.3 | 11.7 | 9.5 | 39000 | 38000 | 97.44% | 1.8 | 31800 | R-410A
215677105 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *80CTL0702120B* | 56000 | 18 | 9 | 9 | 63500 | 45000 | 70.87% | 2.06 | 56000 | R-454B
209960480 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30U-30HFN1-MP0-Q1W | MVC-30HWFN1-MQ1W |  | 30000 | 16 | 10.1 | 9.1 | 34000 | 28400 | 83.53% | 1.8 | 21000 | R-410A
213386475 | 2.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-36HFN1-M3X | MVB-36B23T4N1 |  | 35000 | 15.2 | 10 | 8.5 | 36000 | 30000 | 83.33% | 1.8 | 27000 | R-410A
215439637 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96TC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439646 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80TC0805C*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216766925 | 2.7 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3+P0V0A000M30SD |  | 32400 | 15.5 | 11.5 | 8.1 | 33600 | 24600 | 73.21% | 1.96 | 21800 | R-454B
216766930 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8V2B060M4PDB | 32600 | 16 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.98 | 21600 | R-454B
216766932 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9X1B080D4PSB | 33200 | 16 | 11.7 | 8.5 | 33400 | 24600 | 73.65% | 2.08 | 21600 | R-454B
216766980 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S9X2C080U5PSB | 34400 | 17.1 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.21 | 21400 | R-454B
216679903 | 2.97 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CSPH*4212AL* | 927TA48080V17*** | 35600 | 15.2 | 9.8 | 8.5 | 38500 | 34600 | 89.87% | 1.8 | 29200 | R-410A
211708445 | 3.79 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM8V080C16MP12 | 45500 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.14 | 30200 | R-410A
214389311 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4824AL*+UI | 987MC66120C24*** | 33800 | 19.5 | 12 | 9 | 36600 | 26000 | 71.04% | 2.02 | 31400 | R-410A
213355443 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430U-24HFN1-MR0 | MVBE-24HWFN1-MM3E |  | 24000 | 17 | 10.5 | 10.2 | 26000 | 19400 | 74.62% | 2.33 | 19500 | R-410A
213782201 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X48AAL+WALLCON | *96CTN1202422B* | 32600 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31400 | R-410A
215681725 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0802120A* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
208101910 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-24HFN1-MW | MAC-24HWDN1-MN0 |  | 24000 | 16.5 | 10.7 | 9.5 | 25000 | 20000 | 80% | 1.95 | 21000 | R-410A
212219660 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MU0W-L | MVC-23HWFN1-M |  | 23000 | 18.4 | 11.7 | 9.1 | 26000 | 21200 | 81.54% | 1.9 | 16900 | R-410A
209960479 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-17HFN1-MT0Q1W | MVC-18HWFN1-MQ1W |  | 18000 | 17.5 | 11.7 | 10 | 20000 | 18000 | 90% | 2.13 | 15000 | R-410A
211708495 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM9Y120D20MP11 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.1 | 30400 | R-410A
211708511 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TMLE120C20MP11 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.07 | 30600 | R-410A
216766696 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3+P0V0D000M50SD |  | 51500 | 15.2 | 11.2 | 9 | 50500 | 38000 | 75.25% | 2.21 | 33600 | R-454B
216766764 | 4.38 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S9X2C100U5PSB | 52500 | 15.2 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.21 | 34400 | R-454B
216767047 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X1B080U4PSB | 33200 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.16 | 21200 | R-454B
216770105 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8X2C100M5PTC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
215681425 | 3.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1202422A* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 41500 | R-454B
212380509 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE9J936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215931509 | 3.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | FCMA5B60L0D*+WALLCON |  | 46500 | 23 | 12.5 | 9.5 | 48000 | 35600 | 74.17% | 1.98 | 39000 | R-454B
216620311 | 3.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBM-60D28T6N10 |  | 47000 | 15.2 | 10 | 8.1 | 58000 | 43000 | 74.14% | 1.83 | 36000 | R-454B
216621508 | 4.33 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBM-60C28T6N10 |  | 52000 | 16 | 10 | 8.5 | 56000 | 45000 | 80.36% | 1.8 | 37800 | R-454B
215942555 | 3 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *80CSU1002120A* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
215934769 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X43M21A*+WALLCON | *96CTN0601714B* | 34600 | 20.5 | 11.5 | 8.5 | 38000 | 27600 | 72.63% | 2.06 | 31200 | R-454B
214243969 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | CNPV*4824AL*+UI | 59TN6C100C21**22 | 44000 | 21 | 12 | 8.5 | 46500 | 36400 | 78.28% | 2.16 | 43500 | R-410A
215681665 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0802120B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
212623692 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TL9E060B12UH11 | 33000 | 18 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212621997 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9E100C20MP12 | 32600 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212622063 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622072 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM8Y060A12MP11 | 30400 | 17.6 | 9.6 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622099 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8Y080B12MP11 | 31800 | 17.9 | 9.8 | 8.4 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
212622108 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM8Y080B12MP11 | 32200 | 18 | 9.9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212622313 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212622333 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | TM8E100B12MP11 | 31400 | 17.8 | 9.8 | 8.2 | 33600 | 27200 | 80.95% | 2.56 | 25200 | R-410A
213204255 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *95ESN0601714A* | 23800 | 15.5 | 9.4 | 8.5 | 25400 | 26400 | 103.9% | 2.71 | 25400 | R-410A
213205157 | 2.4 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0702116A* | 28800 | 15.2 | 9 | 8.1 | 33600 | 23800 | 70.83% | 2.69 | 23200 | R-410A
213205175 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *80ES(N,L)0901714A* | 29400 | 15.2 | 8.9 | 8.1 | 33200 | 24000 | 72.29% | 2.8 | 23200 | R-410A
213205426 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *96VTN0802120A* | 29600 | 15.2 | 9 | 8.1 | 33600 | 23800 | 70.83% | 2.67 | 23200 | R-410A
216681339 | 2.55 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CAP**4321AL* | 927TA60080V21*** | 30600 | 15.2 | 9 | 9 | 33000 | 26000 | 78.79% | 1.78 | 23200 | R-410A
215681475 | 3.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU1002120B* | 46000 | 17.5 | 9.5 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215681875 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215682075 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *97CTN1002122A* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
215682125 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M21A*+WALLCON | *80CSU0802120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36200 | 72.4% | 2.02 | 45500 | R-454B
215682225 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN1202422A* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215682885 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *80CSU1002120B* | 57000 | 18 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
215865889 | 4.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBC-60HWFPN10-MD3E |  | 54000 | 16 | 10 | 9 | 56000 | 52000 | 92.86% | 1.8 | 45000 | R-454B
212622374 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A34+TDR | TM8E100B12MP11 | 32000 | 17.9 | 9.9 | 8.3 | 33600 | 27600 | 82.14% | 2.61 | 25400 | R-410A
212622392 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B24+TDR | TM8E100B12MP11 | 30400 | 17.5 | 9 | 8.4 | 33600 | 27600 | 82.14% | 2.61 | 25400 | R-410A
212622424 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A24+TDR | TM8V080C16MP12 | 29800 | 16.9 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.64 | 25200 | R-410A
212622442 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A24+TDR | TM9V100C16MP12 | 29800 | 16.9 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.63 | 25200 | R-410A
212622449 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9E100C16MP12 | 30400 | 17.5 | 9 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212622467 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9E100C16MP12 | 33200 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
215682325 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU0802120B* | 48500 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.12 | 46000 | R-454B
215682425 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *97CTN1202422A* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
212437649 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215681455 | 3.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716B* | 46000 | 17.5 | 9.5 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215681505 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN1002122A* | 46000 | 18 | 10 | 9 | 47500 | 33800 | 71.16% | 2.08 | 42000 | R-454B
216643311 | 1.52 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X19M17A* | *80MS(N,L)0701712A* | 18200 | 15.2 | 11.5 | 11 | 19800 | 17700 | 89.39% | 1.98 | 14800 | R-454B
216643618 | 1.5 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X30M17A* | *80MSU0601716A* | 18000 | 15.2 | 11 | 9.5 | 20200 | 18200 | 90.1% | 1.92 | 15300 | R-454B
214573233 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X48AAL+WALLCON | *97CMN0802120B* | 32600 | 17 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
214573333 | 2.62 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D)4X36L21**+WALLCON | *95CSU1002122B* | 31400 | 17 | 11 | 8.1 | 33000 | 24000 | 72.73% | 1.84 | 31000 | R-410A
214573483 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X48L21**+WALLCON | *96CTN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31400 | R-410A
213779790 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X61L24A*+WALLCON | *97CMN1202422B* | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 1.98 | 31200 | R-410A
214491660 | 1.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA1810A* | CA*EA2422*4B* | D*96SC0805CUA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
214570373 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X36L21A*+WALLCON | *80CTL0702120B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
213821654 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96MSN1402422A* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
216766954 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S9V2C080U5VSB | 32800 | 16 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.13 | 21200 | R-454B
216766968 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S8V2C100M5PCB | 33800 | 16.5 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.19 | 21400 | R-454B
216766969 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3+P0V0C000M50SD |  | 34000 | 17.1 | 12 | 9 | 32600 | 24000 | 73.62% | 2.21 | 21200 | R-454B
213780960 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X37L21A*+WALLCON | *96CTN1002122B* | 33000 | 17 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 1.98 | 31600 | R-410A
213781080 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L21A*+WALLCON | *96CTN1002122B* | 31800 | 17 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.88 | 31200 | R-410A
213781130 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L24A*+WALLCON | *97CMN1202422B* | 31800 | 17 | 11 | 8.1 | 32800 | 24400 | 74.39% | 1.88 | 31200 | R-410A
213781180 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *80CTL0901716B* | 33000 | 17 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
213781260 | 2.73 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *96CTN0801714B* | 32800 | 17 | 11 | 8.5 | 32800 | 25200 | 76.83% | 1.96 | 31800 | R-410A
211708528 | 3.79 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TPLC080C16MP13 | 45500 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.14 | 30200 | R-410A
212437549 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
216764755 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | S8X1C080M5PTC | 33800 | 17.1 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.2 | 21400 | R-454B
208101914 | 2.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOE31U-36HFN1-M | MAC-36HWDN1-MN0 |  | 35000 | 15.2 | 10 | 10 | 39000 | 32000 | 82.05% | 2 | 33000 | R-410A
215681755 | 3.92 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CSU0401712B* | 47000 | 18 | 9.5 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215681855 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU1002120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
216055208 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z9ES080C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 32000 | 24200 | 75.62% | 2 | 26200 | R-454B
207699008 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MW | MVC-24HWFN1-M |  | 24000 | 17.4 | 11.7 | 10 | 24000 | 22600 | 94.17% | 1.91 | 19200 | R-410A
215677745 | 4.58 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CSU0802120A* | 55000 | 18.5 | 9 | 8.5 | 59000 | 41500 | 70.34% | 2.02 | 50500 | R-454B
216766438 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S9X1C100U5PSB | 43500 | 15.2 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29200 | R-454B
216681064 | 3.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4821AL* | 927TA60080V21*** | 36200 | 16 | 10 | 9 | 38000 | 34400 | 90.53% | 1.96 | 29000 | R-410A
214279916 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3621AL* | 59SC6A060M17**16 | 23600 | 17 | 10 | 9 | 25800 | 23600 | 91.47% | 1.96 | 18900 | R-410A
215865887 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3 | MVBC-48HWFPN10-MD3E |  | 48000 | 16 | 10 | 8.5 | 48000 | 38000 | 79.17% | 1.85 | 32400 | R-454B
214280293 | 3 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4321AL* | 59SC6A060M17**16 | 36000 | 15.5 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.06 | 29200 | R-410A
215681465 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0802120B* | 46000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
215681565 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN1202422A* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
214092413 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.1 | 32400 | 45000 | 138.9% | 3.06 | 25800 | R-410A
214092415 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.2 | 32400 | 45000 | 138.9% | 3.11 | 25800 | R-410A
214092446 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.04 | 25800 | R-410A
214389412 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4221AL*+UI | 935CB48060C17*** | 33000 | 18.5 | 11.7 | 9 | 38000 | 26800 | 70.53% | 1.96 | 32200 | R-410A
215681335 | 3.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU1002120B* | 44000 | 17 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.04 | 42500 | R-454B
216764803 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S8X1D120M5PTC | 44000 | 17.1 | 12 | 9 | 44500 | 32400 | 72.81% | 2.2 | 29400 | R-454B
216764821 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8X2D120M5PSC | 43500 | 17.1 | 11.7 | 9 | 44500 | 32600 | 73.26% | 2.2 | 29800 | R-454B
212437663 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215439763 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A*+MBVK12BP1X00A* |  | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215682645 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716B* | 55500 | 18 | 9 | 8.5 | 58500 | 41000 | 70.09% | 2.04 | 50500 | R-454B
215682895 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN0802120A* | 56500 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
216770050 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | L8V1C100U5VSB | 43000 | 16 | 12 | 8.7 | 44500 | 32600 | 73.26% | 2.22 | 29600 | R-454B
215681775 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CSU0802120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36200 | 72.4% | 2 | 45500 | R-454B
215682025 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN1202422A* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216679819 | 2.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3621AL* | 927TA48080V17*** | 34800 | 15.5 | 9.5 | 8.5 | 38500 | 34800 | 90.39% | 1.75 | 29400 | R-410A
212437568 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216453108 | 2.98 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X36A1 | 5PX*D008AS3 | S8V2D120M5PCB | 35800 | 20.6 | 13 | 10 | 32200 | 25000 | 77.64% | 2.2 | 31600 | R-454B
215439650 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80TC0803B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215439764 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A*+MBVK12BP1X00A* |  | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216767063 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3 | S8V2C080M5PDB | 32400 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.11 | 21200 | R-454B
212622749 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.3 | 33800 | 29600 | 87.57% | 2.7 | 26600 | R-410A
212622758 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9E060A10MP12 | 32200 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
216732668 | 1.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *80MS(N,L)0451412A* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19200 | 91.43% | 1.96 | 18000 | R-454B
216732952 | 1.82 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *96VSN0401410B* | 21800 | 15.5 | 10 | 8.5 | 21200 | 19200 | 90.57% | 1.96 | 18100 | R-454B
213781310 | 2.68 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L21A*+WALLCON | *80CTL0902120B* | 32200 | 17 | 11 | 8.1 | 32600 | 24800 | 76.07% | 1.98 | 31200 | R-410A
207699010 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE31U-36HFN1-M | MVC-36HWFN1-M |  | 36000 | 16 | 10 | 9.5 | 40000 | 34400 | 86% | 1.97 | 30400 | R-410A
212986300 | 1.45 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *96MSN0401410A* | 17400 | 16 | 10.5 | 8.5 | 18500 | 19500 | 105.4% | 2.34 | 12400 | R-410A
212986684 | 1.48 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *96MSN0401712A* | 17700 | 15.5 | 10.5 | 8.1 | 17700 | 17800 | 100.6% | 2.14 | 12100 | R-410A
212437567 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
213613580 | 1.93 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24E4 |  | 23200 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213828529 | 3.38 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)60C44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
215682585 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CSU0802120B* | 55500 | 18.5 | 9 | 8.5 | 58500 | 41000 | 70.09% | 2.04 | 50500 | R-454B
215682635 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712B* | 55500 | 18 | 9 | 8.5 | 58500 | 41000 | 70.09% | 2.04 | 50500 | R-454B
212160161 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | V,A,D36H175D149 | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213311182 | 3 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L139+CBPE4B* |  | 36000 | 16 | 9.5 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
213205574 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80ES(N,L)1552420A* | 35400 | 16 | 10 | 8.1 | 39500 | 31200 | 78.99% | 2.72 | 29200 | R-410A
213205660 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *95ESN1202422A* | 35400 | 15.5 | 10.5 | 8.1 | 39500 | 31600 | 80% | 2.72 | 29400 | R-410A
216055419 | 3.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES120D20SMPS1 | 43000 | 17.5 | 11.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
216055919 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055920 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
212437566 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
215681985 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *80CSU0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36200 | 72.4% | 2.12 | 46000 | R-454B
215682035 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *96CTN0802120B* | 48500 | 19 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
216766984 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD05AS3 | S9V2C100D5VSB | 32600 | 16 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.98 | 21600 | R-454B
216766985 | 2.73 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD05AS3 | S9X2C100D5PSB | 32800 | 15.2 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.98 | 21600 | R-454B
212972236 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *80VTL0902120B* | 35600 | 16.5 | 10 | 8.5 | 37800 | 34600 | 91.53% | 2.02 | 29000 | R-410A
216767001 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S9X1C100D5PSB | 34400 | 16 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.15 | 21400 | R-454B
216767035 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X2B080D4PSB | 31600 | 15.2 | 11.2 | 8.7 | 31800 | 23800 | 74.84% | 2.13 | 21000 | R-454B
216767036 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S8V2B080M4PDB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
213080004 | 2.93 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3621AL* | 916SA48080M17*** | 35200 | 15.5 | 9.5 | 8.1 | 39000 | 35400 | 90.77% | 1.84 | 29600 | R-410A
213080513 | 2.92 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3621AL* | 935SB36040M17*** | 35000 | 15.2 | 9.5 | 8.1 | 39000 | 35400 | 90.77% | 1.82 | 29600 | R-410A
213080561 | 3.02 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4321AL* | 935SB36040M17*** | 36200 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2.04 | 29200 | R-410A
213080681 | 3.05 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3721AL* | 935SB48060M17*** | 36600 | 16 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2.06 | 29200 | R-410A
214861550 | 4.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBDM-60HWFN10-WC3 |  | 54000 | 17.5 | 12 | 9.5 | 55000 | 54000 | 98.18% | 1.9 | 35000 | R-454B
216678811 | 2.95 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4217AL* | 927TA48060V17*** | 35400 | 15.5 | 10 | 8.5 | 38500 | 34600 | 89.87% | 1.78 | 29400 | R-410A
216679831 | 3 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3717AL* | 927TA48080V17*** | 36000 | 15.2 | 10 | 8.5 | 38500 | 34600 | 89.87% | 1.92 | 29400 | R-410A
215681445 | 3.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712B* | 46000 | 18 | 9.5 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
216765984 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3 | S9X1B040U3PSB | 23800 | 17.1 | 12.5 | 9 | 21800 | 17400 | 79.82% | 2.08 | 15500 | R-454B
216679435 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3717AL* | 927TA48060V17*** | 24000 | 17 | 10 | 9 | 25200 | 22000 | 87.3% | 1.76 | 18700 | R-410A
216679483 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3612AL* | 927TA48060V17*** | 24000 | 16 | 10 | 8.5 | 25400 | 22200 | 87.4% | 1.75 | 18800 | R-410A
215850179 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z8ET060A12LMPS1 | 20600 | 18.8 | 11.7 | 9 | 23000 | 17700 | 76.96% | 2 | 18200 | R-454B
215681435 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0802120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215681485 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0801716A* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34200 | 71.25% | 2.06 | 42500 | R-454B
215681705 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU1002120B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215681835 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU0601716B* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215682005 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216644075 | 1.5 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X25M17A* | *96VSN0401410B* | 18000 | 15.2 | 11 | 9 | 19700 | 17600 | 89.34% | 1.88 | 14800 | R-454B
212987052 | 1.44 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L14** | *96MSN0601412A* | 17300 | 16 | 10.5 | 8.1 | 18300 | 19200 | 104.9% | 2.32 | 12300 | R-410A
209960476 | 4.58 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30U-55HFN1-M | MVC-60HWFN1-M |  | 55000 | 15.3 | 8.8 | 9.4 | 59000 | 48500 | 82.2% | 1.91 | 42000 | R-410A
216620308 | 2.5 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBM-36A24T4N10 |  | 30000 | 15.3 | 10 | 9.3 | 32000 | 30400 | 95% | 1.78 | 24000 | R-454B
216620309 | 2.42 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBM-36B24T4N10 |  | 29000 | 16 | 10 | 9.5 | 32000 | 32000 | 100% | 1.85 | 25000 | R-454B
216620310 | 2.42 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBM-36C24T4N10 |  | 29000 | 16 | 10 | 9.5 | 32000 | 32000 | 100% | 1.85 | 25000 | R-454B
216032496 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBC-30HWFPN10-MC3E |  | 30000 | 16.8 | 11.7 | 10 | 34000 | 32600 | 95.88% | 1.96 | 23800 | R-454B
213780110 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X42AAL+WALLCON | *96CTN0801714B* | 32400 | 16 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.92 | 31600 | R-410A
216055936 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
216055937 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y120D20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
216055953 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055955 | 3.42 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055972 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055986 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216056002 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
212437572 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212928549 | 2.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOE31U-36HFN1-M | MVB-36B23T4N1 |  | 35000 | 15.5 | 10 | 8.6 | 38000 | 31600 | 83.16% | 1.85 | 27400 | R-410A
216767052 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S8V2B060M4PCB | 33200 | 16.5 | 12 | 8.7 | 32600 | 24000 | 73.62% | 2.15 | 21200 | R-454B
212972488 | 2.53 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X43L21A* | *80VTL1102122B* | 30400 | 15.2 | 9 | 8.1 | 33400 | 26400 | 79.04% | 1.84 | 23200 | R-410A
216767053 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3+P0V0A000M30SD |  | 32600 | 16 | 12 | 8.7 | 32200 | 24000 | 74.53% | 2.12 | 21000 | R-454B
216767054 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3+P0V0B000M40SD |  | 33800 | 17 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.19 | 21400 | R-454B
216766484 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S9X2D120U5PSB | 43500 | 16 | 12 | 9 | 44500 | 32600 | 73.26% | 2.23 | 29800 | R-454B
216766486 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S9X2C080U5PSB | 43500 | 16.5 | 11.7 | 8.7 | 45000 | 33200 | 73.78% | 2.21 | 30200 | R-454B
215850184 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z8ET080B12LMPS1 | 22400 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
209960478 | 4.58 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30U-55HFN1-M-[X](GA) | MVC-60HWFN1-M(GA) |  | 55000 | 15.5 | 9 | 9.2 | 60000 | 53500 | 89.17% | 1.96 | 41000 | R-410A
213206256 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*A070E14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.99 | 19100 | R-410A
213206281 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A070E17**16 | 23800 | 16.5 | 10.3 | 8.1 | 26000 | 20200 | 77.69% | 2.87 | 19000 | R-410A
213206399 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2D040E14**10 | 23200 | 15.4 | 9.8 | 8.1 | 26000 | 20400 | 78.46% | 2.89 | 19100 | R-410A
212437650 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212437657 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215681765 | 3.92 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CSU0601716B* | 47000 | 18 | 9.5 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215682185 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *80CSU0802120B* | 47500 | 18.5 | 10 | 9 | 50000 | 36000 | 72% | 2.02 | 45500 | R-454B
212437651 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212437658 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
212438126 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
215682375 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
215682525 | 4.08 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *80CSU0802120B* | 49000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2.12 | 46500 | R-454B
212400417 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C46+JMET12BS2N1+TDR |  | 34000 | 18 | 8.5 | 8.1 | 36000 | 25400 | 70.56% | 2.64 | 24800 | R-410A
212400415 | 2.95 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C44+JMET12BS4N1+TDR |  | 35400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
216056022 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215676965 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0802120A* | 57000 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 55500 | R-454B
216055603 | 1.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES100B12SMPS1 | 20400 | 18.7 | 11.2 | 9.5 | 22600 | 18000 | 79.65% | 2 | 18300 | R-454B
216055621 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES026A08SMPS1 | 20600 | 17.5 | 11.2 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
211497142 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MW-[X1] | MVC-24HWFN1-MSQ4 |  | 24000 | 17.4 | 11.7 | 10 | 24000 | 22600 | 94.17% | 1.91 | 19200 | R-410A
210135403 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MU0Q1W | MVC-23HWFN1-MQ1W |  | 23000 | 18 | 11.7 | 9.7 | 24000 | 23600 | 98.33% | 1.95 | 18400 | R-410A
215682205 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN0802120A* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215682255 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CSU1002120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216054994 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES080B12SMPS1 | 22400 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
215851291 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C20SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
215850220 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES080B12SMPS1 | 22400 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
215912358 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | L(E,F)W30CJ |  | 22000 | 17 | 11.7 | 8.5 | 22000 | 17000 | 77.27% | 2.1 | 18400 | R-454B
214608432 | 3.92 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-48U3SP2 | AE(D,N,U)+DM60B44+TDR |  | 47000 | 16.5 | 9.8 | 8.1 | 47000 | 33000 | 70.21% | 1.9 | 31000 | R-410A
213204890 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN0802120A* | 23600 | 16.9 | 10.3 | 8.4 | 26000 | 20200 | 77.69% | 3.02 | 19000 | R-410A
216699801 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*96TC1005CNA* | 23000 | 18.2 | 11.7 | 8.5 | 21000 | 21000 | 100% | 2 | 21000 | R-32
216055596 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES080B12SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
216055610 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ET060A12LMPS1 | 21000 | 19 | 11.7 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
216055630 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES040A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18300 | R-454B
213156950 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30U-30HFN1-MR0(X) | MVBE-30HWFN1-ML3E |  | 30000 | 16.9 | 10 | 9 | 31000 | 25000 | 80.65% | 1.8 | 19600 | R-410A
216055864 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055880 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055897 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y100C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216766534 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3+P0V0D000M50SD |  | 43000 | 16.5 | 12.5 | 8.7 | 44000 | 32000 | 72.73% | 2.22 | 29000 | R-454B
216766568 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9V2C100U5VSB | 43000 | 16 | 12 | 8.7 | 44000 | 32400 | 73.64% | 2.2 | 29400 | R-454B
216766586 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8V2C080M5PDB | 43500 | 16 | 12 | 8.7 | 45000 | 32800 | 72.89% | 2.21 | 30000 | R-454B
216766600 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S9X2D120U5PSB | 43500 | 16 | 12 | 9 | 44500 | 32600 | 73.26% | 2.23 | 29800 | R-454B
216030934 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBDM-30HWFN10-WB3-MAS |  | 30000 | 17.2 | 12 | 10.8 | 33000 | 33200 | 100.6% | 1.97 | 24000 | R-454B
214802765 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)30B34+TDR | R801V1004A17UHN | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20000 | 70.42% | 2.62 | 20800 | R-410A
213828522 | 2.4 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)36B44+TDR |  | 28800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213828547 | 2.48 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)37E34+TDR |  | 29800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
216055851 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055858 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055901 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216055926 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215402629 | 1.9 | No | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | L(E,F)W30D4 |  | 22800 | 16 | 9.8 | 8.5 | 25400 | 19800 | 77.95% | 2.8 | 18600 | R-410A
213828548 | 2.43 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)31B44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
212977832 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *80MS(N,L)0451412A* | 17700 | 16.5 | 11 | 8.1 | 18100 | 18600 | 102.8% | 2.24 | 12300 | R-410A
215682685 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN0802120A* | 56000 | 18.5 | 9 | 9 | 60000 | 42000 | 70% | 2.02 | 51500 | R-454B
212972737 | 1.45 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L14** | *96VSN0401410B* | 17400 | 15.5 | 10.5 | 8.5 | 18500 | 19200 | 103.8% | 2.3 | 12400 | R-410A
212973037 | 1.48 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *96VSN0401712B* | 17700 | 16 | 10.5 | 8.1 | 17800 | 17800 | 100% | 2.14 | 12100 | R-410A
212969831 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *80VSL0451412B* | 23600 | 17 | 10.5 | 8.5 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
212972987 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L14** | *96VSN0401410B* | 23400 | 16 | 10 | 8.1 | 26400 | 24800 | 93.94% | 2.04 | 19200 | R-410A
207785323 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD31-23HFN1-MT2Q1W | MVC-23HWFN1-MQ1W |  | 24000 | 16.7 | 11.7 | 9.1 | 24000 | 18100 | 75.42% | 2.29 | 18000 | R-410A
215681535 | 3.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU1002120B* | 46000 | 18 | 9.5 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
215681785 | 3.92 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CSU1002120B* | 47000 | 18 | 9.5 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
212437547 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
216055933 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y100C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055958 | 3.46 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE130D20MP11 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35200 | 76.52% | 2 | 35400 | R-454B
216055983 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC100C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216056042 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
213821166 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN1002120B* | 23400 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213896272 | 4.67 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-60U3SP2 | L(E,G)M60I4 |  | 56000 | 17 | 8 | 8.5 | 56000 | 42000 | 75% | 2.6 | 40000 | R-410A
214336698 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R962V1155A24M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
211708529 | 3.79 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TPLC080C16MP13 | 45500 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.14 | 30200 | R-410A
215399909 | 1.88 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.69 | 18700 | R-454B
213821326 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0802120B* | 23600 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213828544 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)43C34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213386477 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE31U-36HFN1-M | MVBL-36HWFN1-MK3 |  | 36000 | 17 | 10 | 9.9 | 36000 | 36000 | 100% | 1.9 | 32800 | R-410A
216030939 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBC-36HWFN10-MC3E-MAS |  | 36000 | 16.1 | 10 | 8.7 | 36000 | 27000 | 75% | 2 | 25600 | R-454B
213780210 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X48AAL+WALLCON | *95CSU0601716B* | 32400 | 16 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31800 | R-410A
214573633 | 2.63 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X36L21A*+WALLCON | *95CSU1002122B* | 31600 | 17 | 11 | 8.1 | 32800 | 24200 | 73.78% | 1.86 | 31000 | R-410A
214573733 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L21A*+WALLCON | *80CTL0702120B* | 31800 | 17 | 11 | 8.5 | 33000 | 24400 | 73.94% | 1.9 | 31400 | R-410A
216733100 | 1.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *97VTN0601716A* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 18000 | R-454B
216733169 | 1.9 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *80MS(N,L)0451714A* | 22800 | 15.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216733621 | 1.93 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *97VTN0801716A* | 23200 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216733938 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *80MSU0601716A* | 22200 | 16.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
215681735 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1002122A* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
216770018 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | L9X1C100U5VSA | 43500 | 16 | 11.2 | 8.5 | 45000 | 33000 | 73.33% | 2.17 | 30200 | R-454B
216055902 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216055938 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
212622776 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM9E060A10MP12 | 30600 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212622790 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.68 | 25800 | R-410A
212622899 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A24+TDR | TM8E100B12MP11 | 29400 | 17.2 | 9.4 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212623099 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.2 | 33800 | 30000 | 88.76% | 2.77 | 26800 | R-410A
212623142 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8E100B12MP11 | 30400 | 17.5 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623219 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLE100B12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
216681130 | 2.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4221AL* | 927TA60080V21*** | 35600 | 15.5 | 10 | 8.5 | 39000 | 34800 | 89.23% | 1.75 | 29400 | R-410A
213780081 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X42AAL+WALLCON | *97CMN1002122B* | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
215877111 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | L(E,F)W30E4 |  | 23000 | 16 | 10 | 9 | 25400 | 19800 | 77.95% | 2.8 | 18600 | R-410A
211708403 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | CP9C120D20MP13 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.11 | 30600 | R-410A
211708412 | 3.79 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | CPLC100C16MP13 | 45500 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.14 | 30200 | R-410A
211708428 | 3.75 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM8E080C16MP11 | 45000 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.11 | 30200 | R-410A
216679519 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3617AL* | 927TA48060V17*** | 23600 | 16.5 | 10 | 9 | 25800 | 23600 | 91.47% | 1.76 | 18900 | R-410A
216680575 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*2412AL* | 927TA48080V17*** | 23600 | 16 | 10 | 9 | 26200 | 23600 | 90.08% | 1.82 | 19200 | R-410A
216681526 | 1.95 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*2412AL* | 927TA60080V21*** | 23400 | 16 | 9.8 | 9 | 26000 | 23800 | 91.54% | 1.86 | 19100 | R-410A
215385628 | 2.57 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | L(E,F)W36D4 |  | 30800 | 16 | 9.5 | 9 | 34400 | 26000 | 75.58% | 2.05 | 24000 | R-410A
212348354 | 2.82 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | LEW36C4 |  | 33800 | 17.5 | 9.5 | 8.5 | 33000 | 23600 | 71.52% | 2.47 | 23000 | R-410A
216055969 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216056036 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C20SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
216056039 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
216055853 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL9E100C20UH11 | 40000 | 16.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055854 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL9E100C20UH11 | 41000 | 17 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055885 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055886 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V120C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
214336695 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R962V0705A21M4S | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215682235 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *96CTN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
215682535 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *80CSU1002120B* | 48500 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
212623226 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212623292 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | CP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623324 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | CP9C080C16MP13 | 30800 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623401 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TL9E100C20UH11 | 32000 | 17 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.77 | 26200 | R-410A
212438156 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215676705 | 4 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0451712B* | 48000 | 18.5 | 9.5 | 9 | 50000 | 37600 | 75.2% | 1.98 | 47500 | R-454B
215676925 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN1002122B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
207699011 | 3.92 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30U-48HFN1-M-[X1] | MVC-48HWFN1-M |  | 47000 | 15.6 | 8.2 | 9.4 | 50000 | 46000 | 92% | 1.9 | 36000 | R-410A
212976421 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *96VTN0802120B* | 23800 | 17 | 10.5 | 8.5 | 26400 | 24000 | 90.91% | 1.98 | 19200 | R-410A
212977257 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L24A* | *96VTN1202422B* | 35600 | 16.5 | 10 | 8.5 | 37800 | 34600 | 91.53% | 2.02 | 29000 | R-410A
214671470 | 2.87 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | A(E,F)M376+TDR |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
214573883 | 2.73 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *97CMN0602120B* | 32800 | 17 | 11 | 8.5 | 33000 | 25400 | 76.97% | 1.98 | 32000 | R-410A
213828524 | 2.4 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)42A44+TDR |  | 28800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213828525 | 2.43 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)42B44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
214573983 | 2.68 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *95CSU0802120B* | 32200 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214574003 | 2.68 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *97CMN0602120B* | 32200 | 17 | 11 | 8.5 | 32600 | 25200 | 77.3% | 1.96 | 31600 | R-410A
216681559 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3621AL* | 927TA60080V21*** | 23800 | 17 | 10.5 | 9 | 26000 | 23200 | 89.23% | 1.82 | 19000 | R-410A
215681955 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *97CTN0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215682505 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN1002122A* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
212437661 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
211708515 | 3.79 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TMLV100C16MP12 | 45500 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.14 | 30200 | R-410A
211708530 | 3.79 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TPLC100C16MP13 | 45500 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.14 | 30200 | R-410A
215682655 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN0802120B* | 56000 | 18.5 | 9 | 9 | 60000 | 42000 | 70% | 2.02 | 51500 | R-454B
215385624 | 2.13 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | A(E,F)W304+TDR |  | 25600 | 16 | 10 | 8.1 | 28400 | 23200 | 81.69% | 2.07 | 18700 | R-410A
216055887 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055888 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
214336724 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R951V1005A21UHU | 45500 | 15.2 | 10 | 8.1 | 45500 | 34200 | 75.16% | 3.04 | 32600 | R-410A
216055551 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE060A12MP11 | 20800 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216055588 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ES040A12SMPS1 | 21000 | 17.5 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216055601 | 1.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES100B12SMPS1 | 20000 | 18.5 | 11.2 | 9 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215865885 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBC-36HWFPN10-MC3E |  | 36000 | 16.2 | 10 | 8.7 | 36000 | 27000 | 75% | 2 | 24800 | R-454B
211752353 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE34936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213828523 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)36C44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213828526 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)42D34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215851166 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055996 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216056062 | 3.5 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES120D20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
216055845 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216055847 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E100C20UH11 | 40500 | 17.5 | 11.2 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
216055862 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055877 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V080C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055879 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V080C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
213821173 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN1002122B* | 23800 | 16.5 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
214336669 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V1255A24UH | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
216766006 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S8V2A040M3PDB | 31800 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.09 | 21200 | R-454B
216766008 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S8V2B060M4PDB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.11 | 21200 | R-454B
216766060 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S9X2B060U4PSB | 33600 | 16.5 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.18 | 21400 | R-454B
216766092 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S8V2B060M4PCB | 33000 | 16.5 | 12 | 8.5 | 33200 | 24400 | 73.49% | 2.09 | 21600 | R-454B
216766939 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9X2B060D3PSB | 32600 | 16.5 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.05 | 21400 | R-454B
216766948 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S8V2C100M5PCB | 32600 | 16 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.12 | 21200 | R-454B
212623494 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A24+TDR | CP9C100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27200 | 80.47% | 2.47 | 25200 | R-410A
212623542 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TP9C100C20MP13 | 31600 | 17.5 | 9.3 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
212623603 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9Y060B12MP11 | 32200 | 17.5 | 9.5 | 8.1 | 34000 | 29400 | 86.47% | 2.43 | 26600 | R-410A
212623608 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9Y060B12MP11 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 29400 | 86.47% | 2.43 | 26600 | R-410A
212623635 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | CPLC080B12MP13 | 31200 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623651 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TPLC080B12MP13 | 31200 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623662 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623667 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TL9E060B12UH11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
216766957 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S8V2C100M5PDB | 33800 | 16.5 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.19 | 21400 | R-454B
216766975 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S9V2C100U5VSB | 34000 | 17.1 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.2 | 21200 | R-454B
216767000 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8V2C100M5PDB | 34200 | 17 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.16 | 21200 | R-454B
216767030 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3+P0V0B000M40SD |  | 32400 | 16 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.12 | 21000 | R-454B
216770058 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S9V2D120U5VSB | 43000 | 16.5 | 12 | 9 | 44500 | 32400 | 72.81% | 2.23 | 29600 | R-454B
211260172 | 1.48 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L14A* | *96VTN0601412A* | 17800 | 16 | 10.5 | 8.5 | 18800 | 19000 | 101.1% | 2.28 | 12500 | R-410A
216681548 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3612AL* | 927TA60080V21*** | 24200 | 16.5 | 10 | 9 | 25600 | 22000 | 85.94% | 1.75 | 18800 | R-410A
213828528 | 3.33 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)60B44+TDR |  | 40000 | 15.55 | 11.4 | 8.5 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213821164 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0802120B* | 23800 | 16 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213896270 | 4.58 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-60U3SP2 | L(E,G)M60G4 |  | 55000 | 16.5 | 8 | 8.2 | 55000 | 40500 | 73.64% | 2.46 | 39000 | R-410A
214056956 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE(D,N,U)+DM36A34+TDR |  | 31400 | 18.3 | 10.3 | 8.4 | 33000 | 26200 | 79.39% | 2.65 | 24400 | R-410A
215439760 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A*+MBVK16CP1X00A* |  | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215681935 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU1002120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
215682165 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M21A*+WALLCON | *97CTN1002122A* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
212438120 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
212438127 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216679399 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3017AL* | 927TA48060V17*** | 23600 | 16.5 | 10 | 9 | 25800 | 23800 | 92.25% | 1.86 | 18900 | R-410A
216027572 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-23HFPN10-M1 | MVBC-24HWFPN10-MB1 |  | 24000 | 19.4 | 11.7 | 9.1 | 24000 | 18000 | 75% | 2.1 | 22000 | R-454B
213306298 | 2.9 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D34+TDR | Z8ES080C20SMPS1 | 34800 | 17 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213821319 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0601716B* | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.93 | 19400 | R-410A
213828521 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)30D44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
214336681 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V1505A24UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
216766440 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S9X1C080U5PSB | 43000 | 16.5 | 12 | 8.7 | 43500 | 32000 | 73.56% | 2.21 | 29200 | R-454B
216766422 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCD008AS3 | S8V2D120M5PCB | 34200 | 17.1 | 12.5 | 9 | 32600 | 24200 | 74.23% | 2.22 | 21400 | R-454B
216766488 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S9X1D120U5PSB | 43500 | 16 | 12 | 9 | 44500 | 32600 | 73.26% | 2.23 | 29800 | R-454B
216766490 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S9X1C080U5PSB | 43500 | 16.5 | 11.7 | 8.7 | 45000 | 33200 | 73.78% | 2.21 | 30200 | R-454B
214802742 | 1.9 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)30B34+TDR | R801V1004A17UHS | 22800 | 16 | 12 | 8.4 | 23000 | 16300 | 70.87% | 3.07 | 17000 | R-410A
216766815 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S8V2B080M4PCB | 23800 | 17.5 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2.06 | 15500 | R-454B
216766822 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD04AS3 | S8V2B060M4PCB | 23400 | 17 | 12 | 8.1 | 22400 | 17300 | 77.23% | 1.83 | 15400 | R-454B
216766849 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S9X1B060U4PSB | 23200 | 16 | 12.5 | 8.7 | 21800 | 17200 | 78.9% | 2.01 | 15300 | R-454B
212437565 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
212924806 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE31U-36HFN1-M | MVBE-36HWFN1-ML3E |  | 36000 | 17.6 | 10.2 | 9.2 | 38000 | 33400 | 87.89% | 1.81 | 28600 | R-410A
214336677 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V1255A24DZ | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336693 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R951V1005A21UHU | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
212437569 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212437573 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216766538 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S9X2D120D5PSB | 43000 | 16 | 12 | 8.7 | 44500 | 32400 | 72.81% | 2.2 | 29600 | R-454B
216766540 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8V2D120M5PDB | 43000 | 16 | 12 | 8.7 | 44000 | 32400 | 73.64% | 2.21 | 29400 | R-454B
211599530 | 3.25 | Yes | Yes | FRASER-JOHNSTON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B42T21 | LEM48C4 |  | 39000 | 16 | 12.5 | 8.1 | 40500 | 29000 | 71.6% | 3.33 | 28200 | R-410A
216766604 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S9X1C080U5PSB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.22 | 29200 | R-454B
216766622 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S9X2C100U5PSB | 43500 | 15.2 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.22 | 29400 | R-454B
216055913 | 3.38 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E120D20MP12 | 40500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055927 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055961 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLV100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055963 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLV100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
214608430 | 2.75 | No | Yes | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | AE(D,N,U)+DM42B34+TDR |  | 33000 | 17 | 9.8 | 8.5 | 35000 | 26000 | 74.29% | 2.05 | 24000 | R-410A
215385625 | 2.5 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | A(E,F)W364+TDR |  | 30000 | 16 | 10 | 8.1 | 34200 | 26000 | 76.02% | 2.05 | 24000 | R-410A
216030946 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBE-36HWFN10-WL3E-MAS |  | 36000 | 16.7 | 10.2 | 9.3 | 37000 | 29200 | 78.92% | 1.99 | 24800 | R-454B
213896271 | 4.63 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-60U3SP2 | L(E,G)M60H4 |  | 55500 | 17 | 8 | 8.5 | 55500 | 41000 | 73.87% | 2.58 | 39500 | R-410A
211708420 | 3.71 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TL9E060B12UH11 | 44500 | 15.5 | 11 | 8.1 | 44500 | 31600 | 71.01% | 3.01 | 30800 | R-410A
211708429 | 3.75 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM8E080C16MP11 | 45000 | 16 | 11.9 | 8.2 | 44000 | 30800 | 70% | 3.11 | 30200 | R-410A
211708470 | 3.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9E100C16MP12 | 45000 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
211708484 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9V120D20MP12 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.11 | 30600 | R-410A
215678365 | 1.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *97CTN0601716A* | 23600 | 16.5 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 19900 | R-454B
216967947 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-36HFN10-M3X | MVBDM-36HWFN10-WC3 |  | 36000 | 18 | 12 | 10 | 36000 | 36000 | 100% | 2.46 | 31000 | R-454B
213238538 | 3.71 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM8E100C20MP11 | 44500 | 16.3 | 11.7 | 8.5 | 45000 | 31600 | 70.22% | 3.16 | 31000 | R-410A
213238547 | 3.54 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM8V100C16MP12 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
216766858 | 1.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S9V2B040D3VSB | 21800 | 15.5 | 11.5 | 8.5 | 21200 | 16900 | 79.72% | 1.94 | 15100 | R-454B
216766863 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8V2A040M3PCB | 23200 | 16.5 | 12 | 8.7 | 21800 | 17300 | 79.36% | 2.01 | 15500 | R-454B
213821175 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN1002122B* | 23800 | 16.5 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
215402627 | 1.9 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | L(E,F)W30D4 |  | 22800 | 15.5 | 9 | 9 | 24400 | 22000 | 90.16% | 2.8 | 19600 | R-410A
216623446 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBM-24B18T3N10-MAS |  | 24000 | 16 | 10 | 9.5 | 25000 | 21000 | 84% | 1.8 | 19700 | R-454B
211708510 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TMLE120C20MP11 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.07 | 30600 | R-410A
213306316 | 2.9 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D34+TDR | Z8ES100C20SMPS1 | 34800 | 16.5 | 9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
215385623 | 1.78 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-24U3SF2 | L(E,F)W36D4 |  | 21400 | 15.8 | 10 | 8.1 | 23200 | 17700 | 76.29% | 1.98 | 17000 | R-410A
216767057 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3 | S9V2C080U5VSB | 32800 | 16 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.13 | 21200 | R-454B
212621513 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A24+TDR | TM9V120D20MP12 | 29400 | 16.3 | 9 | 8.4 | 32000 | 28000 | 87.5% | 2.77 | 25200 | R-410A
212621561 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212621570 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TPLC120C20MP13 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212621572 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TPLC120C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212621629 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TPLC100C20MP13 | 28600 | 15.6 | 8.4 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212621647 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | CPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621670 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | CPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
215865882 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBC-24HWFPN10-MB3E |  | 23000 | 18.4 | 11.7 | 10 | 24000 | 21600 | 90% | 1.87 | 20000 | R-454B
213771144 | 2.03 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X37L21A*+WALLCON | *80CTL0701716B* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213612908 | 3.75 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | L(E,G)M60A6 |  | 45000 | 15.5 | 11.8 | 8.1 | 45500 | 37800 | 83.08% | 3.7 | 34600 | R-410A
216055604 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES100B12SMPS1 | 21000 | 19 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
216055637 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES060B12SMPS1 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18600 | 83.04% | 2 | 18500 | R-454B
212621697 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8V100C20MP12 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621722 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM8V120C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212621729 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8V120C20MP12 | 30400 | 16.1 | 8 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212621731 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621754 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621779 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
216055422 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TL8E060A12UH11 | 19500 | 17 | 11 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
216055424 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TL8E060A12UH11 | 21000 | 18 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
216055463 | 1.67 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8Y060A12MP11 | 20000 | 17.5 | 9.8 | 8.5 | 22600 | 18400 | 81.42% | 2 | 18500 | R-454B
216055481 | 1.68 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E040A10MP12 | 20200 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216055524 | 1.66 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y040A10MP11 | 19900 | 16 | 10 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055542 | 1.65 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE040A12MP11 | 19800 | 16 | 11.2 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216055547 | 1.68 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE060A12MP11 | 20200 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
216765876 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD04AS3 | S8V2B080M4PCB | 23200 | 17.1 | 12.5 | 8.1 | 22200 | 17100 | 77.03% | 1.83 | 15300 | R-454B
216765892 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3 | S9X2B060D3PSB | 23800 | 17.1 | 12.5 | 8.7 | 22200 | 17400 | 78.38% | 1.99 | 15500 | R-454B
216765908 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3 | S8V2A040M3PCB | 23800 | 17.1 | 12.5 | 8.7 | 22400 | 17500 | 78.12% | 1.98 | 15600 | R-454B
216766913 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S9X2B080U4PSB | 33200 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.16 | 21200 | R-454B
216766915 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3+P0V0B000M40SD |  | 33800 | 17 | 12 | 8.7 | 32600 | 24000 | 73.62% | 2.19 | 21200 | R-454B
214802758 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0754A17UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20000 | 70.42% | 2.62 | 20800 | R-410A
213828527 | 3.42 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)48D44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
216766160 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S8V2C100M5PCB | 33800 | 17 | 12 | 9 | 32800 | 24200 | 73.78% | 2.2 | 21400 | R-454B
216766276 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S9X1B060U4PSB | 32400 | 16 | 11.7 | 8.7 | 32600 | 24200 | 74.23% | 2.12 | 21400 | R-454B
216766292 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S8V2B080M4PCB | 32200 | 16 | 12 | 8.7 | 32200 | 24000 | 74.53% | 2.11 | 21200 | R-454B
216766442 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S9V2C100U5VSB | 43000 | 16 | 12 | 8.7 | 44000 | 32400 | 73.64% | 2.2 | 29400 | R-454B
216766444 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S9V2C080U5VSB | 43500 | 16.5 | 12.5 | 8.7 | 43500 | 32000 | 73.56% | 2.22 | 29000 | R-454B
216766542 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8V2D120M5PCB | 43000 | 16 | 12 | 8.7 | 44000 | 32400 | 73.64% | 2.21 | 29400 | R-454B
216766558 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8V2C080M5PCB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
211752354 | 1.97 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE32936 | A97USMV070B12 | 23600 | 20 | 13 | 8.45 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
213161302 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P159+AEFE4B* |  | 23400 | 21 | 13.5 | 8.7 | 20600 | 15700 | 76.21% | 2.26 | 13300 | R-410A
212621790 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621795 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TPLC120C20MP13 | 32000 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621829 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9Y120D20MP11 | 32800 | 16.5 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212621856 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621874 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9V120D20MP12 | 30200 | 16.5 | 9.1 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212621879 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9V120D20MP12 | 32600 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
213821336 | 1.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN1002122B* | 22800 | 17.3 | 10.2 | 8.4 | 25200 | 19900 | 78.97% | 2.96 | 18600 | R-410A
213828545 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)37D34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215851364 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES120D20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
214336721 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R802V1005A21UHN | 45500 | 16 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.17 | 32400 | R-410A
216055447 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
214608431 | 2.68 | No | Yes | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | AE(D,N,U)+DM48E34+TDR |  | 32200 | 17 | 9.8 | 8.5 | 34800 | 26000 | 74.71% | 2.05 | 24000 | R-410A
216766933 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S8V2B080M4PCB | 32400 | 16 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.04 | 21200 | R-454B
216030940 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3 | MVBC-48HWFN10-MD3E-MAS |  | 48000 | 16 | 10 | 8.5 | 48000 | 38000 | 79.17% | 1.85 | 32400 | R-454B
216766949 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S9X2C080U5PSB | 32600 | 16 | 11.7 | 8.7 | 32200 | 24000 | 74.53% | 2.12 | 21200 | R-454B
216766972 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S8V2C080M5PDB | 34200 | 16.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.2 | 21400 | R-454B
216766974 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S9X1C080U5PSB | 34400 | 17.1 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.21 | 21400 | R-454B
216767038 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S8V2A040M3PDB | 32800 | 16 | 11.7 | 8.7 | 32600 | 24200 | 74.23% | 2.13 | 21400 | R-454B
216767058 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3 | S8V2C100M5PCB | 32600 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.12 | 21200 | R-454B
216770098 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S8X1C100M5PSC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216770100 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S8X2C100M5PSC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216770107 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TAMXC03AV31 |  | 33000 | 16.5 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.06 | 21400 | R-454B
216055465 | 1.7 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8Y060A12MP11 | 20400 | 17.5 | 9.8 | 9 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216055490 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E060A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18600 | R-454B
216055567 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TP9C060B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216620302 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBM-24A18T3N10 |  | 24000 | 16 | 10 | 9.5 | 25000 | 21000 | 84% | 1.8 | 19700 | R-454B
213238567 | 3.5 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9E080C16MP12 | 42000 | 15.9 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.12 | 30400 | R-410A
212437655 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36AX** | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212438158 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215385618 | 1.72 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-24U3SF2 | A(E,F)W244+TDR |  | 20600 | 15.8 | 10 | 8.1 | 23000 | 17700 | 76.96% | 1.98 | 17000 | R-410A
215318732 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBDM-60HWFN10-WC3 |  | 48000 | 17.5 | 12 | 9.5 | 48000 | 48000 | 100% | 2 | 34000 | R-454B
214447344 | 1.75 | Yes | Yes | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-24U3SF2 | A(E,F)M304+TDR |  | 21000 | 16.5 | 10 | 9 | 22800 | 33000 | 144.7% | 1.9 | 31000 | R-410A
216055852 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055871 | 3.42 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055889 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
215851294 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
216055855 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E100C20UH11 | 41000 | 17 | 11 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055921 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055922 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055954 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055988 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC120C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055989 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216056003 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C16SMPS1 | 40000 | 17.5 | 11.5 | 8.1 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
216056004 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES120C16SMPS1 | 41000 | 18 | 11.7 | 8.5 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
216055869 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055870 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E120C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055903 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216055904 | 3.46 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C20MP12 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055939 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
216055952 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055970 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
212621888 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9V120D20MP12 | 30200 | 16.5 | 9.1 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212621890 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9V120D20MP12 | 30600 | 16.6 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
216055549 | 1.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE060A12MP11 | 20400 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216055572 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TP9C080B12MP13 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216055597 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES080B12SMPS1 | 22000 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
216626168 | 3.75 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBM-60C28T6N10 |  | 45000 | 15.2 | 10 | 8.8 | 48000 | 42000 | 87.5% | 1.85 | 34400 | R-454B
216055643 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES080B12SMPS1 | 21600 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216055446 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E080B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055462 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8V080B12MP12 | 22600 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055495 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E060B12MP12 | 22000 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
210321396 | 1.5 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-17HFN1-MT0W | MAC-24HWDN1-MN0-N |  | 18000 | 15.2 | 11.7 | 9.5 | 19500 | 14600 | 74.87% | 2.2 | 13000 | R-410A
214336670 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R801V1505A24UH | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336672 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802V0755A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
212624003 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9Y080B12MP11 | 33200 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624026 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TMLE080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624053 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TMLE080B12MP11 | 33400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624069 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | CPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624078 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.75 | 26000 | R-410A
212624096 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624162 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624253 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212624255 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212624262 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLE080C16MP11 | 32200 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624294 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212624321 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624371 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8V080C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.68 | 25400 | R-410A
212624421 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9Y080C16MP11 | 30800 | 18.2 | 9.2 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624444 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212624505 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | CPLC100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624587 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624596 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8V080C16MP12 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213205692 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96VTN1002122A* | 35200 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
213355438 | 2.92 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48A6 |  | 35000 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
216055670 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055704 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C20MP11 | 31000 | 18 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055736 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055753 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9Y100C16MP11 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
216055771 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
211708435 | 3.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM8E100C16MP11 | 45000 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
211708462 | 3.71 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9E060B12MP12 | 44500 | 15.5 | 11 | 8.1 | 44500 | 31200 | 70.11% | 3 | 30600 | R-410A
211708467 | 3.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM9E080C16MP12 | 45000 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
215385622 | 1.73 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-24U3SF2 | L(E,F)W30D4 |  | 20800 | 15.8 | 10 | 8.1 | 23000 | 17700 | 76.96% | 1.98 | 17000 | R-410A
212348355 | 2.83 | Yes | Yes | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | LEW36D4 |  | 34000 | 18 | 10 | 8.5 | 33400 | 23400 | 70.06% | 2.46 | 23000 | R-410A
215851282 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES120C16SMPS1 | 41000 | 18 | 11.7 | 8.5 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
212624662 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624680 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TPLC080C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624714 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624728 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624812 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TL8E080C16UH11 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624880 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | CP9C100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624882 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | CP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624930 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
216766610 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S9V2C100U5VSB | 43000 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.21 | 29200 | R-454B
216765792 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S8V2B080M4PCB | 23200 | 17.1 | 12.5 | 8.7 | 21800 | 17200 | 78.9% | 2.02 | 15300 | R-454B
216765806 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S9X2B040U3PSB | 23200 | 17.1 | 12.5 | 8.7 | 21800 | 17200 | 78.9% | 2.02 | 15300 | R-454B
216055946 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216765824 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S9V2B060U4VSB | 23200 | 17.1 | 12.5 | 8.7 | 21800 | 17200 | 78.9% | 2.02 | 15400 | R-454B
216765826 | 1.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | S9X1B040D3PSB | 22000 | 16 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2.02 | 15100 | R-454B
216055513 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9V060B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055849 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
213803500 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ET120C20LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.72 | 26400 | R-410A
216055908 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E100C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055935 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
216055976 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C120D20MP13 | 40000 | 17.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055985 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
212625048 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625062 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625105 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625182 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TL8E100C20UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
212625214 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8Y120C20MP11 | 33000 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625241 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TL8E100C20UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625289 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TL8E100C20UH11 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625296 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212625307 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM9V100C20MP12 | 30000 | 17 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.69 | 25800 | R-410A
212625414 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9V100C20MP12 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625482 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8V120C20MP12 | 30600 | 16.2 | 8.7 | 8.4 | 32000 | 27600 | 86.25% | 2.66 | 25000 | R-410A
212625530 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM9Y120D20MP11 | 31000 | 16.2 | 9.2 | 8.3 | 32200 | 28000 | 86.96% | 2.73 | 25200 | R-410A
212625591 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TMLV120C20MP12 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625607 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TPLC120C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625614 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9Y120D20MP11 | 29800 | 15.9 | 9 | 8.5 | 32200 | 28000 | 86.96% | 2.77 | 25200 | R-410A
212625634 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TP9C120D20MP13 | 31800 | 17 | 9.4 | 8.1 | 32200 | 28200 | 87.58% | 2.5 | 25400 | R-410A
214336714 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R801V0755A21UHN | 45500 | 15.2 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.18 | 32400 | R-410A
216055642 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES060B12SMPS1 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18600 | 81.58% | 2 | 18700 | R-454B
216734227 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | 986TD42080C17*** | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
215399910 | 2.55 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR |  | 30600 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.56 | 27000 | R-454B
216055647 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES080B12SMPS1 | 22400 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216055472 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8Y080B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216055517 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9V080B12MP12 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216055625 | 1.68 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES040A10SMPS1 | 20200 | 17.5 | 11.2 | 8.1 | 22600 | 17800 | 78.76% | 2 | 18200 | R-454B
216055634 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z9ES060A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
213803492 | 2.78 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ET100C16LMPS1 | 33400 | 18 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.72 | 26400 | R-410A
212625641 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CPLC120C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625675 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | CPLC100C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625684 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625716 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8V100C20MP12 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625734 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8V120C20MP12 | 32000 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625743 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625757 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TMLV120C20MP12 | 32800 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625773 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TPLC100C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
216765924 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3+P0V0A000M30SD |  | 23200 | 17.1 | 12.5 | 8.7 | 21800 | 17300 | 79.36% | 2.02 | 15400 | R-454B
216765958 | 1.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3+P0V0B000M40SD |  | 22800 | 17.1 | 12.5 | 11 | 21400 | 17000 | 79.44% | 1.99 | 15100 | R-454B
216765974 | 1.87 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3 | S9X1B080D4PSB | 22400 | 15.2 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2.02 | 15100 | R-454B
216765992 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3 | S8V2A040M3PCB | 23800 | 17.1 | 12.5 | 9 | 22000 | 17500 | 79.55% | 2.08 | 15500 | R-454B
216030942 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBDM-48HWFN10-WC3-MAS |  | 48000 | 17.5 | 12 | 9.5 | 48000 | 48000 | 100% | 2 | 34000 | R-454B
216055529 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9Y060B12MP11 | 21600 | 17 | 11 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18500 | R-454B
216055562 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE100B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055563 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE100B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055594 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ES060A12SMPS1 | 21200 | 17.5 | 11.7 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055426 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TL8E060A12UH11 | 21000 | 17.5 | 11.2 | 9 | 22800 | 17900 | 78.51% | 2 | 18300 | R-454B
216055444 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216055445 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
213803493 | 2.78 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ET100C16LMPS1 | 33400 | 18 | 9.5 | 8.4 | 33000 | 30000 | 90.91% | 2.8 | 26600 | R-410A
215407287 | 2.65 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)48D3J+TDR |  | 31800 | 15.2 | 10 | 8.5 | 31400 | 31800 | 101.3% | 2.64 | 27200 | R-454B
215851339 | 3.42 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES100C16SMPS1 | 41000 | 17.5 | 10.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
216055867 | 3.5 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C20MP11 | 42000 | 17 | 10.5 | 8.1 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
216055874 | 3.46 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E130D20MP11 | 41500 | 16.5 | 10.5 | 8.1 | 46000 | 35200 | 76.52% | 2 | 35400 | R-454B
216055881 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
212625798 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9Y120D20MP11 | 31600 | 16.5 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625800 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9Y120D20MP11 | 32000 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625816 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9Y120D20MP11 | 32800 | 16.5 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625834 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | CP9C120D20MP13 | 29400 | 16.3 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625866 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V120D20MP12 | 32800 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625884 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TP9C120D20MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
216055489 | 1.7 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E060A10MP12 | 20400 | 16.5 | 9.8 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18500 | R-454B
216055491 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060A10MP12 | 20600 | 16.5 | 10.5 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18500 | R-454B
216055530 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y060B12MP11 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216055539 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y080B12MP11 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18500 | 81.86% | 2 | 18500 | R-454B
216055548 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE060A12MP11 | 19500 | 17 | 11 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216055555 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055575 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C080B12MP13 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055609 | 1.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ET060A12LMPS1 | 20400 | 18.7 | 11 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18000 | R-454B
216055614 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ET080B12LMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
211708509 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TMLE120C16MP11 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
213612243 | 3.75 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | L(E,G)M60A4 |  | 45000 | 15.5 | 11.8 | 8.1 | 45500 | 37800 | 83.08% | 3.7 | 34600 | R-410A
216055437 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E040A12MP11 | 20800 | 16.5 | 11.7 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216055452 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E100B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
213803498 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ET120C20LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.72 | 26400 | R-410A
213803499 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ET120C20LMPS1 | 33600 | 18.5 | 9.5 | 8.4 | 33000 | 30000 | 90.91% | 2.83 | 26600 | R-410A
216055738 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V100C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055805 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055468 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8Y060A12MP11 | 21000 | 17.5 | 10.5 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216055461 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8V080B12MP12 | 22400 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055477 | 1.72 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E026A08MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 17600 | 77.19% | 2 | 17800 | R-454B
216055478 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E026A08MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216055479 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E026A08MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 17600 | 77.19% | 2 | 17800 | R-454B
216055493 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060B12MP12 | 21600 | 17 | 11 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055494 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E060B12MP12 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18600 | R-454B
213803491 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ET080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.74 | 26400 | R-410A
216055565 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TP9C060B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055574 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TP9C080B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216055599 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES080B12SMPS1 | 22200 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
216055617 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ET080B12LMPS1 | 22200 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
216055633 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES060A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
215399912 | 2.53 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR |  | 30400 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.54 | 27000 | R-454B
216055733 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V080C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216057054 | 1.88 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.72 | 18700 | R-454B
216055423 | 1.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TL8E060A12UH11 | 20400 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18200 | R-454B
216055425 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL8E060A12UH11 | 20600 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18200 | R-454B
216055439 | 1.68 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E060A12MP11 | 20200 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
216055464 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8Y060A12MP11 | 19500 | 17 | 10 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216055466 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8Y060A12MP11 | 21000 | 18 | 10.5 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216055557 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE080B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216056013 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
216055846 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216055662 | 2.58 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055663 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055694 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
215385626 | 2.22 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | L(E,F)W30E4 |  | 26600 | 16 | 10 | 8.1 | 28600 | 23200 | 81.12% | 2.07 | 18700 | R-410A
212349320 | 2.82 | Yes | Yes | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | LEM36F4 |  | 33800 | 17 | 10 | 9 | 33400 | 23400 | 70.06% | 2.61 | 23000 | R-410A
216055629 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES040A10SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17800 | 78.07% | 2 | 18200 | R-454B
216055646 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z9ES080B12SMPS1 | 22600 | 17 | 12 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
216055582 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TPLC080B12MP13 | 22600 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055429 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TL9E060B12UH11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055443 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E060A12MP11 | 20800 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216055476 | 1.64 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E026A08MP12 | 19700 | 16 | 10 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216055509 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V040A10MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 17500 | 76.75% | 2 | 17700 | R-454B
216055511 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9V060B12MP12 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055512 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V060B12MP12 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055526 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055898 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055934 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C20MP11 | 40000 | 16.5 | 10.5 | 8.1 | 45500 | 34800 | 76.48% | 2 | 34400 | R-454B
216055948 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055984 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC100C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055991 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C16SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216056048 | 3.5 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES100C16SMPS1 | 42000 | 18 | 10.5 | 8.5 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
215439671 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*97MC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216055432 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TL9E060B12UH11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055448 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E080B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055507 | 1.72 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9V040A10MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 17500 | 76.75% | 2 | 17700 | R-454B
216055516 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9V060B12MP12 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055525 | 1.72 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9Y040A10MP11 | 20600 | 16.5 | 9.8 | 8.1 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216055735 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V080C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055819 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
216055838 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z9ES080C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 32000 | 24200 | 75.62% | 2 | 26200 | R-454B
216055550 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216055559 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055566 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TP9C060B12MP13 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055591 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES060A12SMPS1 | 20600 | 17.5 | 11.2 | 8.5 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216055598 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES080B12SMPS1 | 22600 | 18 | 12 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
216055632 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES060A10SMPS1 | 19600 | 17 | 11.2 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216055639 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES060B12SMPS1 | 22000 | 17 | 11.7 | 8.5 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
213803494 | 2.78 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ET100C16LMPS1 | 33400 | 18 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.7 | 26400 | R-410A
213493962 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100C20SMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
213493980 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES120C20LMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.64 | 25600 | R-410A
213495298 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ES080C20SMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 28200 | 85.45% | 2.67 | 25600 | R-410A
213495332 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES100C16SMPS1 | 32200 | 18 | 9.4 | 8.5 | 33200 | 28200 | 84.94% | 2.7 | 25600 | R-410A
213495348 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES100C20SMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
216055971 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055987 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216056053 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES100C20SMPS1 | 41000 | 17.5 | 11.2 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
216055752 | 2.58 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 31000 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
216055768 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE100B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055769 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055455 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E100B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055473 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y080B12MP11 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055482 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E040A10MP12 | 19500 | 16 | 10 | 9 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
216055532 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y060B12MP11 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216055584 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES040A12SMPS1 | 19500 | 17 | 11 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216055607 | 1.68 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ET060A12LMPS1 | 20200 | 18.5 | 11.2 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055500 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E080B12MP12 | 21000 | 17 | 11.2 | 9 | 22600 | 18700 | 82.74% | 2 | 18700 | R-454B
216055573 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TP9C080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055580 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
212674080 | 2.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E4 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
216055675 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055543 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE040A12MP11 | 20600 | 16.5 | 11.2 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216055546 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TMLE040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216055579 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TPLC080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055613 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ET080B12LMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
216055627 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES040A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17800 | 78.07% | 2 | 18300 | R-454B
213803490 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ET080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.4 | 33000 | 30000 | 90.91% | 2.85 | 26600 | R-410A
216055679 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E120C16MP11 | 30600 | 18 | 11 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216056033 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES080C16SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
216056065 | 3.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES120D20SMPS1 | 43000 | 17.5 | 11.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
216055499 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E080B12MP12 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
216055506 | 1.64 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V040A10MP12 | 19700 | 16 | 10 | 9 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216055508 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9V040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216055515 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V060B12MP12 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055531 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9Y060B12MP11 | 22000 | 17 | 11.7 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216055787 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080B12MP13 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055802 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC080C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055836 | 2.48 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C16SMPS1 | 29800 | 17.5 | 10.5 | 8.5 | 30400 | 23400 | 76.97% | 2 | 25600 | R-454B
216055837 | 2.45 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z9ES080C16SMPS1 | 29400 | 17.5 | 10.5 | 8.5 | 30400 | 23400 | 76.97% | 2 | 25600 | R-454B
216055587 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES040A12SMPS1 | 20600 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216055602 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES100B12SMPS1 | 19500 | 18 | 11 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
216055651 | 2.6 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL8E080C16UH11 | 31200 | 18 | 10.5 | 8.5 | 31800 | 25600 | 80.5% | 2 | 28000 | R-454B
216055533 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y060B12MP11 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216055624 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES026A08SMPS1 | 21200 | 17.5 | 11.7 | 8.1 | 23000 | 17300 | 75.22% | 2 | 17700 | R-454B
216055440 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E060A12MP11 | 19500 | 17 | 11 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216055449 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8E080B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055458 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8V080B12MP12 | 21200 | 17 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216055483 | 1.72 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E040A10MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216055431 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL9E060B12UH11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
213495271 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ES080C16LMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
216055638 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES060B12SMPS1 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18600 | 81.58% | 2 | 18700 | R-454B
213495357 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES120C16LMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
212674075 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36F4 |  | 33000 | 17 | 9.5 | 8.1 | 31800 | 27000 | 84.91% | 2.72 | 24600 | R-410A
216055650 | 2.62 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 31400 | 18 | 10.5 | 8.5 | 31600 | 25600 | 81.01% | 2 | 28000 | R-454B
216055689 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8V080C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055766 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE100B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055807 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TPLC100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055843 | 2.67 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z9ES100C16SMPS1 | 32000 | 17.5 | 10.5 | 8.1 | 32600 | 24600 | 75.46% | 2 | 26400 | R-454B
215399907 | 1.8 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR |  | 21600 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.63 | 18600 | R-454B
216055435 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E040A12MP11 | 20600 | 16.5 | 11.2 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216055436 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216055453 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E100B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055485 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E040A10MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
216055487 | 1.67 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060A10MP12 | 20000 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18400 | R-454B
216055518 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V080B12MP12 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216055521 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V080B12MP12 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055636 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES060A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216055454 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E100B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055470 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8Y080B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216055503 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E080B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
215934969 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X48M21A*+WALLCON | *96CTN0601714B* | 34600 | 20.5 | 11.5 | 8.5 | 38000 | 27600 | 72.63% | 2.05 | 31200 | R-454B
213896274 | 2.82 | Yes | Yes | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | L(E,G)M36F4 |  | 33800 | 17 | 10 | 9 | 33400 | 23400 | 70.06% | 2.61 | 23000 | R-410A
213495267 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES080B12SMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.66 | 26200 | R-410A
213493888 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES080C16LMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
216055616 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ET080B12LMPS1 | 22600 | 18 | 12 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
212625950 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
216055659 | 2.62 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL9E100C20UH11 | 31400 | 17 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
216055664 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055691 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055698 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080C16MP11 | 31000 | 18 | 11.2 | 8.1 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
214336688 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R921V1005A21M4S | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215679845 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN1002122A* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215679945 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
216764901 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S8X2D120M5PTC | 52000 | 17 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 33800 | R-454B
216055730 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9V080B12MP12 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055496 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E060B12MP12 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18600 | R-454B
216055510 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9V040A10MP12 | 21200 | 17 | 10.5 | 8.5 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216055794 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055696 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
215677005 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0902120B* | 57000 | 18.5 | 9.5 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
216055701 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 31000 | 18 | 11.2 | 8.1 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
214336696 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R962V0855A21M4S | 51500 | 17 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215679835 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN0802120A* | 34000 | 16 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.76 | 30600 | R-454B
216055484 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
216055501 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E080B12MP12 | 22000 | 17 | 11.7 | 8.5 | 22400 | 18700 | 83.48% | 2 | 18700 | R-454B
216055520 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9V080B12MP12 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
215679925 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1202422A* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
216055695 | 2.57 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y080B12MP11 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27200 | R-454B
216055745 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
216055793 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055810 | 2.53 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES080B12SMPS1 | 30400 | 18 | 11.2 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216055811 | 2.6 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES080C16SMPS1 | 31200 | 18 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055812 | 2.62 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C16SMPS1 | 31400 | 18 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216030944 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBDM-36HWFN10-WB3-MAS |  | 36000 | 18 | 12 | 10 | 37000 | 37400 | 101.1% | 1.9 | 31000 | R-454B
213493875 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES080B12LMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.66 | 26200 | R-410A
213493941 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES100C16SMPS1 | 31200 | 17.8 | 9.3 | 8.3 | 33000 | 28200 | 85.45% | 2.66 | 25600 | R-410A
213495344 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ES100C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
216055427 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TL9E060B12UH11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055428 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TL9E060B12UH11 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216623449 | 3 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBM-36B24T4N10-MAS |  | 36000 | 15.8 | 10.7 | 9.4 | 38000 | 36000 | 94.74% | 1.9 | 29200 | R-454B
216623450 | 3 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBM-36C24T4N10-MAS |  | 36000 | 15.8 | 10.7 | 9.4 | 38000 | 36000 | 94.74% | 1.9 | 29200 | R-454B
216030943 | 4.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBDM-60HWFN10-WC3-MAS |  | 54000 | 17.5 | 12 | 9.5 | 55000 | 54000 | 98.18% | 1.9 | 35000 | R-454B
216055519 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9V080B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055537 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9Y080B12MP11 | 22000 | 17 | 11.7 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18500 | R-454B
216055552 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TMLE060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216055569 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C060B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
214574103 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X61L21A*+WALLCON | *95CSU0802120B* | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 25000 | 78.12% | 2 | 31200 | R-410A
214574603 | 2.68 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D,W)4X48L21**+WALLCON | *97CMN0602120B* | 32200 | 17 | 11.5 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31800 | R-410A
213493958 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES100C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
213494023 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ET100C20LMPS1 | 32200 | 18.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
213495413 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ET120C20LMPS1 | 31200 | 18.3 | 9.3 | 8.3 | 33000 | 27800 | 84.24% | 2.66 | 25400 | R-410A
216055666 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055673 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216734069 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *92MSN0601714A* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216734272 | 1.85 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *96VTN0601716B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216732649 | 1.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *80CSU0401712A* | 22600 | 17 | 10.5 | 8.5 | 21400 | 19300 | 90.19% | 1.96 | 18200 | R-454B
216055705 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y100C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055721 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9E100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055653 | 2.6 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL8E100C20UH11 | 31200 | 17 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055671 | 2.58 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
213841888 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG80936 | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
214336694 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R951V1155A24M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
213494011 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ET100C16LMPS1 | 31200 | 17.8 | 9.3 | 8.3 | 33000 | 27800 | 84.24% | 2.66 | 25400 | R-410A
213494027 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ET120C20LMPS1 | 31200 | 18.3 | 9.3 | 8.3 | 33000 | 27800 | 84.24% | 2.66 | 25400 | R-410A
213495242 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES040A12LMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
213493868 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES040A12SMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
213613564 | 1.46 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24E4 |  | 17500 | 15.2 | 9.8 | 8.2 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
216620306 | 3 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBM-36B24T4N10 |  | 36000 | 15.8 | 10.7 | 9.4 | 38000 | 36000 | 94.74% | 1.9 | 29200 | R-454B
213493922 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100B12LMPS1 | 32200 | 18.5 | 9.4 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
216055749 | 2.62 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080C16MP11 | 31400 | 18 | 10.5 | 8.5 | 31800 | 25800 | 81.13% | 2 | 28000 | R-454B
216055806 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055826 | 2.62 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES120C16SMPS1 | 31400 | 18 | 11 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216766054 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S8V2B080M4PDB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216055623 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES026A08SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
216055641 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES060B12SMPS1 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
216766646 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S9V2C080U5VSB | 51000 | 15.2 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34200 | R-454B
212674054 | 2.92 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M36E4 |  | 35000 | 18 | 9 | 8.1 | 35400 | 26000 | 73.45% | 2.81 | 25400 | R-410A
213204392 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0451412A* | 23800 | 16.5 | 10.4 | 8.5 | 26000 | 24800 | 95.38% | 2.54 | 24400 | R-410A
213204410 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)0701412A* | 23800 | 17 | 10 | 8.5 | 26200 | 25600 | 97.71% | 2.52 | 24800 | R-410A
213204803 | 1.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0902120A* | 23200 | 16.7 | 10 | 8.3 | 25600 | 20000 | 78.12% | 2.92 | 18800 | R-410A
213204810 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0902120A* | 23800 | 17 | 10.3 | 8.5 | 25800 | 20000 | 77.52% | 2.98 | 18900 | R-410A
213204837 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN0401712A* | 23400 | 16 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.87 | 19100 | R-410A
213204844 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN0401712A* | 23800 | 16 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.87 | 19100 | R-410A
213204846 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92ESN0401712A* | 23800 | 16 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.87 | 19100 | R-410A
211627569 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TL8E100C20UH11 | 31200 | 17.4 | 9.8 | 8.3 | 25200 | 31800 | 126.2% | 2.84 | 25400 | R-410A
213204921 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *95ESN0401410A* | 23800 | 15.2 | 10 | 8.5 | 26600 | 20600 | 77.44% | 2.84 | 19400 | R-410A
213204944 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *95ESN0601412A* | 23200 | 15.8 | 9.8 | 8.4 | 26000 | 20400 | 78.46% | 2.92 | 19100 | R-410A
213204953 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0601714A* | 23400 | 16.3 | 10.2 | 8.4 | 26000 | 20200 | 77.69% | 2.94 | 19000 | R-410A
216055817 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
216055824 | 2.65 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C20SMPS1 | 31800 | 18 | 10.5 | 8.5 | 31600 | 25400 | 80.38% | 2 | 27600 | R-454B
216732851 | 1.82 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *97CMN0601714B* | 21800 | 15.5 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 17900 | R-454B
215374763 | 3.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-42HFN10-M3X-D | MVBC-48HWFN10-MD3E-DD |  | 42000 | 16.7 | 11.7 | 9.5 | 50000 | 46000 | 92% | 1.9 | 37000 | R-454B
213238592 | 3.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM9Y100C16MP11 | 43500 | 16.2 | 11 | 8.4 | 44500 | 31200 | 70.11% | 3.21 | 30600 | R-410A
215669087 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *96CTN1002122B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
214336702 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R98MV0855A21UPS | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
210191039 | 3.92 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30U-48HFN1-M-[X] | MVC-48HWFN1-MQ3 |  | 47000 | 15.6 | 8.2 | 9.4 | 50000 | 46000 | 92% | 1.85 | 36000 | R-410A
215678145 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN1002122B* | 55500 | 17 | 8.5 | 8.5 | 60000 | 42000 | 70% | 1.9 | 51500 | R-454B
213828552 | 3.42 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)43E44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
212159705 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE33936 | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
211627753 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 25400 | 31600 | 124.4% | 2.87 | 25400 | R-410A
211628338 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.84 | 25600 | R-410A
211628403 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 25200 | 31400 | 124.6% | 2.85 | 25200 | R-410A
212973237 | 2 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *96VSN0401712B* | 24000 | 16 | 10 | 8.1 | 25400 | 22000 | 86.61% | 1.82 | 18900 | R-410A
212973907 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *96VSN0801716B* | 23400 | 16.5 | 10 | 8.1 | 25800 | 24200 | 93.8% | 2 | 18900 | R-410A
213204389 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0451412A* | 23800 | 16.4 | 10.3 | 8.5 | 26000 | 26000 | 100% | 2.76 | 25200 | R-410A
216766650 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S9X1C080U5PSB | 51000 | 15.2 | 10 | 8.7 | 52000 | 39000 | 75% | 2.18 | 34400 | R-454B
216770080 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S8X1D120M5PSC | 51500 | 16 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34400 | R-454B
213204994 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0401410A* | 23400 | 16 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
213204996 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0401410A* | 23200 | 16 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
214264143 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J936 | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
213828551 | 3.42 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)43D44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
216679735 | 1.45 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CSPH*2412AL* | 927TA48060V17*** | 17400 | 15.5 | 10 | 8.1 | 18100 | 18400 | 101.7% | 2.05 | 12200 | R-410A
213828553 | 3.38 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)49C44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213828555 | 3.38 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)61B44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
215402628 | 1.93 | No | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | L(E,F)W30C4 |  | 23200 | 16 | 9.8 | 8.5 | 25600 | 19900 | 77.73% | 2.9 | 18700 | R-410A
215318730 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBDM-24HWFN10-WA3 |  | 18000 | 19 | 12.5 | 10.2 | 18000 | 18600 | 103.3% | 2.12 | 14700 | R-454B
212621906 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
216770117 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TAMXD06AV41 |  | 43500 | 16 | 12 | 8.7 | 44500 | 32400 | 72.81% | 2.17 | 29400 | R-454B
216766330 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9X1B040U3PSB | 33200 | 17 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.17 | 21400 | R-454B
216030932 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBDM-18HWFN10-WA3-MAS |  | 18000 | 19 | 12.5 | 10.1 | 18000 | 18600 | 103.3% | 2.12 | 14700 | R-454B
216766682 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S9X2C080U5PSB | 52500 | 16 | 11 | 8.7 | 51000 | 38500 | 75.49% | 2.21 | 34200 | R-454B
216055767 | 2.58 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055776 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE120C16MP11 | 30800 | 18 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055790 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055840 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z9ES080C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 32000 | 24200 | 75.62% | 2 | 26200 | R-454B
209960477 | 4.58 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30U-55HFN1-MQ3 | MVC-60HWFN1-MR0 |  | 55000 | 15.3 | 8.8 | 9.4 | 59000 | 48500 | 82.2% | 1.91 | 42000 | R-410A
214861555 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3 | MVBC-48HWFN10-MD3E |  | 48000 | 16 | 10 | 8.5 | 48000 | 38000 | 79.17% | 1.85 | 32400 | R-454B
215677025 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *95CSU0802120B* | 56500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.06 | 56000 | R-454B
215677075 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN1002122B* | 56500 | 18.5 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56000 | R-454B
216764903 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S8X2D120M5PSC | 52000 | 17 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 33800 | R-454B
216764905 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S8X2C080M5PTC | 52500 | 16.5 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 34000 | R-454B
210321397 | 1.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-24HFN1-MU0W | MAC-24HWDN1-MN0-N |  | 23000 | 15.2 | 11.7 | 9.8 | 24600 | 23000 | 93.5% | 2.08 | 22000 | R-410A
214861529 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN10-M1X | MVBC-24HWFN10-MB1 |  | 23000 | 18.8 | 12 | 10 | 26000 | 23600 | 90.77% | 2.16 | 16900 | R-454B
213204909 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *95ESN0261410A* | 23000 | 16.5 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
214447345 | 3.75 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-48U3SP2 | A(E,F)M494+TDR |  | 45000 | 17.2 | 9.8 | 8.1 | 46500 | 33000 | 70.97% | 1.9 | 31000 | R-410A
213828520 | 2.43 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)30C44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215677145 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *95CSU0802120B* | 56500 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
212976077 | 2.05 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *96VTN0801716B* | 24600 | 17 | 10.5 | 8.5 | 25200 | 21200 | 84.13% | 1.78 | 18700 | R-410A
212976695 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *96VTN1002120B* | 23600 | 17 | 10.5 | 8.5 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
213781181 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *80CTL0901716B* | 33000 | 17 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
213781331 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L21A*+WALLCON | *95CSU0601716B* | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.94 | 31600 | R-410A
216055441 | 1.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E060A12MP11 | 20400 | 17.5 | 11.2 | 8.5 | 22800 | 17900 | 78.51% | 2 | 18100 | R-454B
216055457 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8V080B12MP12 | 21600 | 17 | 11.7 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216680839 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 927TA48080V17*** | 17200 | 16 | 10.5 | 8.5 | 18100 | 19200 | 106.1% | 2.2 | 12200 | R-410A
212159503 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H***P449 | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
214573703 | 2.73 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X37L21A*+WALLCON | *97CMN0602120B* | 32800 | 17 | 11 | 8.5 | 33000 | 25400 | 76.97% | 1.98 | 32000 | R-410A
212159733 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE32936 | A80UH2E090B12 | 23800 | 21 | 13 | 8.45 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
211627595 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TL9E080C16UH11 | 31200 | 17.4 | 9.3 | 8.3 | 25600 | 32200 | 125.8% | 2.8 | 25800 | R-410A
213146640 | 3.08 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H175P159+AEFE4B* |  | 37000 | 16 | 10 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
213306295 | 2.9 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D34+TDR | Z8ES080C20LMPS1 | 34800 | 17 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
216620293 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBL-24HWFN10-MI3 |  | 24000 | 16 | 10 | 9 | 25000 | 19000 | 76% | 1.8 | 19800 | R-454B
216766040 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S9X1B080U4PSB | 33600 | 16.5 | 12 | 8.7 | 32800 | 24400 | 74.39% | 2.18 | 21600 | R-454B
216766110 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S9X2B060D3PSB | 33200 | 17 | 12 | 8.5 | 33400 | 24400 | 73.05% | 2.09 | 21600 | R-454B
211627675 | 2.68 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8E100B12MP11 | 32200 | 18 | 9.9 | 8.5 | 25400 | 31600 | 124.4% | 2.84 | 25400 | R-410A
211627777 | 2.55 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM8V120C20MP12 | 30600 | 16.2 | 8.7 | 8.3 | 25000 | 31600 | 126.4% | 2.82 | 25200 | R-410A
213781431 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *97CMN1002122B* | 32400 | 17 | 11 | 8.5 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213781501 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X60L24A*+WALLCON | *97CMN1002122B* | 32800 | 17.5 | 11.5 | 8.1 | 31800 | 24600 | 77.36% | 1.98 | 30800 | R-410A
216620304 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBM-24A18T3N10 |  | 24000 | 16 | 10 | 9 | 25000 | 19000 | 76% | 1.8 | 19700 | R-454B
215677445 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *80CTL0702120B* | 56000 | 18 | 9 | 9 | 63500 | 45000 | 70.87% | 2.06 | 56000 | R-454B
211708469 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM9E080C20MP12 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
216766126 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C005AS3 | S9V2C080U5VSB | 32400 | 16.5 | 12 | 8.7 | 32000 | 23800 | 74.38% | 2.13 | 21000 | R-454B
216766174 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 | S8V2C100M5PDB | 34200 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.22 | 21200 | R-454B
213796168 | 1.88 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE33936+AEFE3A* |  | 22600 | 20 | 13 | 8.45 | 20600 | 15600 | 75.73% | 2.2 | 13200 | R-410A
212159680 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H175P149 | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
213796566 | 1.48 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P219+CBPE3A* |  | 17800 | 15.5 | 10.5 | 9 | 17100 | 19400 | 113.5% | 2.4 | 11500 | R-410A
216030941 | 4.5 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-60HFN10-M3 | MVBC-60HWFN10-MD3E-MAS |  | 54000 | 15.2 | 8.6 | 8.4 | 54000 | 38000 | 70.37% | 1.8 | 33000 | R-454B
212674055 | 2.92 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48A4 |  | 35000 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
216623445 | 1.5 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBM-24B18T3N10-MAS |  | 18000 | 16.1 | 11.7 | 9.5 | 19000 | 18000 | 94.74% | 2.06 | 15200 | R-454B
216680887 | 1.46 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CSPH*3012AL* | 927TA48080V17*** | 17500 | 15.5 | 10.5 | 8.1 | 18000 | 18100 | 100.6% | 2 | 12200 | R-410A
216684113 | 3.75 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBM-60C28T6N10-MAS |  | 45000 | 15.2 | 10 | 8.8 | 48000 | 42000 | 87.5% | 1.85 | 34400 | R-454B
215285715 | 2.93 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y91E080C16SMPS1 | 35200 | 17 | 8 | 8.5 | 36000 | 25200 | 70% | 2.06 | 26600 | R-410A
214264154 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
213146643 | 3 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H***P449+AEFE3A* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
213753766 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC2E080M21**20 | 35000 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
207802615 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MU0W | MVC-23HWFN1-M |  | 23000 | 18.4 | 11.7 | 9.3 | 26000 | 21200 | 81.54% | 1.9 | 16900 | R-410A
213753773 | 2.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC2E100M21**22 | 34800 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
216766192 | 2.83 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 | S9X2C100U5PSB | 34000 | 15.2 | 12 | 9 | 32400 | 24000 | 74.07% | 2.21 | 21200 | R-454B
216766208 | 2.73 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD05AS3 | S9X2C100D5PSB | 32800 | 15.2 | 12 | 8.2 | 33400 | 24400 | 73.05% | 1.99 | 21600 | R-454B
216766226 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD09AS3 | S9X1C100D5PSB | 34400 | 16 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.17 | 21400 | R-454B
216766274 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S9X1B080U4PSB | 32200 | 16 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.11 | 21000 | R-454B
215865886 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBC-48HWFPN10-MD3E |  | 48000 | 16.5 | 10.5 | 9.5 | 50000 | 46000 | 92% | 1.9 | 37000 | R-454B
213306313 | 2.9 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D34+TDR | Z8ES100C20LMPS1 | 34800 | 16.5 | 9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
215681925 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0802120B* | 48500 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.12 | 46000 | R-454B
215675205 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0902120B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33600 | 70% | 2.06 | 42000 | R-454B
216766730 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S8V2D120M5PCB | 51000 | 15.2 | 11.2 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34000 | R-454B
215940543 | 2.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *97CTN0601716A* | 34000 | 20 | 11 | 8.5 | 39500 | 28800 | 72.91% | 2.02 | 32800 | R-454B
215940743 | 2.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN0802120A* | 35000 | 21 | 12 | 8.5 | 38500 | 28400 | 73.77% | 2.04 | 32600 | R-454B
215940793 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN1002122A* | 35400 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215940843 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *97CTN0601716A* | 35200 | 21 | 11.7 | 8.5 | 38500 | 29200 | 75.84% | 2 | 33400 | R-454B
212506703 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE9J936 | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213088112 | 1.92 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | V,A,D36H***D129+AEFE3A* |  | 23000 | 20 | 12.5 | 8.45 | 20400 | 15000 | 73.53% | 2.04 | 13900 | R-410A
216766660 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S8V2D120M5PDB | 51000 | 15.2 | 11.2 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34000 | R-454B
216766692 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S8V2D120M5PDB | 52500 | 16 | 11.2 | 9 | 50500 | 38500 | 76.24% | 2.23 | 33800 | R-454B
214802830 | 3.29 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | D(A,C,E)60C34+TDR | R801V1005A21DZ | 39500 | 15.6 | 10.1 | 8.1 | 40000 | 28600 | 71.5% | 2.95 | 30000 | R-410A
216765840 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | S9X2B060U4PSB | 23800 | 17.1 | 12.5 | 9 | 21800 | 17400 | 79.82% | 2.08 | 15400 | R-454B
215679255 | 2.8 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *97CTN0601716A* | 33600 | 17 | 9 | 9 | 36000 | 25800 | 71.67% | 1.88 | 31000 | R-454B
215679405 | 2.77 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CTN1002122A* | 33200 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.84 | 31000 | R-454B
216055652 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TL8E100C20UH11 | 31000 | 17 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055486 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18400 | R-454B
216055553 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TMLE080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055571 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TP9C080B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216055434 | 1.65 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E040A12MP11 | 19800 | 16 | 11.2 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215679605 | 2.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712B* | 35000 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
216680851 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2517AL* | 927TA48080V17*** | 17700 | 16.5 | 10.5 | 8.5 | 17600 | 17500 | 99.43% | 1.94 | 12000 | R-410A
216770090 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*CD09AS3 | *DHMC100CCV4 | 23600 | 17.1 | 13 | 8.7 | 21400 | 17000 | 79.44% | 2.02 | 15100 | R-454B
215941243 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0802120A* | 45000 | 20 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
215677555 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN1202422B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
211628405 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TPLC120C20MP13 | 31000 | 16.3 | 8.8 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
211628470 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | YP9C100C20MP13 | 31600 | 17.5 | 9.3 | 8.1 | 34000 | 28000 | 82.35% | 2.53 | 25800 | R-410A
215385627 | 2.23 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-36U3SA2 | L(E,F)W30F4 |  | 26800 | 16 | 10 | 8.1 | 28600 | 23200 | 81.12% | 2.07 | 18700 | R-410A
216620292 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBL-24HWFN10-MI3 |  | 24000 | 17.5 | 10.8 | 9.2 | 26000 | 20000 | 76.92% | 1.9 | 19800 | R-454B
214861539 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBC-18HWFN10-MB3E |  | 18000 | 19 | 12.5 | 9.8 | 19000 | 18000 | 94.74% | 2 | 15000 | R-454B
215676755 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL1102120B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
215676825 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0801714B* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.02 | 46000 | R-454B
214264212 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
213752307 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*B070V17**16 | 23400 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.9 | 20000 | R-410A
213752457 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC6A060M14**12 | 22600 | 15.8 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.9 | 19700 | R-410A
215679855 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN1202422A* | 34000 | 16 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
211627751 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM8V100C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 25200 | 31800 | 126.2% | 2.82 | 25400 | R-410A
216766360 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 | S8V2C100M5PDB | 32600 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.13 | 21200 | R-454B
216766374 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | S8V2C080M5PDB | 33800 | 17 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.19 | 21400 | R-454B
216766392 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3+P0V0C000M50SD |  | 34000 | 17.1 | 12.5 | 9 | 32600 | 24000 | 73.62% | 2.22 | 21200 | R-454B
216766394 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC009AS3 | S8V2C080M5PDB | 34200 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.21 | 21400 | R-454B
216766408 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC009AS3 | S9V2C080U5VSB | 34200 | 17.1 | 12.5 | 9 | 32200 | 24000 | 74.53% | 2.23 | 21200 | R-454B
216766410 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC009AS3 | S9V2C100U5VSB | 34000 | 17.1 | 12 | 9 | 32200 | 23800 | 73.91% | 2.21 | 21200 | R-454B
213205522 | 2.88 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0901714A* | 34600 | 16 | 9.9 | 8.5 | 38500 | 31400 | 81.56% | 2.75 | 29000 | R-410A
213205613 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *92ESN1002122A* | 35400 | 15.5 | 10 | 8.5 | 39500 | 31600 | 80% | 2.71 | 29400 | R-410A
216699821 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | DFVE48DP1300A* |  | 34200 | 19 | 11.7 | 9.2 | 33400 | 33000 | 98.8% | 2.1 | 32000 | R-32
212498324 | 1.48 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CE2403C+TXV |  | 17700 | 17 | 11 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
216055590 | 1.64 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES060A12SMPS1 | 19700 | 17 | 11.2 | 9 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055592 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES060A12SMPS1 | 21000 | 17.5 | 11.7 | 9 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055615 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ET080B12LMPS1 | 22000 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
216055856 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055890 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y080C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055924 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055931 | 3.29 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055940 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055990 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216770116 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TAM5D06AC41 |  | 43500 | 16 | 12 | 8.5 | 43500 | 31800 | 73.1% | 2.16 | 29000 | R-454B
216055722 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055665 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C16MP11 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055674 | 2.62 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C16MP11 | 31400 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
214802748 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0503A14UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20000 | 70.42% | 2.63 | 20800 | R-410A
211627978 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9V060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
215679905 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN0802120A* | 34200 | 16 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
212365391 | 3.75 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOE30U-45HFN1-M | MAC-60HWDN1-MN0 |  | 45000 | 15.2 | 10 | 9.2 | 55000 | 46500 | 84.55% | 1.8 | 37000 | R-410A
215877110 | 1.88 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | L(E,F)W30B4 |  | 22600 | 15.2 | 9.5 | 8.1 | 25400 | 19800 | 77.95% | 2.8 | 18600 | R-410A
215934700 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X32M17A*+WALLCON | *96CTN0401410B* | 33800 | 19.5 | 11.5 | 8.1 | 37200 | 26600 | 71.51% | 2.02 | 29200 | R-454B
215934920 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CMN0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
215935000 | 2.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *80CTL0451712B* | 35200 | 21 | 11.7 | 8.5 | 39000 | 29400 | 75.38% | 2 | 33600 | R-454B
215932210 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU1002120A* | 32600 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30800 | R-454B
215449739 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBDM-36HWFN10-WB3-D |  | 36000 | 18 | 12 | 10 | 37000 | 37400 | 101.1% | 1.9 | 31000 | R-454B
215933490 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN1002122B* | 33600 | 19 | 11.5 | 9 | 34600 | 26600 | 76.88% | 1.94 | 30400 | R-454B
215682435 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0802120B* | 48500 | 19 | 10.5 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676015 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *95CSU0802120B* | 48500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
216766668 | 4.33 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S9X1D120U5PSB | 52000 | 15.2 | 11.2 | 9 | 50500 | 38500 | 76.24% | 2.23 | 33600 | R-454B
216766700 | 4.21 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8V2C080M5PDB | 50500 | 15.2 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.17 | 34000 | R-454B
215677065 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN1002122B* | 56500 | 18.5 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56000 | R-454B
216766720 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S9X1D120U5PSB | 51000 | 15.2 | 11.2 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34000 | R-454B
216766768 | 4.38 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S8V2C100M5PDB | 52500 | 15.2 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.22 | 34000 | R-454B
215679955 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0601716B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 30000 | R-454B
212160153 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE33936 | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
210473280 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA3* | EA*4X48L21A*+WALLCON | *95CSU0802120A* | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
210473445 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA3* | EA*4X48L24A*+WALLCON | *95CSU0802120A* | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
210474601 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA3* | EHD4X48AAL+WALLCON | *97CMN1002122A* | 24200 | 16 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.04 | 20600 | R-410A
214570523 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X42L21A*+WALLCON | *97CMN0602120B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
213796207 | 1.9 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | F,PE*G33925 |  | 22800 | 21 | 13 | 8.45 | 20600 | 15600 | 75.73% | 2.2 | 13200 | R-410A
213205663 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *95ESN1202422A* | 35400 | 15.5 | 10 | 8.1 | 39500 | 31600 | 80% | 2.72 | 29400 | R-410A
213205670 | 2.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *95ESN1402422A* | 35400 | 15.2 | 9.9 | 8.5 | 39500 | 31200 | 78.99% | 2.74 | 29200 | R-410A
213205672 | 2.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *95ESN1402422A* | 35400 | 15.2 | 9.9 | 8.5 | 39500 | 31200 | 78.99% | 2.74 | 29200 | R-410A
213796167 | 1.9 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE33936+AEFE4B* |  | 22800 | 21 | 13 | 8.45 | 20600 | 15600 | 75.73% | 2.2 | 13200 | R-410A
215865883 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBC-24HWFPN10-MB3E |  | 24000 | 18.1 | 11 | 9.7 | 26000 | 21600 | 83.08% | 1.87 | 20000 | R-454B
216030937 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBC-24HWFN10-MB3E-MAS |  | 24000 | 18.1 | 11 | 9.7 | 26000 | 21600 | 83.08% | 1.87 | 20000 | R-454B
215681745 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1202422A* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215675995 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL1102120B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
213204441 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0702116A* | 23800 | 17 | 10 | 8.1 | 26200 | 26800 | 102.3% | 2.7 | 25600 | R-410A
212974944 | 2 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X25L17A* | *96VTN0401410B* | 24000 | 16 | 10 | 8.1 | 25200 | 22000 | 87.3% | 1.82 | 18700 | R-410A
215676765 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *95CSU0601716B* | 48000 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 2 | 47000 | R-454B
215676915 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN0802120B* | 48500 | 19 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
214264204 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212594778 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DD14936 | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213821321 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0801716B* | 23200 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.91 | 19000 | R-410A
213205583 | 2.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92ESN0601714A* | 35200 | 16 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.53 | 29400 | R-410A
213205616 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *92ESN1002122A* | 35400 | 15.5 | 10 | 8.5 | 39500 | 31600 | 80% | 2.71 | 29400 | R-410A
215934850 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CTL0902120B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.02 | 32600 | R-454B
215934900 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CMN0602120B* | 35400 | 21 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33200 | R-454B
215323719 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBDM-36HWFN10-WB3 |  | 36000 | 18 | 12 | 10 | 37000 | 37400 | 101.1% | 1.9 | 31000 | R-454B
215931810 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU1002120A* | 56000 | 18 | 11 | 8.1 | 61000 | 46000 | 75.41% | 1.95 | 47500 | R-454B
216766070 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD04AS3 | S9X1B080D4PSB | 32400 | 16 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.97 | 21600 | R-454B
215933020 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X30M12A*+WALLCON | *96CTN0601714B* | 32400 | 18 | 10 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
214608433 | 4.58 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-60U3SP2 | AE(D,N,U)+DM60B44+TDR |  | 55000 | 16 | 8 | 8.1 | 56000 | 40000 | 71.43% | 1.9 | 40000 | R-410A
213204808 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0902120A* | 23600 | 16.9 | 10.3 | 8.4 | 25800 | 20000 | 77.52% | 2.95 | 18900 | R-410A
213204825 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN0401410A* | 23200 | 15.4 | 9.8 | 8.5 | 26000 | 20400 | 78.46% | 2.94 | 19100 | R-410A
213204839 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *92ESN0401712A* | 23400 | 16 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.87 | 19100 | R-410A
213204858 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92ESN0601412A* | 23600 | 17 | 10 | 8.5 | 25600 | 20000 | 78.12% | 2.87 | 18800 | R-410A
213204925 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0401410A* | 23800 | 15.2 | 10 | 8.5 | 26600 | 20600 | 77.44% | 2.84 | 19400 | R-410A
215681845 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU0802120B* | 48500 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.12 | 46000 | R-454B
215676615 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CTL0902120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215676775 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *95CSU0802120B* | 48500 | 18.5 | 10 | 9 | 50000 | 37000 | 74% | 2 | 47000 | R-454B
215676875 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *80CTL0902120B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
215676195 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *80CTL0702120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2.02 | 46000 | R-454B
215676295 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL0702120B* | 47500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
213161304 | 1.93 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H***P449+AEFE3A* |  | 23200 | 20 | 13.5 | 8.7 | 20600 | 15700 | 76.21% | 2.26 | 13300 | R-410A
216620305 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBM-24B18T3N10 |  | 24000 | 16 | 10 | 9 | 25000 | 19000 | 76% | 1.8 | 19700 | R-454B
215939623 | 2.7 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0601716B* | 32400 | 19.5 | 11 | 9.5 | 35000 | 27000 | 77.14% | 2 | 30800 | R-454B
215939673 | 2.73 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0601716B* | 32800 | 20 | 11.5 | 9.5 | 34800 | 26600 | 76.44% | 2 | 30600 | R-454B
215939723 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0802120B* | 33400 | 20 | 11.5 | 9.5 | 34600 | 26400 | 76.3% | 2.04 | 30200 | R-454B
215939773 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0802120A* | 33400 | 20 | 11.5 | 9.5 | 34600 | 26400 | 76.3% | 2.04 | 30200 | R-454B
215675225 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL1352422B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33600 | 70% | 2.06 | 42000 | R-454B
215675625 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215931550 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0902120B* | 56000 | 18.5 | 11.5 | 8.5 | 60500 | 45500 | 75.21% | 2.06 | 47000 | R-454B
215931650 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1202422B* | 56000 | 18.5 | 11 | 8.5 | 60500 | 46000 | 76.03% | 2.06 | 47500 | R-454B
211627887 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9E060A10MP12 | 32600 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.48 | 25400 | R-410A
211627935 | 2.68 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9E100C16MP12 | 32200 | 18 | 9.9 | 8.5 | 25200 | 31400 | 124.6% | 2.86 | 25200 | R-410A
216764761 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S8X2C080M5PSC | 43500 | 17.1 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29200 | R-454B
216764946 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8X2B060M4PSC | 32600 | 17.1 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.9 | 21600 | R-454B
215931560 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1102120B* | 56000 | 18.5 | 11.5 | 8.5 | 60500 | 45500 | 75.21% | 2.06 | 47000 | R-454B
215931760 | 4.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1002122B* | 57000 | 18.5 | 11.5 | 8.5 | 60500 | 46500 | 76.86% | 2.02 | 48000 | R-454B
215931501 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | FCMA5B48L0C*+WALLCON |  | 34400 | 21.5 | 12.5 | 9.5 | 34200 | 25800 | 75.44% | 2.06 | 29800 | R-454B
215932060 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0451712B* | 32000 | 19 | 10 | 9 | 36000 | 27800 | 77.22% | 1.88 | 31800 | R-454B
213796208 | 1.92 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | F,PE*E34930 |  | 23000 | 21 | 13 | 8.55 | 20600 | 15700 | 76.21% | 2.24 | 13200 | R-410A
216766809 | 1.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S9X1B060D3PSB | 22200 | 16 | 11.7 | 8.7 | 21400 | 17100 | 79.91% | 2.03 | 15200 | R-454B
216766708 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8V2D120M5PDB | 51000 | 15.2 | 11 | 8.7 | 51000 | 38500 | 75.49% | 2.19 | 33600 | R-454B
216766710 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8V2C100M5PDB | 51000 | 15.2 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.18 | 34000 | R-454B
216766827 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD04AS3 | S8V2A040M3PDB | 23400 | 17 | 12 | 8.1 | 22400 | 17200 | 76.79% | 1.83 | 15400 | R-454B
216766842 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S9V2B040D3VSB | 23800 | 17.5 | 12.7 | 8.5 | 22200 | 17400 | 78.38% | 1.97 | 15500 | R-454B
216766844 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S9X1B060D3PSB | 23800 | 17.5 | 12.7 | 8.5 | 22200 | 17400 | 78.38% | 1.97 | 15500 | R-454B
216766859 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S9X1B040D3PSB | 21600 | 15.5 | 11.5 | 8.5 | 21200 | 16800 | 79.25% | 1.91 | 14900 | R-454B
215797518 | 3 | Yes | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3X | MVBC-36HWFN10-MC3E-D |  | 36000 | 16.5 | 10 | 8.2 | 37000 | 32000 | 86.49% | 1.85 | 23200 | R-454B
213088242 | 3 | Yes | No | ARCOAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG35936+AEFE4B* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
212437660 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
216030945 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBE-24HWFN10-WM3E-MAS |  | 24000 | 17.4 | 10.8 | 10.4 | 25000 | 19600 | 78.4% | 1.96 | 20800 | R-454B
213205502 | 2.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0701712A* | 34400 | 15.5 | 9.9 | 8.5 | 38500 | 31400 | 81.56% | 2.71 | 29000 | R-410A
213367837 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36A44+TDR | Y81E080C20SMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
212979891 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *80MS(N,L)0901714A* | 24200 | 17.5 | 10 | 8.5 | 25200 | 21800 | 86.51% | 1.82 | 18700 | R-410A
212980275 | 2.03 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *80MS(N,L)0902116A* | 24400 | 17.5 | 10.5 | 8.5 | 25200 | 21200 | 84.13% | 1.8 | 18600 | R-410A
215940973 | 3.58 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0801716A* | 43000 | 20 | 10.5 | 9.5 | 48500 | 37400 | 77.11% | 2 | 40000 | R-454B
215675395 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CTL1102120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
214570743 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X48L24A*+WALLCON | *95CSU0802120B* | 24000 | 16.5 | 11 | 8.5 | 21000 | 16600 | 79.05% | 2.02 | 20400 | R-410A
215434360 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*97MC1205DNA* | 45500 | 16.5 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
215434375 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA6030*3A* | D*80TC0804C*A* | 45500 | 16.5 | 10 | 8.5 | 46500 | 33600 | 72.26% | 2 | 29000 | R-32
212977592 | 2.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X25L17A* | *80MS(N,L)0451412A* | 24200 | 17 | 10 | 8.5 | 25200 | 21800 | 86.51% | 1.82 | 18700 | R-410A
216623451 | 3.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBM-60D28T6N10-MAS |  | 47000 | 15.2 | 10 | 8.1 | 58000 | 43000 | 74.14% | 1.83 | 36000 | R-454B
215931690 | 4.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0702120B* | 56500 | 18.5 | 11 | 8.5 | 60500 | 47000 | 77.69% | 2.02 | 48000 | R-454B
215931820 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0702120B* | 56000 | 17.5 | 11 | 8.1 | 61000 | 46500 | 76.23% | 1.95 | 47500 | R-454B
216681042 | 2.92 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4224AL* | 927TA60080V21*** | 35000 | 16 | 9.8 | 8.5 | 38500 | 34600 | 89.87% | 1.75 | 29200 | R-410A
214264214 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J936 | A97US2V070B12S | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216054756 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | LP9C080B12MP13 | 21600 | 17 | 12 | 8.5 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216054763 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | LPLC080B12MP13 | 21200 | 17 | 11.7 | 9 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216054804 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8V080B12MP12 | 21600 | 17 | 11.7 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216054847 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E080B12MP12 | 21000 | 17 | 11.2 | 9 | 22600 | 18700 | 82.74% | 2 | 18700 | R-454B
213281550 | 2.93 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E080C20LMPS1 | 35200 | 17 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213281551 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E080C20SMPS1 | 32400 | 16.6 | 8 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
212975061 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *96VTN0401410B* | 23400 | 16 | 10 | 8.1 | 26400 | 24600 | 93.18% | 2.04 | 19200 | R-410A
213204907 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0261410A* | 23000 | 16.5 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
212980992 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *80MS(N,L)1102120A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 23800 | 90.84% | 2 | 19000 | R-410A
212981746 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *80MSU1002120A* | 23600 | 17 | 10 | 8.5 | 26200 | 24000 | 91.6% | 2 | 19100 | R-410A
216055570 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TP9C060B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055586 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z8ES040A12SMPS1 | 21000 | 18 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
214264142 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
216620291 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBL-18HWFN10-MH3 |  | 18000 | 16.8 | 12 | 10.5 | 19000 | 19000 | 100% | 1.8 | 15000 | R-454B
213205518 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80ES(N,L)0702116A* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31400 | 83.07% | 2.75 | 28800 | R-410A
213205567 | 2.87 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80ES(N,L)1352420A* | 34400 | 16 | 9.9 | 8.5 | 38500 | 31400 | 81.56% | 2.74 | 29000 | R-410A
213367795 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y81E080C20SMPS1 | 32400 | 16.6 | 8 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213367796 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y81E100B12LMPS1 | 32600 | 17.5 | 8 | 8.1 | 36000 | 25600 | 71.11% | 2.6 | 25000 | R-410A
216764948 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8X2B080M4PTC | 32600 | 17.1 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.9 | 21600 | R-454B
216764981 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S8X2C080M5PSC | 33800 | 17.1 | 12 | 8.7 | 33400 | 24400 | 73.05% | 2.1 | 21600 | R-454B
216764982 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S8X2C100M5PSC | 33200 | 17.1 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2 | 21400 | R-454B
216764998 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S8X1B080M4PTC | 31800 | 17.1 | 11.7 | 8.5 | 32000 | 23800 | 74.38% | 2 | 21000 | R-454B
216765032 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*C009AS3 | S8X2C080M5PSC | 43500 | 16.5 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29200 | R-454B
214810349 | 2.92 | No | No | ARCOAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG33936 | *80MS(N,L)0701712A* | 35000 | 16 | 9.5 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
216681075 | 2.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4824AL* | 927TA60080V21*** | 35400 | 16.5 | 10 | 8.5 | 37400 | 34200 | 91.44% | 1.94 | 28800 | R-410A
213088113 | 1.92 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | V,A,D36H175D149+AEFE4B* |  | 23000 | 21 | 13 | 8.55 | 20600 | 15700 | 76.21% | 2.24 | 13200 | R-410A
216054856 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9V040A10MP12 | 20800 | 16.5 | 10.5 | 8.5 | 22800 | 17500 | 76.75% | 2 | 17700 | R-454B
216620295 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBL-30HWFN10-WJ3 |  | 30000 | 16.3 | 11 | 9.5 | 31000 | 31000 | 100% | 1.86 | 24000 | R-454B
213088203 | 3 | Yes | No | ARCOAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG35936+AEFE3A* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
213927549 | 1.93 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | V,A,D36H***D449+AEFE3A* |  | 23200 | 20 | 13.5 | 8.7 | 20600 | 15700 | 76.21% | 2.26 | 13300 | R-410A
215933190 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN0801714B* | 33000 | 18.5 | 10.5 | 9 | 35600 | 27200 | 76.4% | 1.92 | 31200 | R-454B
215933240 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0601714B* | 33000 | 18.5 | 10.5 | 9 | 34400 | 26200 | 76.16% | 1.92 | 30200 | R-454B
214264213 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A97US2V070B12S | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215675545 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CTL0702120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676565 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *96CTN0801714B* | 47500 | 18.5 | 10 | 9 | 50000 | 36200 | 72.4% | 2.02 | 45500 | R-454B
215677265 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X61M24A*+WALLCON | *97CMN0602120B* | 56500 | 18 | 8.5 | 9 | 65000 | 45500 | 70% | 2.06 | 57000 | R-454B
213367802 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y81E120C16LMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
212977699 | 1.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *80MS(N,L)0451412A* | 23600 | 17 | 10.5 | 8.5 | 26400 | 24200 | 91.67% | 2 | 19100 | R-410A
215934730 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X36M17A*+WALLCON | *96CTN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
213828542 | 2.43 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)43A44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213204429 | 1.98 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0701716A* | 23800 | 16.3 | 10.2 | 8.4 | 26000 | 24600 | 94.62% | 2.52 | 24200 | R-410A
216054791 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216054793 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E080B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054794 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054825 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E026A08MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216054842 | 1.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E060B12MP12 | 22000 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
216054859 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V060B12MP12 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
214264157 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J936 | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214861566 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M2X | MVBC-36HWFN10-MC2 |  | 36000 | 17.3 | 11.7 | 9.5 | 38000 | 38000 | 100% | 2.06 | 28000 | R-454B
216030935 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBC-36HWFN10-MC3E-MAS |  | 36000 | 17.3 | 11.7 | 10.3 | 37000 | 39000 | 105.4% | 1.9 | 31800 | R-454B
213205026 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN0601714A* | 23600 | 16.5 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.91 | 19100 | R-410A
213205075 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *96VTN1002122A* | 23400 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
212437659 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
215679725 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU0601716B* | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
213828543 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)37B44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215939873 | 2.85 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0801716A* | 34200 | 20 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30400 | R-454B
215940173 | 2.82 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1202422A* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.92 | 30400 | R-454B
215940393 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215940473 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M24A*+WALLCON | *96CTN0802120B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215940593 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X38M17A*+WALLCON | *80CSU0601716B* | 35600 | 22 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 33000 | R-454B
215931710 | 4.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1102120B* | 57000 | 19 | 11.5 | 8.5 | 60500 | 46500 | 76.86% | 2.02 | 47500 | R-454B
215931860 | 4.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU1002122B* | 56500 | 18 | 11.5 | 8.1 | 61000 | 45500 | 74.59% | 2 | 47000 | R-454B
215940803 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN1202422A* | 35600 | 22 | 12.5 | 8.5 | 38500 | 28400 | 73.77% | 2.04 | 32800 | R-454B
215940923 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN0801716A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.04 | 32800 | R-454B
215939703 | 2.72 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CTN0802120A* | 32600 | 19.5 | 11.7 | 9.5 | 34800 | 26800 | 77.01% | 2.02 | 30600 | R-454B
215939853 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716B* | 34400 | 20.5 | 12 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
215939953 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU0401712B* | 33400 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215940053 | 2.77 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN0601716A* | 33200 | 18.5 | 10.5 | 9 | 35600 | 27200 | 76.4% | 1.92 | 31200 | R-454B
215940253 | 2.85 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1202422A* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
213367803 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y81E120C16SMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
213367738 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C24+TDR | Y81E100C20LMPS1 | 31400 | 15.9 | 8.5 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213367836 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36A44+TDR | Y81E080C20LMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
215677335 | 4.58 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0701716B* | 55000 | 18 | 9.5 | 9 | 59500 | 43500 | 73.11% | 2.1 | 54000 | R-454B
213205023 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0601412A* | 23600 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
212975711 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L14** | *96VTN0601412B* | 23200 | 16.5 | 10 | 8.5 | 26800 | 25400 | 94.78% | 2.12 | 19500 | R-410A
213828531 | 3.42 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)61C44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213205084 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN1002122A* | 23600 | 17 | 10.5 | 8.1 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213204396 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0451712A* | 23800 | 17 | 10 | 8.5 | 26200 | 24600 | 93.89% | 2.52 | 24200 | R-410A
213205649 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *95ESN1002120A* | 35400 | 16 | 10 | 8.1 | 39500 | 31200 | 78.99% | 2.69 | 29200 | R-410A
213205651 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *95ESN1002120A* | 35400 | 16 | 10 | 8.1 | 39500 | 31200 | 78.99% | 2.69 | 29200 | R-410A
213204800 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0902120A* | 23400 | 16.8 | 10.2 | 8.4 | 25800 | 20000 | 77.52% | 2.96 | 18900 | R-410A
213204830 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92ESN0401410A* | 23600 | 15.5 | 9.9 | 8.5 | 26000 | 20400 | 78.46% | 2.94 | 19100 | R-410A
213204832 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92ESN0401410A* | 23200 | 15.4 | 9.8 | 8.5 | 26000 | 20400 | 78.46% | 2.94 | 19100 | R-410A
213204848 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN0601412A* | 23200 | 17 | 10 | 8.5 | 25600 | 20000 | 78.12% | 2.87 | 18800 | R-410A
216054876 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9Y060B12MP11 | 21600 | 17 | 11 | 8.1 | 22600 | 18400 | 81.42% | 2 | 18500 | R-454B
216054877 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y060B12MP11 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
216054892 | 1.73 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE040A12MP11 | 20800 | 16.5 | 11.7 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216054910 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE100B12MP11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054943 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES080B12SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18500 | R-454B
216054960 | 1.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ET080B12LMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
216054977 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES040A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18300 | R-454B
216055631 | 1.68 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES060A10SMPS1 | 20200 | 17.5 | 11.2 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18000 | R-454B
216765047 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | S8X2D120M5PSC | 44000 | 17.1 | 12 | 9 | 44500 | 32400 | 72.81% | 2.2 | 29400 | R-454B
216764895 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S8X1C080M5PTC | 52500 | 16.5 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 34000 | R-454B
216765049 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | S8X2C100M5PTC | 43500 | 17.1 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29400 | R-454B
211628069 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212977013 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X36L21A* | *96VTN1002122B* | 29800 | 15.2 | 9 | 8.1 | 34200 | 28000 | 81.87% | 1.78 | 23600 | R-410A
213350117 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y81E040A12SMPS1 | 33200 | 18 | 10 | 8.2 | 32800 | 29800 | 90.85% | 2.72 | 26400 | R-410A
213350119 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.68 | 26200 | R-410A
215932110 | 2.58 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *96CTN0401410B* | 31000 | 17.5 | 10.5 | 9 | 34200 | 26400 | 77.19% | 1.92 | 30400 | R-454B
215940503 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN1202422A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215940573 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *97CTN1002122A* | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
215940673 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *97CTN0802120A* | 34400 | 20.5 | 11.7 | 8.5 | 38500 | 28200 | 73.25% | 2.04 | 32200 | R-454B
213770172 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG80936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215399937 | 1.8 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR |  | 21600 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.63 | 18600 | R-454B
213205021 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0601412A* | 23400 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213204135 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92ESN0401712A* | 23400 | 15.2 | 9 | 8.1 | 25200 | 27400 | 108.7% | 2.61 | 25400 | R-410A
213204798 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0901714A* | 23800 | 17 | 10.3 | 8.5 | 25800 | 20000 | 77.52% | 2.98 | 18900 | R-410A
213204817 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80ES(N,L)1102120A* | 23800 | 16.5 | 10.4 | 8.5 | 26200 | 20200 | 77.1% | 2.99 | 19100 | R-410A
215932590 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU1002122B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.04 | 29600 | R-454B
215932690 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0451712B* | 34000 | 19.5 | 11 | 9 | 35200 | 26800 | 76.14% | 1.92 | 30800 | R-454B
213204914 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0261410A* | 23200 | 16.5 | 10 | 8.5 | 25600 | 20200 | 78.91% | 2.86 | 18900 | R-410A
213205031 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN0601714A* | 23800 | 16.5 | 10 | 8.5 | 26000 | 20400 | 78.46% | 2.91 | 19100 | R-410A
216699825 | 2.78 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CHPEA4830*3A*+MBVK16CP1X00A* |  | 33400 | 18.2 | 11 | 9 | 31000 | 31000 | 100% | 2 | 30800 | R-32
216025756 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBE-24HWFN10-WM3E |  | 24000 | 17.5 | 10.8 | 10.5 | 25000 | 19600 | 78.4% | 1.96 | 21800 | R-454B
215932650 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1202422B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 26000 | 76.47% | 2.06 | 29800 | R-454B
213204103 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80ES(N,L)0902120A* | 23800 | 16 | 9.5 | 8.5 | 25800 | 29000 | 112.4% | 2.59 | 26200 | R-410A
213204257 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *95ESN0601714A* | 23600 | 15.3 | 9.3 | 8.4 | 25400 | 26800 | 105.5% | 2.74 | 25600 | R-410A
213204321 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0601412A* | 23200 | 16 | 9.4 | 8.1 | 24400 | 26000 | 106.6% | 2.72 | 25200 | R-410A
216766458 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S8V2C080M5PDB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
216766508 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S8V2C100M5PCB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.22 | 29200 | R-454B
216766510 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S8V2D120M5PCB | 44000 | 17 | 12.5 | 9 | 44000 | 32000 | 72.73% | 2.24 | 29200 | R-454B
214802744 | 1.85 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)36D24+TDR | R801V1004A17UHS | 22200 | 16.3 | 11.8 | 8.5 | 23200 | 16400 | 70.69% | 3.15 | 17100 | R-410A
216766826 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD04AS3 | S9X2B060D3PSB | 23400 | 17.1 | 12.5 | 8.1 | 22200 | 17200 | 77.48% | 1.84 | 15400 | R-454B
216766828 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD04AS3 | S8V2B060M4PDB | 23400 | 17 | 12 | 8.1 | 22400 | 17300 | 77.23% | 1.83 | 15400 | R-454B
216766843 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S9X1B040D3PSB | 23600 | 17.1 | 12.7 | 8.5 | 22200 | 17300 | 77.93% | 1.94 | 15400 | R-454B
216766862 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3+P0V0A000M30SD |  | 23200 | 17 | 12 | 8.7 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
216766876 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S8V2A040M3PCB | 23800 | 17.1 | 12.7 | 9 | 22000 | 17500 | 79.55% | 2.06 | 15500 | R-454B
213204865 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92ESN0601714A* | 23800 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
216699798 | 1.98 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | DFVE48CP0300A* |  | 23800 | 19.2 | 11.7 | 9.2 | 23200 | 22400 | 96.55% | 2.1 | 23000 | R-32
216055707 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 31000 | 18 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
215065729 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH48A34+TDR | TM8V080C16MP12 | 32000 | 17.5 | 9.9 | 8.2 | 33600 | 23800 | 70.83% | 2.08 | 25200 | R-410A
215932680 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU1002120A* | 34400 | 20 | 11.7 | 9 | 34600 | 26200 | 75.72% | 1.94 | 30200 | R-454B
215931960 | 2.62 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X24M17A*+WALLCON | *96CTN0601714B* | 31400 | 18.5 | 10 | 9.5 | 35000 | 26800 | 76.57% | 2 | 30800 | R-454B
213204089 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80ES(N,L)0901714A* | 23800 | 16 | 9 | 8.1 | 25600 | 28000 | 109.4% | 2.62 | 25800 | R-410A
213204187 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *92ESN0802120A* | 23800 | 16 | 9 | 8.5 | 26000 | 28200 | 108.5% | 2.62 | 25800 | R-410A
213204274 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *95ESN0802120A* | 23800 | 15.5 | 9 | 8.5 | 26000 | 27000 | 103.8% | 2.7 | 25800 | R-410A
213204338 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0801716A* | 23800 | 16 | 9 | 8.1 | 25400 | 25600 | 100.8% | 2.54 | 24800 | R-410A
215676865 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *80CTL0702120B* | 48500 | 19 | 10.5 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676245 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *95CSU1002122B* | 47000 | 18.5 | 10 | 9 | 50000 | 36200 | 72.4% | 2.02 | 45500 | R-454B
213752474 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC6A080M17**16 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.88 | 20200 | R-410A
213203960 | 1.44 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *92ESN0601412A* | 17300 | 16.3 | 10.7 | 8.5 | 18500 | 13900 | 75.14% | 2.26 | 14300 | R-410A
215933440 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN1002122B* | 33600 | 19 | 11.5 | 9 | 34600 | 26600 | 76.88% | 1.94 | 30400 | R-454B
215931970 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X25M17A*+WALLCON | *97CMN0601714B* | 33400 | 19 | 10.5 | 9.5 | 34400 | 26200 | 76.16% | 2.04 | 30200 | R-454B
215932070 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701716B* | 32200 | 19 | 10.5 | 9.5 | 35400 | 27200 | 76.84% | 2 | 31200 | R-454B
215932120 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *96CTN0601714B* | 32000 | 19 | 10.5 | 9.5 | 34600 | 26600 | 76.88% | 2.02 | 30400 | R-454B
213350158 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y81E100C20LMPS1 | 32000 | 17.5 | 9.4 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213350167 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E120C16LMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
213350178 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y81E120C20SMPS1 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216766926 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S9X2B080D4PSB | 32400 | 16 | 11.5 | 8.1 | 33400 | 24600 | 73.65% | 1.96 | 21600 | R-454B
216766928 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S9X2B040D3PSB | 32600 | 16 | 11.2 | 8.1 | 33800 | 24800 | 73.37% | 1.97 | 22000 | R-454B
216766943 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S8V2A040M3PDB | 32600 | 16 | 11.7 | 8.5 | 33200 | 24400 | 73.49% | 2.04 | 21400 | R-454B
216766945 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9V2B040D3VSB | 32600 | 16 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.05 | 21400 | R-454B
213752508 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SP6A060V14**12 | 22600 | 15.8 | 9.3 | 8.1 | 24400 | 22000 | 90.16% | 2.87 | 19600 | R-410A
216764779 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*CD09AS3 | S8X1C100M5PTC | 43500 | 17.1 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.1 | 29400 | R-454B
213841887 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG8J936 | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
214336760 | 4.58 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-60U3SP2 | L(E,G)M60B4 |  | 55000 | 16.5 | 8 | 8.5 | 55500 | 41000 | 73.87% | 1.9 | 39000 | R-410A
214861574 | 2.75 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-33HFN10-M1X | MVBC-36HWFN10-MC1-D |  | 33000 | 16.5 | 11.7 | 10 | 35000 | 34000 | 97.14% | 2 | 27400 | R-454B
214574653 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D)4X48L24**+WALLCON | *95CSU1002122B* | 32400 | 17.5 | 11.5 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31400 | R-410A
214093368 | 2.88 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B36+TDR | Z8ES080C20LMPS1 | 34600 | 17 | 9 | 8.1 | 32400 | 44000 | 135.8% | 3.24 | 25400 | R-410A
213828541 | 2.4 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)37A44+TDR |  | 28800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213076347 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *95MSU1002122A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 23800 | 90.84% | 1.98 | 19000 | R-410A
213075928 | 3.03 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *95MSU1002120A* | 36400 | 16 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.06 | 29000 | R-410A
216699833 | 2.78 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CHPEA4830*3A* | D*80TC0805C*A* | 33400 | 18.2 | 11 | 9 | 31000 | 31000 | 100% | 2 | 30800 | R-32
216699835 | 2.78 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CHPEA4830*3A* | D*80TC0804C*A* | 33400 | 18.2 | 11 | 9 | 31000 | 31000 | 100% | 2 | 30800 | R-32
216025754 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBE-36HWFN10-WL3E |  | 36000 | 16.8 | 11.2 | 9.6 | 37000 | 34600 | 93.51% | 1.8 | 30200 | R-454B
213204340 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0801716A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 26800 | 105.5% | 2.7 | 25600 | R-410A
216055535 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9Y080B12MP11 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18400 | R-454B
212973357 | 1.44 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X18L14** | *96VSN0601412B* | 17300 | 16 | 10.5 | 8.5 | 18500 | 19800 | 107% | 2.38 | 12400 | R-410A
213203970 | 1.5 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *92ESN0801716A* | 18000 | 16 | 11 | 8.5 | 19500 | 13700 | 70.26% | 2.29 | 14200 | R-410A
212974527 | 2.52 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *96VSN1202422B* | 30200 | 15.2 | 9 | 8.1 | 34400 | 27400 | 79.65% | 1.8 | 23600 | R-410A
212361579 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M080B3A | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 33400 | R-410A
212361580 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M080B3B | 41000 | 16 | 11 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 33400 | R-410A
215677035 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *95CSU1002122B* | 57000 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 55500 | R-454B
216763338 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | L8V1A060U3VSB | 23200 | 17.1 | 12.5 | 9 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
216763340 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | L8V1B080U4VSB | 23200 | 17.1 | 12.5 | 9 | 21800 | 17300 | 79.36% | 2 | 15500 | R-454B
216763354 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S9V2B040U3PSC | 23200 | 17.1 | 12.5 | 9 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
216763470 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TEM6D05AV41+TDR |  | 23800 | 17.1 | 12.5 | 9.5 | 21800 | 17400 | 79.82% | 2.1 | 15400 | R-454B
216763688 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | L8V1C100U5VSB | 33800 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216763690 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | L9X1C100U5VSA | 32800 | 17.1 | 12 | 8.7 | 32400 | 24200 | 74.69% | 2.1 | 21200 | R-454B
216763704 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S9V2C100D4VSB | 31400 | 16 | 11.2 | 9 | 31600 | 23600 | 74.68% | 2.1 | 21000 | R-454B
216763722 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD05AS3 | S9V2C100D4VSB | 32600 | 17.1 | 12 | 8.2 | 33400 | 24400 | 73.05% | 1.9 | 21600 | R-454B
216763738 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD09AS3 | S9V2C100D4VSB | 33600 | 17.1 | 12.5 | 8.7 | 32000 | 23600 | 73.75% | 2.1 | 21000 | R-454B
216763754 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*D010AS3 | S9V2D120U5PSC | 34400 | 17.1 | 12.5 | 9 | 32200 | 24000 | 74.53% | 2.2 | 21200 | R-454B
214264215 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215940953 | 3.63 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0401712B* | 43500 | 21 | 11 | 9.5 | 48000 | 36400 | 75.83% | 1.92 | 39500 | R-454B
213204883 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92ESN0802120A* | 23600 | 16.8 | 10.2 | 8.4 | 26000 | 20200 | 77.69% | 3.02 | 19000 | R-410A
213204949 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *95ESN0601412A* | 23400 | 15.9 | 9.8 | 8.5 | 26000 | 20400 | 78.46% | 2.97 | 19100 | R-410A
213205048 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *96VTN0801716A* | 23400 | 17 | 10.3 | 8.5 | 25600 | 19900 | 77.73% | 2.98 | 18700 | R-410A
216766560 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9X2C100U5PSB | 43500 | 15.2 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29200 | R-454B
216766608 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S8V2C080M5PDB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.21 | 29200 | R-454B
215676955 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *96CTN1202422B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
215676355 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CMN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
213205433 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *96VTN0802120A* | 29600 | 15.2 | 9 | 8.1 | 33600 | 23800 | 70.83% | 2.67 | 23200 | R-410A
213752658 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M17**12 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.86 | 19000 | R-410A
213752673 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B070M21**16 | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213752743 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*B070V17**16 | 22400 | 17.3 | 9.7 | 8.4 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213752791 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2E040M17**12 | 23400 | 16 | 9 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19300 | R-410A
214602070 | 1 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX330U-12HFN1-MR0 | MVC-12HWFN1-M |  | 12000 | 17.5 | 11.7 | 9 | 13000 | 11000 | 84.62% | 2.6 | 12000 | R-410A
215935305 | 2.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAMA6021XMA*+UI | 986TD42080C17*** | 35400 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 33000 | R-454B
213828549 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)31C44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215359327 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBC-60HWFN10-MD3E-D |  | 48000 | 16.5 | 10.5 | 9.5 | 50000 | 46000 | 92% | 1.9 | 37000 | R-454B
212976449 | 2.53 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X37L21A* | *96VTN0802120B* | 30400 | 15.2 | 9 | 8.5 | 33400 | 26400 | 79.04% | 1.86 | 23200 | R-410A
213770171 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG34936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214264159 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J936 | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216763808 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S8X1B080M4PSC | 32600 | 17.1 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
216763822 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S8X1A040M3PSC | 32400 | 17.1 | 11.5 | 8.7 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216763856 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9V2B060U4PSC | 33200 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.1 | 21200 | R-454B
216766064 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3+P0V0B000M40SD |  | 33800 | 17.1 | 12 | 9 | 32600 | 24000 | 73.62% | 2.2 | 21200 | R-454B
216766096 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3+P0V0B000M40SD |  | 33600 | 16.5 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2.13 | 21600 | R-454B
216766114 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S8V2B080M4PCB | 33000 | 16.5 | 12 | 8.5 | 33200 | 24400 | 73.49% | 2.09 | 21400 | R-454B
216766148 | 2.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S9X1C100U5PSB | 33600 | 15.2 | 12 | 9 | 32600 | 24200 | 74.23% | 2.19 | 21400 | R-454B
216766164 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3+P0V0C000M50SD |  | 34000 | 17.1 | 12.5 | 9 | 32600 | 24000 | 73.62% | 2.22 | 21200 | R-454B
213205513 | 2.8 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0702116A* | 33600 | 16.4 | 9.8 | 8.5 | 37800 | 31400 | 83.07% | 2.75 | 28800 | R-410A
214053842 | 1.83 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430U-22HFN1-MR0 | MVBM-24A18T3N1 |  | 22000 | 15.4 | 10 | 9.2 | 22000 | 16000 | 72.73% | 2 | 22600 | R-410A
215676505 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *95CSU0802120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676605 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CTL0702120B* | 47500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215939943 | 2.77 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0802120B* | 33200 | 19 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30800 | R-454B
215939993 | 2.77 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CTN0802120A* | 33200 | 19 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30800 | R-454B
216766878 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S8V2B080M4PCB | 23800 | 17.5 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2.06 | 15500 | R-454B
215940963 | 3.63 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716B* | 43500 | 21 | 11 | 9.5 | 48000 | 36600 | 76.25% | 1.9 | 39500 | R-454B
213205653 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *95ESN1002122A* | 35400 | 15.5 | 10.5 | 8.5 | 39500 | 31600 | 80% | 2.71 | 29400 | R-410A
213355363 | 2.9 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48C6 |  | 34800 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
216055680 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C16MP11 | 30800 | 18 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
213367777 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | YP9C080B12MP13 | 31800 | 17 | 9 | 8.1 | 33600 | 29400 | 87.5% | 2.72 | 26600 | R-410A
212590800 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DD12936 | A96US2V070B12 | 23800 | 20 | 13.5 | 8.45 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212437548 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A80UH1E045A12 | 23400 | 21 | 13.5 | 8.5 | 21200 | 14900 | 70.28% | 1.86 | 13200 | R-410A
211628395 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
216682588 | 2.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *97VTN1002122A* | 35800 | 16.5 | 10 | 9 | 37400 | 34200 | 91.44% | 1.94 | 28800 | R-410A
213821581 | 2.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0902116A* | 34800 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.52 | 29400 | R-410A
213367785 | 2.55 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | YPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.5 | 33800 | 27400 | 81.07% | 2.67 | 25400 | R-410A
213821612 | 2.87 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80VTL1102122B* | 34400 | 16.5 | 9.9 | 8.5 | 38000 | 31600 | 83.16% | 2.73 | 29000 | R-410A
213821632 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *92MSN1202420A* | 35400 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
213821647 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96MSN1002122A* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.71 | 29000 | R-410A
214239409 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D,W)4X60L24**+WALLCON | *96CTN1002122B* | 32800 | 17.5 | 12 | 8.1 | 32200 | 24600 | 76.4% | 1.96 | 31200 | R-410A
213367735 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C24+TDR | Y81E100B12SMPS1 | 31800 | 17.5 | 8.4 | 8.1 | 35800 | 25400 | 70.95% | 2.61 | 24800 | R-410A
211628104 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.78 | 25600 | R-410A
216766196 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD05AS3 | S8V2C100M5PCB | 32800 | 16 | 12 | 8.2 | 33400 | 24600 | 73.65% | 2 | 21600 | R-454B
216766228 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD09AS3 | S9V2C100D5VSB | 33600 | 17.1 | 12.5 | 8.7 | 32000 | 23600 | 73.75% | 2.15 | 21000 | R-454B
216766312 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9V2B060U4VSB | 33200 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.17 | 21200 | R-454B
216763708 | 2.8 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 |  | 33600 | 16 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
216763881 | 2.7 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 |  | 32400 | 15.2 | 11 | 8.7 | 33200 | 24800 | 74.7% | 2.1 | 22000 | R-454B
216766364 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 | S9X2C080U5PSB | 32600 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.13 | 21200 | R-454B
216766396 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC009AS3 | S8V2C100M5PDB | 34200 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.22 | 21200 | R-454B
216766428 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCD010AS3 | S9X2D120U5PSB | 34400 | 16 | 12.5 | 9 | 32200 | 23800 | 73.91% | 2.23 | 21200 | R-454B
213367820 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
216699834 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*80TC0805C*A* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
213203972 | 1.5 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *92ESN0801716A* | 18000 | 16 | 11 | 8.5 | 19500 | 14100 | 72.31% | 2.22 | 14500 | R-410A
212975128 | 1.44 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *96VTN0401712B* | 17300 | 16 | 10.5 | 8.1 | 17900 | 18600 | 103.9% | 2.22 | 12200 | R-410A
212975778 | 1.48 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96VTN0801716B* | 17700 | 16.5 | 10.5 | 8.1 | 17700 | 17900 | 101.1% | 2.16 | 12100 | R-410A
216766432 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCD010AS3 | S9X1D120U5PSB | 34400 | 16 | 12.5 | 9 | 32200 | 23800 | 73.91% | 2.23 | 21200 | R-454B
212348365 | 4.58 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-60U3SP2 | LEM60G4 |  | 55000 | 16.5 | 8 | 8.2 | 55000 | 40500 | 73.64% | 2.46 | 39000 | R-410A
216620323 | 3 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBL-36HWFN10-WK3 |  | 36000 | 15.4 | 9.2 | 8.7 | 37000 | 28400 | 76.76% | 1.86 | 24600 | R-454B
213205695 | 2.87 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96VTN1202422A* | 34400 | 16 | 9.9 | 8.5 | 38500 | 31400 | 81.56% | 2.74 | 29000 | R-410A
216763963 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S9V2C100U4VSB | 43000 | 17.1 | 12 | 9 | 44000 | 32000 | 72.73% | 2.2 | 29200 | R-454B
213367821 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
216763981 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8X1D120M5PSC | 43500 | 17.1 | 11.7 | 9 | 44500 | 32600 | 73.26% | 2.2 | 29800 | R-454B
215676185 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *80CSU1002120A* | 47000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2.02 | 46000 | R-454B
215675915 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *95CSU1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.02 | 46000 | R-454B
213205515 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0702116A* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31400 | 83.07% | 2.75 | 28800 | R-410A
213205656 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *95ESN1002122A* | 35400 | 15.5 | 10 | 8.5 | 39500 | 31600 | 80% | 2.71 | 29400 | R-410A
216620303 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBM-24B18T3N10 |  | 24000 | 16 | 10 | 9.5 | 25000 | 21000 | 84% | 1.8 | 19700 | R-454B
216763504 | 1.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3 | L9X1A050U3VSA | 22800 | 17.1 | 11.7 | 8.7 | 22000 | 17600 | 80% | 1.9 | 15700 | R-454B
216765928 | 1.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3 | S9X1B060D3PSB | 21800 | 15.2 | 11.7 | 8.5 | 21200 | 16900 | 79.72% | 1.96 | 15100 | R-454B
216765946 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3 | S8V2B060M4PCB | 23200 | 17.1 | 12.5 | 8.7 | 21800 | 17300 | 79.36% | 2.02 | 15400 | R-454B
216766514 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S9V2C100U5VSB | 43000 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.21 | 29200 | R-454B
216766562 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9X2C080U5PSB | 43000 | 16.5 | 12 | 8.7 | 43500 | 32000 | 73.56% | 2.21 | 29200 | R-454B
216766580 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S9V2C080U5VSB | 43000 | 16.5 | 12 | 9 | 44500 | 32600 | 73.26% | 2.22 | 29600 | R-454B
213205688 | 2.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96VTN1002120A* | 35400 | 15.5 | 9.5 | 8.1 | 39500 | 32000 | 81.01% | 2.5 | 29600 | R-410A
213796206 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG8J936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216766614 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S8V2D120M5PCB | 44000 | 17 | 12.5 | 9 | 44000 | 32200 | 73.18% | 2.24 | 29200 | R-454B
216699839 | 2.78 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CHPEA4830*3A* | D*97MC1005CNA* | 33400 | 18.2 | 11 | 9 | 31000 | 31000 | 100% | 2 | 30800 | R-32
216699841 | 2.78 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CHPEA4830*3A* | D*97MC0804CNA* | 33400 | 18.2 | 11 | 9 | 31000 | 31000 | 100% | 2 | 30800 | R-32
214574497 | 2.62 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH837GKA2* | EN(A,D)4X36L21**+WALLCON | *97CMN0802120B* | 31400 | 17 | 11 | 8.1 | 33200 | 24200 | 72.89% | 1.82 | 31200 | R-410A
211627771 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8V100C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
211627857 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.2 | 26800 | 33800 | 126.1% | 2.92 | 27000 | R-410A
211627948 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 25000 | 31200 | 124.8% | 2.83 | 25000 | R-410A
215675835 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676435 | 3.96 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0451712B* | 47500 | 18 | 9.5 | 9 | 50000 | 37600 | 75.2% | 1.98 | 47500 | R-454B
213367843 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36A44+TDR | Y81E100C20SMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
211628134 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TMLE040A12MP11 | 32800 | 18 | 10 | 8.1 | 33600 | 27200 | 80.95% | 2.5 | 25200 | R-410A
211628225 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TMLV060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211628316 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
211628364 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 25400 | 31600 | 124.4% | 2.87 | 25400 | R-410A
211628368 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
215682285 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN1202422A* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
215676385 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *96CTN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
213927550 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | PL36H***P229+AEFE3A* |  | 23400 | 20 | 13.5 | 8.85 | 20800 | 15700 | 75.48% | 2.3 | 13300 | R-410A
215385621 | 1.77 | Yes | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-24U3SF2 | L(E,F)W30C4 |  | 21200 | 15.8 | 10 | 8.1 | 23000 | 17700 | 76.96% | 1.98 | 17000 | R-410A
215675885 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *80CTL1102120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
215675985 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL0902120B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
213828546 | 2.48 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)43D34+TDR |  | 29800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
216623447 | 2.42 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBM-36B24T4N10-MAS |  | 29000 | 16 | 10 | 9.5 | 32000 | 32000 | 100% | 1.85 | 25000 | R-454B
215676735 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0901716B* | 48500 | 19 | 10 | 9 | 50000 | 37000 | 74% | 2 | 47000 | R-454B
215676885 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *80CTL1352422B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
214264158 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A80UH2E090B12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213367734 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C24+TDR | Y81E100B12LMPS1 | 31800 | 17.5 | 8.4 | 8.1 | 35800 | 25400 | 70.95% | 2.61 | 24800 | R-410A
216055700 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y100C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216699823 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | DFVE48CP1300A* |  | 34200 | 19 | 11.7 | 9.2 | 33400 | 33000 | 98.8% | 2.1 | 32000 | R-32
216699830 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*96TC0804CNA* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
216055681 | 2.53 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055706 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y120C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055708 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y120C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216055731 | 2.57 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080B12MP12 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055781 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLV100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055783 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLV100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055808 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES080B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
214336689 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R921V1155A24M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
212498333 | 2.45 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CE2903A+TXV |  | 29400 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
216699822 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | DFVE48DP0300A* |  | 34200 | 19 | 11.7 | 9.2 | 33400 | 33000 | 98.8% | 2.1 | 32000 | R-32
211628494 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | YPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.84 | 25600 | R-410A
216055243 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
216055654 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL8E100C20UH11 | 31000 | 17 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
213355435 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E6 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
213614463 | 1.98 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YZT48B21 | D(A,C,E)60B44+TDR | TM9Y080C16MP11 | 23800 | 16 | 12.4 | 8.4 | 47500 | 34200 | 72% | 3.03 | 33200 | R-410A
213752793 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2E060M14**12 | 23800 | 17 | 10 | 8.5 | 26600 | 20200 | 75.94% | 2.86 | 19200 | R-410A
213752959 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SP6A080V21**20 | 23800 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.92 | 19000 | R-410A
213752961 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SP6A080V21**20 | 23800 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.92 | 19000 | R-410A
213752977 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SP6A100V21**20 | 23800 | 17 | 10 | 8.5 | 26000 | 20000 | 76.92% | 2.89 | 18900 | R-410A
216699837 | 2.78 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CHPEA4830*3A* | D*80SC0805CUA* | 33400 | 18.2 | 11 | 9 | 31000 | 31000 | 100% | 2 | 30800 | R-32
216766674 | 4.38 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S9V2C080U5VSB | 52500 | 15.2 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.22 | 33800 | R-454B
215679585 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1202422A* | 34400 | 18.5 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215679935 | 2.88 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0802120B* | 34600 | 16.5 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
215679985 | 2.88 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0802120A* | 34600 | 16.5 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
215676495 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *95CSU0601716B* | 47500 | 18 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
213367819 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29200 | 86.9% | 2.64 | 26400 | R-410A
215588495 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 59TN6C080C21**20 | 52500 | 19.5 | 12 | 8.5 | 53500 | 46500 | 86.92% | 1.95 | 48000 | R-454B
208101911 | 2.5 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30U-30HFN1-MR0(X) | MAC-36HWDN1-MN0 |  | 30000 | 15.5 | 10.5 | 9.7 | 33000 | 27000 | 81.82% | 1.85 | 22600 | R-410A
213821172 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN1002122B* | 23800 | 16.5 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
213204096 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80ES(N,L)0901714A* | 23800 | 16 | 9.5 | 8.1 | 25600 | 28200 | 110.2% | 2.62 | 25800 | R-410A
213204248 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *95ESN0601412A* | 23800 | 15.2 | 9.4 | 8.1 | 25400 | 27400 | 107.9% | 2.68 | 25400 | R-410A
213204316 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0601412A* | 23200 | 16 | 9.4 | 8.1 | 24400 | 26800 | 109.8% | 2.7 | 25600 | R-410A
213204330 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0601714A* | 23800 | 15.5 | 9.5 | 8.1 | 25200 | 27000 | 107.1% | 2.69 | 25800 | R-410A
216055245 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055259 | 3.42 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055275 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055277 | 3.33 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055292 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
214861615 | 4.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBDM-60HWFN10-WC3-D |  | 54000 | 17.5 | 12 | 9.5 | 55000 | 54000 | 98.18% | 1.9 | 35000 | R-454B
211627584 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.8 | 25600 | R-410A
211627636 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 25400 | 31600 | 124.4% | 2.84 | 25400 | R-410A
211627701 | 2.68 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8E120C16MP11 | 32200 | 18 | 9.9 | 8.5 | 25200 | 31400 | 124.6% | 2.88 | 25200 | R-410A
215676595 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CSU1002120A* | 48000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
216766052 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S8V2A040M3PCB | 32800 | 16 | 12 | 8.7 | 32400 | 24200 | 74.69% | 2.14 | 21200 | R-454B
216766120 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S8V2A040M3PCB | 32600 | 16 | 12 | 8.5 | 33200 | 24400 | 73.49% | 2.05 | 21400 | R-454B
216766186 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 | S9X1C080U5PSB | 34400 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.22 | 21400 | R-454B
216766188 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 | S8V2C080M5PDB | 34200 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.21 | 21400 | R-454B
211752355 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE33936 | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214244019 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CNPV*3617AL*+UI | 59TN6C060C17**14 | 23200 | 19.5 | 12.5 | 9.5 | 26800 | 20000 | 74.63% | 2.36 | 25200 | R-410A
211628416 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | YP9C060B12MP13 | 32200 | 17.5 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.82 | 25600 | R-410A
211628548 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | YPLC100C20MP13 | 31000 | 16.3 | 8.8 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
215932310 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CMN0801714B* | 32400 | 19.5 | 11 | 9.5 | 35400 | 27200 | 76.84% | 2 | 31000 | R-454B
215677185 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *97CMN1202422B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
216055312 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V080C16MP12 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055392 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055395 | 3.46 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
212437662 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A97USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212437570 | 2 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36CX** | A80UH2E070A12 | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213295992 | 1.83 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4A6V0024A1 | D(A,C,E)36A44+JMET08BS2N1+TDR |  | 22000 | 18.9 | 12.3 | 8.3 | 21400 | 19900 | 92.99% | 2.43 | 17500 | R-410A
215359331 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBDM-60HWFN10-WC3-D |  | 48000 | 17.5 | 12 | 9.5 | 48000 | 48000 | 100% | 2 | 34000 | R-454B
215678005 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1202422B* | 56000 | 18.5 | 9 | 9 | 60000 | 42000 | 70% | 2 | 51500 | R-454B
216766286 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S9X2B040U3PSB | 32200 | 16 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.11 | 21200 | R-454B
216766290 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S8V2B060M4PDB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.11 | 21200 | R-454B
215676645 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *95CSU1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.02 | 46000 | R-454B
215676795 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN0602120B* | 48000 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 2 | 47000 | R-454B
216766789 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S8V2B080M4PDB | 23200 | 17 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2 | 15300 | R-454B
216766807 | 1.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S9X2B040D3PSB | 22000 | 16 | 11.7 | 8.7 | 21200 | 17000 | 80.19% | 2 | 15100 | R-454B
213350118 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.2 | 32800 | 29400 | 89.63% | 2.7 | 26200 | R-410A
212975830 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *96VTN0801716B* | 17700 | 16 | 11 | 8.5 | 18700 | 19100 | 102.1% | 2.3 | 12500 | R-410A
216025753 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBE-30HWFN10-WL3E |  | 30000 | 17.5 | 11.7 | 10.2 | 32000 | 32000 | 100% | 2 | 23200 | R-454B
214389305 | 2.8 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4824AL*+UI | 88*TB60110C21*** | 33600 | 19.5 | 12.5 | 9 | 36600 | 26000 | 71.04% | 2.04 | 31200 | R-410A
216766976 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S9V2C080U5VSB | 34200 | 17.1 | 12 | 8.7 | 32200 | 24000 | 74.53% | 2.22 | 21200 | R-454B
216699826 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A*+MBVK16CP1X00A* |  | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
211627768 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8V100C20MP12 | 31000 | 16.3 | 8.8 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
211627803 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM8Y080B12MP11 | 31600 | 17.8 | 9.8 | 8.2 | 25000 | 31600 | 126.4% | 2.77 | 25200 | R-410A
212976734 | 2.52 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L21A* | *96VTN1002120B* | 30200 | 15.2 | 9 | 8.5 | 34200 | 27600 | 80.7% | 1.8 | 23600 | R-410A
214522509 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36C34+TDR | Y81E120C16SMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 23400 | 71.78% | 1.92 | 25400 | R-410A
212976491 | 2.55 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X43L21A* | *96VTN0802120B* | 30600 | 15.2 | 9 | 8.1 | 33400 | 26400 | 79.04% | 1.86 | 23200 | R-410A
213350125 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y81E080B12SMPS1 | 33000 | 18 | 9.5 | 8.2 | 32800 | 29400 | 89.63% | 2.7 | 26200 | R-410A
213350168 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E120C16LMPS1 | 33600 | 18 | 9.5 | 8.3 | 32800 | 30000 | 91.46% | 2.76 | 26600 | R-410A
213350175 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E120C20LMPS1 | 31600 | 17.5 | 9.3 | 8.5 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
215677205 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *96CTN1202422B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.1 | 55500 | R-454B
213205461 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *96VTN1002122A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.63 | 23400 | R-410A
208101906 | 2 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430U-24HFN1-MR0 | MAC-24HWDN1-MN0 |  | 24000 | 15.7 | 10 | 9.8 | 25600 | 18500 | 72.27% | 2.2 | 22000 | R-410A
213311181 | 2.95 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L129+CBPE3A* |  | 35400 | 15.2 | 9.5 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
216699802 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*96TC1005CNA* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
216055999 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055231 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | LPLC100C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055238 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 40000 | 16.5 | 11.2 | 8.1 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216055247 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL9E100C20UH11 | 40000 | 16.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
211168130 | 1.93 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4A6V8X24A1 | 4PXFH003AZ3+TDR | *DHMB080ACV3 | 23200 | 18 | 12 | 8.5 | 20200 | 19300 | 95.54% | 2.48 | 16800 | R-410A
211752351 | 1.97 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE32936 | A96US2V070B12 | 23600 | 20 | 13 | 8.45 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
211752352 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DE33936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213925624 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E4 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
213925625 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E6 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
214093100 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.3 | 32400 | 45000 | 138.9% | 3.11 | 26000 | R-410A
214093150 | 2.58 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TPLC100C20MP13 | 31000 | 16.3 | 8.8 | 8.5 | 32400 | 43500 | 134.3% | 3.13 | 25000 | R-410A
214092231 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | LP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 46500 | 143.5% | 3.12 | 26600 | R-410A
213350192 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y82E100C16LMPS1 | 32000 | 18 | 9.4 | 8.5 | 33400 | 28000 | 83.83% | 2.7 | 25600 | R-410A
215677815 | 4.58 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU1002122B* | 55000 | 18.5 | 9 | 8.5 | 59000 | 41500 | 70.34% | 2.04 | 50500 | R-454B
215677915 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0702120B* | 55500 | 18.5 | 8.5 | 9 | 60000 | 42000 | 70% | 2 | 51500 | R-454B
215865888 | 4.5 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-60HFN10-M3 | MVBC-60HWFPN10-MD3E |  | 54000 | 15.2 | 8.6 | 8.4 | 54000 | 38000 | 70.37% | 1.8 | 33000 | R-454B
213367822 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
215677615 | 4.67 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN0602120B* | 56000 | 17.5 | 8.5 | 9 | 65000 | 46000 | 70.77% | 2.06 | 57500 | R-454B
215677535 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN1202422B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
216699824 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | DFVE48CP0300A* |  | 34200 | 19 | 11.7 | 9.2 | 33400 | 33000 | 98.8% | 2.1 | 32000 | R-32
216699838 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*80SC0805CUA* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
216623448 | 2.42 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBM-36C24T4N10-MAS |  | 29000 | 16 | 10 | 9.5 | 32000 | 32000 | 100% | 1.85 | 25000 | R-454B
215039490 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ML17XP1-048-230A** | CH60B34+TDR | EL196UH110XE60C* | 45000 | 15.5 | 12.4 | 8.1 | 44500 | 31600 | 71.01% | 2.75 | 30800 | R-410A
214092282 | 2.73 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E040A12MP11 | 32800 | 18 | 10 | 8.1 | 32400 | 45500 | 140.4% | 3.1 | 26200 | R-410A
214092297 | 2.75 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.3 | 32400 | 45000 | 138.9% | 3.11 | 26000 | R-410A
214092329 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8Y100C16MP11 | 31600 | 18.4 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092330 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y100C16MP11 | 32400 | 18.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214092332 | 2.8 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 32400 | 46500 | 143.5% | 3.12 | 26800 | R-410A
214092380 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9Y060B12MP11 | 32600 | 17.5 | 9.5 | 8.1 | 32400 | 46000 | 142% | 2.98 | 26400 | R-410A
214092433 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 46000 | 142% | 3.06 | 26400 | R-410A
214092448 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.09 | 25800 | R-410A
214092449 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 45500 | 140.4% | 2.97 | 26200 | R-410A
214092934 | 2.6 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | LP9C120D20MP13 | 31200 | 16.8 | 9.3 | 8.5 | 32400 | 44000 | 135.8% | 3.21 | 25200 | R-410A
214092950 | 2.65 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | LPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25200 | R-410A
214092966 | 2.72 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL9E060B12UH11 | 32600 | 18 | 9.5 | 8.1 | 32400 | 44500 | 137.3% | 3.05 | 25600 | R-410A
214092968 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.1 | 32400 | 45000 | 138.9% | 3.14 | 25800 | R-410A
214092998 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V080B12MP12 | 32400 | 17 | 9.5 | 8.1 | 32400 | 46000 | 142% | 3.03 | 26400 | R-410A
213367842 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36A44+TDR | Y81E100C20LMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
212442654 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | LEM48B6 |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
216055049 | 2.55 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E120C16MP11 | 30600 | 18 | 11 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
215678205 | 1.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *97CTN0601716A* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
214447343 | 1.63 | No | No | HISENSE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUWR-24U3SF2 | AFM234+TDR |  | 19600 | 16.1 | 9.7 | 8.5 | 22600 | 16900 | 74.78% | 2.05 | 16000 | R-410A
216699840 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*97MC1005CNA* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
214093000 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8V080C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
214093001 | 2.7 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V080C16MP12 | 32400 | 17.5 | 10 | 8.5 | 32400 | 44000 | 135.8% | 3.14 | 25400 | R-410A
216055008 | 2.63 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | LP9C100C20MP13 | 31600 | 17.5 | 9.8 | 8.1 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
216055010 | 2.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | LP9C100C20MP13 | 31600 | 18 | 10 | 8.5 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
216055043 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055059 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8V080C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055092 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055108 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V100C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
213352879 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MW | MVBL-24HWFN1-MI3 |  | 24000 | 19 | 12 | 9.3 | 27400 | 24000 | 87.59% | 1.91 | 19200 | R-410A
216764295 | 2.8 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 |  | 33600 | 16 | 11.2 | 8.7 | 33400 | 24800 | 74.25% | 2.1 | 22000 | R-454B
216764411 | 2.8 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC009AS3 |  | 33600 | 16 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
213204079 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80ES(N,L)0702116A* | 23800 | 16 | 9.5 | 8.1 | 25400 | 27800 | 109.4% | 2.65 | 25600 | R-410A
213204196 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92ESN1002120A* | 23800 | 16 | 9.5 | 8.5 | 26000 | 27600 | 106.2% | 2.7 | 25000 | R-410A
213204281 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *95ESN0802120A* | 23800 | 15.5 | 9 | 8.5 | 26000 | 26000 | 100% | 2.74 | 25200 | R-410A
215039643 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ML17XP1-048-230A** | CH60B34+TDR | ML180UH090E60C* | 45000 | 15.7 | 12.4 | 8.1 | 44500 | 31200 | 70.11% | 2.74 | 30600 | R-410A
214264155 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J936 | A80UH2E045A12 | 23600 | 21 | 13.5 | 8.5 | 21400 | 15000 | 70.09% | 1.9 | 13300 | R-410A
215934010 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0902120B* | 44000 | 21 | 11 | 9.5 | 48000 | 36200 | 75.42% | 1.92 | 39000 | R-454B
215934080 | 3.54 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0801714B* | 42500 | 20 | 11 | 9 | 48500 | 35200 | 72.58% | 2 | 35800 | R-454B
215934210 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0601716B* | 44500 | 20.5 | 11 | 9.5 | 49000 | 36600 | 74.69% | 2 | 39500 | R-454B
216699810 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*80TC0804C*A* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
215678165 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1002122B* | 55500 | 17 | 8.5 | 8.5 | 60000 | 42000 | 70% | 1.9 | 51500 | R-454B
215399942 | 2.53 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR |  | 30400 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.54 | 27000 | R-454B
216699814 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*80SC0805CUA* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
216764424 | 3.58 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*C009AS3 |  | 43000 | 15.5 | 11.7 | 8.7 | 44500 | 32600 | 73.26% | 2.1 | 29800 | R-454B
216699797 | 1.98 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | DFVE48CP1300A* |  | 23800 | 19.2 | 11.7 | 9.2 | 23200 | 22400 | 96.55% | 2.1 | 23000 | R-32
216699804 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*96TC0804CNA* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
213821598 | 2.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)1552420A* | 35000 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213821613 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92MSN0601412A* | 35000 | 15.5 | 9 | 8.1 | 38500 | 32400 | 84.16% | 2.51 | 29600 | R-410A
213821614 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *92MSN0601412A* | 35000 | 15.5 | 9.5 | 8.1 | 38500 | 32400 | 84.16% | 2.51 | 29600 | R-410A
213821631 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92MSN1202420A* | 35200 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
213821646 | 2.8 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *96MSN1002122A* | 33600 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.71 | 29000 | R-410A
216699815 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*97MC1005CNA* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
216699811 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*96SC0805CUA* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
216025755 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBE-18HWFN10-WM3E |  | 18000 | 19.3 | 12.1 | 10.8 | 19000 | 19600 | 103.2% | 2.1 | 19600 | R-454B
216699818 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*97MC0804CNA* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
215683055 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN0802120B* | 56500 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
215677325 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU1002120A* | 56500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56000 | R-454B
216055063 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055131 | 2.6 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C16MP11 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055206 | 2.48 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C16SMPS1 | 29800 | 17.5 | 10.5 | 8.5 | 30400 | 23400 | 76.97% | 2 | 25600 | R-454B
216054895 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE060A12MP11 | 19500 | 17 | 11 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216770122 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TAMXD07AV51 |  | 51000 | 15.2 | 11 | 8.5 | 50500 | 38000 | 75.25% | 2.14 | 33600 | R-454B
214092702 | 2.78 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.3 | 33400 | 29400 | 88.02% | 2.78 | 26400 | R-410A
214092761 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.66 | 26400 | R-410A
213752441 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC6A040M14**10 | 23200 | 15.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
211628537 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | YPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
212924805 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MW | MVBE-24HWFN1-MM3E |  | 24000 | 17.5 | 11.7 | 10.5 | 26000 | 24000 | 92.31% | 2 | 20000 | R-410A
216620299 | 1.5 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBM-24B18T3N10 |  | 18000 | 16.1 | 11.7 | 9.5 | 19000 | 18000 | 94.74% | 2.06 | 15200 | R-454B
216699819 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | DFVE60DP1300A* |  | 34200 | 19 | 11.7 | 9.2 | 33800 | 33000 | 97.63% | 2.1 | 32000 | R-32
216699820 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | DFVE60DP0300A* |  | 34200 | 19 | 11.7 | 9.2 | 33800 | 33000 | 97.63% | 2.1 | 32000 | R-32
214264209 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214301297 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BP**+TXV | A98USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216620298 | 1.5 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBM-24A18T3N10 |  | 18000 | 16.1 | 11.7 | 9.5 | 19000 | 18000 | 94.74% | 2.06 | 15200 | R-454B
214264205 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J936 | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
211599657 | 3.25 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YH2F42TB21 | LEM48C4 |  | 39000 | 16 | 12.5 | 8.1 | 40500 | 29000 | 71.6% | 3.33 | 28200 | R-410A
212977700 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *80MS(N,L)0451412A* | 23600 | 17 | 10.5 | 8.5 | 26400 | 24200 | 91.67% | 2 | 19100 | R-410A
211628520 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | YPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 25400 | 31600 | 124.4% | 2.87 | 25400 | R-410A
215359330 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3 | MVBC-60HWFN10-MD3E-D |  | 48000 | 16 | 10 | 8.5 | 48000 | 38000 | 79.17% | 1.85 | 32400 | R-454B
216699809 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*80TC0804C*A* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
213205166 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0702116A* | 29600 | 15.2 | 9 | 8.1 | 33600 | 23800 | 70.83% | 2.69 | 23200 | R-410A
214092788 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.3 | 33000 | 29000 | 87.88% | 2.72 | 26000 | R-410A
214092820 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214092913 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | YPLC100C16MP13 | 32400 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214092745 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E060A10MP12 | 32400 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.59 | 25400 | R-410A
215065661 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | Y81E100C20SMPS1 | 30800 | 17.2 | 9.2 | 8.1 | 32800 | 24200 | 73.78% | 2.14 | 25000 | R-410A
215065670 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | Y81E120C20LMPS1 | 30800 | 17.2 | 9.2 | 8.1 | 33400 | 24600 | 73.65% | 2.12 | 25400 | R-410A
216055158 | 2.57 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080B12MP13 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055160 | 2.57 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055177 | 2.58 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TPLC100C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
213311191 | 3 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H***P449+CBPE3A* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
215677525 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN1002122B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
213281574 | 2.93 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E100C20LMPS1 | 35200 | 16.5 | 9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213281577 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36B34+TDR | Y81E100C20SMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
215677775 | 4.58 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0902120B* | 55000 | 18.5 | 9 | 9 | 59000 | 41500 | 70.34% | 2.04 | 50500 | R-454B
215677825 | 4.5 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0602120B* | 54000 | 17.5 | 8 | 8.5 | 60500 | 42500 | 70.25% | 1.86 | 52000 | R-454B
213205067 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN1002120A* | 23000 | 17 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.96 | 18600 | R-410A
213821546 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *96VTN1002120B* | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
213821548 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *96VTN1002120B* | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
213367722 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YPLC080C16MP13 | 29800 | 16.9 | 9.5 | 8.5 | 33800 | 27400 | 81.07% | 2.67 | 25400 | R-410A
213367786 | 2.5 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | YPLC100C20MP13 | 30000 | 16 | 8.6 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
213927854 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A3G+TXV+TDR | TM9Y100C20MP11 | 32200 | 15.5 | 9.4 | 8.1 | 34000 | 27400 | 80.59% | 2.45 | 25400 | R-410A
213367718 | 2.47 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YP9C100C20MP13 | 29600 | 16.9 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
216680635 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3617AL* | 927TA48080V17*** | 23400 | 16.5 | 10 | 9 | 25800 | 23800 | 92.25% | 1.78 | 18900 | R-410A
215359326 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBDM-36HWFN10-WB3-D |  | 30000 | 17.2 | 12 | 10.8 | 33000 | 33200 | 100.6% | 1.97 | 24000 | R-454B
213941156 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9E080B12MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
216766891 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8V2A040M3PDB | 31600 | 15.5 | 11.7 | 8.5 | 32000 | 23800 | 74.38% | 2.07 | 21000 | R-454B
216766898 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8V2B060M4PCB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.09 | 21200 | R-454B
216766923 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8V2B060M4PCB | 32600 | 16 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.98 | 21600 | R-454B
216699799 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A*+MBVK16CP1X00A* |  | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
216699813 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*80SC0805CUA* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
214091944 | 2.7 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TL8E080C16UH11 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
214091969 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.2 | 33000 | 28600 | 86.67% | 2.7 | 25800 | R-410A
214092008 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y100C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
214092042 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.69 | 26600 | R-410A
214092049 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9V100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
216054913 | 1.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TP9C060B12MP13 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055213 | 2.67 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z9ES100C16SMPS1 | 32000 | 17.5 | 10.5 | 8.1 | 32600 | 24600 | 75.46% | 2 | 26400 | R-454B
213355417 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36F6 |  | 33000 | 17 | 9.5 | 8.1 | 31800 | 27000 | 84.91% | 2.73 | 24600 | R-410A
215318731 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBDM-36HWFN10-WB3 |  | 30000 | 17.2 | 12.1 | 10.8 | 33000 | 33200 | 100.6% | 1.97 | 24000 | R-454B
215931510 | 3.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | FCMA5B60L0D*+WALLCON |  | 46500 | 23 | 12.5 | 9.5 | 48000 | 35600 | 74.17% | 1.98 | 39000 | R-454B
215678255 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *97CTN0801716A* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2.02 | 19800 | R-454B
213607597 | 1.51 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FTMA4X24L0B* |  | 18100 | 16.5 | 11 | 8.5 | 18200 | 18200 | 100% | 2.2 | 12400 | R-410A
214279929 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3717AL* | 59SC6A060M17**16 | 24200 | 16.5 | 10 | 9 | 25400 | 21800 | 85.83% | 1.82 | 18800 | R-410A
213203948 | 1.49 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0701712A* | 17900 | 16.5 | 11 | 8.5 | 18700 | 13200 | 70.59% | 2.21 | 14100 | R-410A
215439762 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A*+MBVK12BP1X00A* |  | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
213367716 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YP9C080C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
213203953 | 1.42 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *92ESN0401410A* | 17000 | 15.3 | 10.2 | 8.5 | 18400 | 13800 | 75% | 2.28 | 14200 | R-410A
211755737 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TL8E060A12UH11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211755835 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9V060B12MP12 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
215285708 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y91E080C16SMPS1 | 31600 | 17 | 9.9 | 8.5 | 32000 | 22400 | 70% | 1.8 | 25000 | R-410A
215285709 | 2.65 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y91E080C20SMPS1 | 31800 | 17 | 9.9 | 8.5 | 32800 | 23000 | 70.12% | 1.8 | 25600 | R-410A
215065773 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH48A34+TDR | Y81E080C20SMPS1 | 31800 | 18 | 9.9 | 8.3 | 33000 | 24400 | 73.94% | 2.12 | 25600 | R-410A
215065790 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH48A34+TDR | Y81E100C20SMPS1 | 31800 | 17.5 | 9.4 | 8.3 | 33000 | 24200 | 73.33% | 2.14 | 25200 | R-410A
213821549 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)42B34+TDR | *96VTN1002120B* | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
214092053 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9V120D20MP12 | 31200 | 16.8 | 9.3 | 8.5 | 32200 | 28000 | 86.96% | 2.79 | 25200 | R-410A
214092001 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y080B12MP11 | 32600 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
214092035 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9V040A10MP12 | 31000 | 16.9 | 9.3 | 8.1 | 33200 | 27400 | 82.53% | 2.6 | 25200 | R-410A
214092060 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9Y080B12MP11 | 32400 | 17.5 | 9.5 | 8.1 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
211755817 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9E060B12MP12 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.46 | 25800 | R-410A
211755831 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.5 | 25000 | R-410A
211755833 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9V040A10MP12 | 31400 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.49 | 25200 | R-410A
213205168 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)42B34+TDR | *80ES(N,L)0702116A* | 29600 | 15.2 | 9 | 8.1 | 33600 | 23800 | 70.83% | 2.69 | 23200 | R-410A
213205251 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *80ES(N,L)1102420A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.7 | 23400 | R-410A
213205316 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *92ESN0801716A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.67 | 23400 | R-410A
216764503 | 4.33 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D010AS3 |  | 52000 | 15.2 | 10 | 8.7 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
215675895 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *80CTL1352422B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
214091953 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.64 | 25800 | R-410A
214091954 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL9E080C16UH11 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.64 | 25800 | R-410A
214091956 | 2.78 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.3 | 33400 | 29400 | 88.02% | 2.78 | 26400 | R-410A
214092005 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y080C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
214092072 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9Y120D20MP11 | 32000 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.76 | 25400 | R-410A
214092120 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TP9C120D20MP13 | 32000 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
213753059 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C100V21**22 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.94 | 19100 | R-410A
212984743 | 1.49 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *92MSN0801716A* | 17900 | 16.5 | 10.5 | 8.5 | 18500 | 18700 | 101.1% | 2.26 | 12400 | R-410A
211755909 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
211755948 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211755964 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YPLC100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211756000 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8V060A12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211756068 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
211756075 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE120C16MP11 | 32000 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
214861556 | 4.5 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-60HFN10-M3 | MVBC-60HWFN10-MD3E |  | 54000 | 15.2 | 8.7 | 8.4 | 54000 | 38000 | 70.37% | 1.8 | 33000 | R-454B
216797095 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B040D3PSC+LRP | 29800 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.68 | 39000 | R-454B
213205463 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)42B34+TDR | *96VTN1002122A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.63 | 23400 | R-410A
211755890 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLE120C16MP11 | 32000 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
211755908 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
211755922 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TPLC080B12MP13 | 32000 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.49 | 26400 | R-410A
211755931 | 2.53 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TPLC100C20MP13 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755933 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755958 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YPLC080B12MP13 | 32000 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.49 | 26400 | R-410A
211755967 | 2.53 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YPLC100C20MP13 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
216766893 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8V2B060M4PDB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.09 | 21200 | R-454B
216766894 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8V2B080M4PDB | 32000 | 16 | 11.7 | 8.5 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216766910 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S8V2B060M4PDB | 33200 | 16.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
216766946 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3+P0V0C000M50SD |  | 32800 | 16.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
216766993 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S8V2C080M5PDB | 33400 | 16.5 | 12 | 8.5 | 33400 | 24400 | 73.05% | 2.1 | 21600 | R-454B
214092171 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y81E120C16SMPS1 | 33600 | 18 | 9.5 | 8.2 | 32800 | 30000 | 91.46% | 2.76 | 26600 | R-410A
214092173 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y81E120C20LMPS1 | 32600 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214092174 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E120C20SMPS1 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214092187 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | YP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.63 | 25600 | R-410A
214092189 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | YP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.63 | 26400 | R-410A
214092022 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.59 | 25800 | R-410A
214861590 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBDM-30HWFN10-WB3-D |  | 30000 | 17.2 | 12 | 10.8 | 33000 | 33200 | 100.6% | 1.97 | 24000 | R-454B
213821203 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0901714A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821220 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80MS(N,L)1102120A* | 23400 | 17.5 | 10.3 | 8.5 | 25600 | 20000 | 78.12% | 3.01 | 18800 | R-410A
213821338 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *96VTN1002122B* | 23200 | 17.5 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
213821339 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN1002122B* | 23000 | 17.4 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
213821354 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *80MS(N,L)0701412A* | 29600 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
215676985 | 4.58 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0701716B* | 55000 | 18 | 9.5 | 9 | 59500 | 43500 | 73.11% | 2.1 | 54000 | R-454B
216764367 | 2.78 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 |  | 33400 | 16 | 11.2 | 8.7 | 33200 | 24600 | 74.1% | 2.1 | 21800 | R-454B
213203974 | 1.45 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *95ESN0261410A* | 17400 | 15.9 | 10.8 | 8.5 | 18600 | 14200 | 76.34% | 2.24 | 14500 | R-410A
213367776 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | YP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.63 | 25600 | R-410A
211755738 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TL8E060A12UH11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211755858 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9Y080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
211755872 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLE040A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.5 | 25200 | R-410A
211755915 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
211755917 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
211755947 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211755949 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
211755951 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
216767012 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*D010AS3 | S9X1D120U5PSB | 34400 | 16 | 12.5 | 9 | 32200 | 23800 | 73.91% | 2.22 | 21000 | R-454B
216767027 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S8V2B060M4PDB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.09 | 21200 | R-454B
216767029 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3+P0V0A000M30SD |  | 31800 | 15.5 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.08 | 21200 | R-454B
213203946 | 1.49 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *80ES(N,L)0701712A* | 17900 | 16.5 | 11 | 8.5 | 18700 | 13700 | 73.26% | 2.27 | 14200 | R-410A
213203981 | 1.42 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *95ESN0401410A* | 17000 | 15.8 | 10.2 | 8.5 | 18200 | 15400 | 84.62% | 2.3 | 15500 | R-410A
213203995 | 1.45 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *96VTN0401410A* | 17400 | 16 | 10.5 | 8.5 | 18300 | 14200 | 77.6% | 2.24 | 14500 | R-410A
216699803 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*96TC0804CNA* | 23000 | 16.9 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
213367818 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.63 | 25600 | R-410A
213367825 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 28800 | 85.71% | 2.59 | 26200 | R-410A
216699805 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*80TC1005C*A* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
216699807 | 1.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CHPEA4830*3A* | D*80TC0805C*A* | 23000 | 18.2 | 11.7 | 9 | 21000 | 21000 | 100% | 2 | 21000 | R-32
215065611 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | Y81E080C16LMPS1 | 30800 | 17.8 | 9 | 8.1 | 32800 | 24200 | 73.78% | 2.14 | 25000 | R-410A
213821071 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80VTL0902120B* | 23400 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213821103 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *92MSN0802120A* | 23800 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821105 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *92MSN0802120A* | 23800 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213821119 | 1.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96MSN0401410A* | 22800 | 15.4 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
213821122 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96MSN0401712A* | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213821139 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96MSN0802120A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213821156 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96VTN0801716B* | 23200 | 16 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
213821170 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN1002120B* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
215065627 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | TM8V100C16MP12 | 31000 | 17.3 | 9.7 | 8.1 | 33400 | 23800 | 71.26% | 2.08 | 25200 | R-410A
215065629 | 2.52 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | TM8V100C20MP12 | 30200 | 16.1 | 8 | 8.2 | 31800 | 23800 | 74.84% | 2.06 | 24800 | R-410A
215065652 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | Y81E100C16LMPS1 | 30800 | 17.8 | 9.2 | 8.1 | 32800 | 24400 | 74.39% | 2.12 | 25400 | R-410A
214574717 | 2.73 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH837GKA2* | EN(A,D,W)4X60L24**+WALLCON | *95CSU1002122B* | 32800 | 19 | 12 | 8.5 | 32200 | 24600 | 76.4% | 1.98 | 31200 | R-410A
215797517 | 3 | Yes | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3X | MVBC-36HWFN10-MC3E |  | 36000 | 16.5 | 10 | 8.2 | 37000 | 32000 | 86.49% | 1.85 | 23200 | R-454B
216699832 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*80TC1005C*A* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
214522499 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36C34+TDR | Y81E080C16SMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 23400 | 70.48% | 2.02 | 25600 | R-410A
211756116 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | YP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
211755823 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9E080C16MP12 | 31200 | 17.8 | 9.7 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
211755834 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9V040A10MP12 | 31600 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.49 | 25200 | R-410A
211755866 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.44 | 25600 | R-410A
211755891 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TMLE120C16MP11 | 32200 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
216766712 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S9V2D120D5VSB | 51000 | 15.2 | 11 | 8.7 | 51000 | 38500 | 75.49% | 2.19 | 33800 | R-454B
215065655 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | Y81E100C16SMPS1 | 30800 | 17.8 | 9.2 | 8.1 | 32800 | 24400 | 74.39% | 2.12 | 25400 | R-410A
211755787 | 2.53 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8V100C20MP12 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755818 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9E060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.46 | 25800 | R-410A
211755836 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9V060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
215065617 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH36A34+TDR | Y81E080C20LMPS1 | 30800 | 17.8 | 9 | 8.1 | 32800 | 24400 | 74.39% | 2.12 | 25400 | R-410A
215065735 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH48A34+TDR | TM8V100C20MP12 | 31200 | 16.4 | 8.8 | 8.4 | 32000 | 23800 | 74.38% | 2.06 | 25000 | R-410A
215065787 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH48A34+TDR | Y81E100C20LMPS1 | 31800 | 17.5 | 9.4 | 8.3 | 33000 | 24200 | 73.33% | 2.14 | 25200 | R-410A
213367783 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | YPLC080B12MP13 | 31600 | 17 | 9 | 8.1 | 33600 | 29200 | 86.9% | 2.69 | 26400 | R-410A
216699806 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*80TC1005C*A* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
211755886 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE100C16MP11 | 32600 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.57 | 26000 | R-410A
211755918 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
211755920 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211755937 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YP9C060B12MP13 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
211755953 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
213206316 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A090E21**20 | 23800 | 17 | 10.3 | 8.1 | 25800 | 20000 | 77.52% | 3.02 | 18900 | R-410A
213206323 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A110E21**20 | 23800 | 16.5 | 10.4 | 8.1 | 26200 | 20200 | 77.1% | 3.02 | 19100 | R-410A
213206355 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*A070V17**16 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
216766991 | 2.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S9X2C100D5PSB | 33800 | 15.5 | 11.7 | 8.7 | 33600 | 24600 | 73.21% | 2.11 | 21800 | R-454B
216767023 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S9X1B060U4PSB | 32000 | 16 | 11.7 | 8.5 | 32000 | 23800 | 74.38% | 2.09 | 21000 | R-454B
213927853 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9Y100C20MP11 | 32800 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.44 | 25600 | R-410A
213927869 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A4G+TXV+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.5 | 25000 | R-410A
213367808 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y82E120C20LMPS1 | 32800 | 18.5 | 8 | 8.1 | 36000 | 25600 | 71.11% | 2.62 | 25000 | R-410A
211755747 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.46 | 25600 | R-410A
211755824 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9E080C16MP12 | 32200 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
211755856 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9Y080B12MP11 | 31000 | 17.8 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
211755865 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9Y100C20MP11 | 30800 | 15.2 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.44 | 25600 | R-410A
211755883 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE100B12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211755897 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211755899 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211756040 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
211756083 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
211756090 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211756106 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211756117 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
211755965 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211755972 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755999 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8V060A12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211756026 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E060A10MP12 | 31800 | 17.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.48 | 25400 | R-410A
211756067 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
211756081 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211756092 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
215932100 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *97CMN0801714B* | 32000 | 19 | 10.5 | 9.5 | 35600 | 27400 | 76.97% | 1.98 | 31400 | R-454B
213205832 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*A070E14**12 | 23800 | 16 | 9.5 | 8.1 | 25600 | 22400 | 87.5% | 2.94 | 20200 | R-410A
213205914 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*A070V14**12 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.85 | 20400 | R-410A
214389281 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4821AL*+UI | 88*TB48070C17*** | 33400 | 19 | 12 | 9 | 36800 | 26200 | 71.2% | 2.02 | 31400 | R-410A
213205916 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*A070V14**12 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.85 | 20400 | R-410A
213205921 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*A070V17**16 | 23800 | 16.5 | 9.5 | 8.1 | 25200 | 22600 | 89.68% | 2.85 | 20200 | R-410A
213205955 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58TP*A090V21**20 | 23800 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.98 | 20000 | R-410A
213206005 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2D060E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.87 | 20400 | R-410A
211755898 | 2.53 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLV120C20MP12 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
215942499 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0901716B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.02 | 32600 | R-454B
216766628 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S8V2C100M5PDB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.22 | 29200 | R-454B
213205805 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*A045E14**12 | 23800 | 15.5 | 9.4 | 8.5 | 25600 | 22400 | 87.5% | 2.92 | 20200 | R-410A
213206030 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2D080E21**20 | 23800 | 16 | 9 | 8.5 | 26000 | 23000 | 88.46% | 2.92 | 20600 | R-410A
213206039 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59SC2D080E21**20 | 23800 | 16 | 9.5 | 8.5 | 26000 | 23000 | 88.46% | 2.91 | 20600 | R-410A
213752541 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SP6A080V21**20 | 23800 | 16 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213752574 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6C040V17**12 | 23400 | 15.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.82 | 19900 | R-410A
211618662 | 2.92 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | LEM36E4 |  | 35000 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
215031314 | 2.6 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CH48B34+TDR | D*97MC1005CNA* | 31200 | 19 | 11.9 | 8.1 | 33600 | 24400 | 72.62% | 1.8 | 21400 | R-410A
213214823 | 1.53 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN1-MW | MVC-18HWFN1-M |  | 18400 | 19.4 | 13.1 | 9.8 | 20400 | 22200 | 108.8% | 1.75 | 13800 | R-410A
212623962 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8E080B12MP11 | 33000 | 18 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212984623 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *92MSN0801716A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 23800 | 90.84% | 2 | 19000 | R-410A
213206334 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*A045V14**12 | 23600 | 17 | 10.4 | 8.1 | 25600 | 20000 | 78.12% | 2.98 | 18800 | R-410A
212985952 | 1.44 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L14** | *96MSN0261410A* | 17300 | 20 | 10.5 | 8.1 | 18300 | 19200 | 104.9% | 2.3 | 12300 | R-410A
212623561 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9E040A10MP12 | 31600 | 17 | 9 | 8.1 | 33400 | 28400 | 85.03% | 2.42 | 25800 | R-410A
212623643 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8V080B12MP12 | 31200 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623693 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TL9E060B12UH11 | 31000 | 17.8 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623727 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9E060B12MP12 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623736 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9E060B12MP12 | 33000 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623836 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | CP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
213207254 | 2.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36C34+TDR | 59SC5B080E21**20 | 34800 | 15.5 | 9.9 | 8.1 | 39000 | 31600 | 81.03% | 2.8 | 29200 | R-410A
213206488 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC5B026E14**10 | 23200 | 16.5 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
216764269 | 2.75 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 |  | 33000 | 16 | 11.2 | 8.5 | 33800 | 24800 | 73.37% | 2 | 22000 | R-454B
212622771 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9E060A10MP12 | 32600 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212622772 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9E060A10MP12 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
211755987 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211756036 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.5 | 25000 | R-410A
211756054 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9Y080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
211756071 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
213785014 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CAP**2417AL*+UI | 88*TB48070C17*** | 23000 | 19.5 | 12.5 | 10 | 27000 | 20200 | 74.81% | 2.28 | 25200 | R-410A
213785132 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CAP**4221AL*+UI | 88*TB48070C17*** | 23400 | 20 | 13 | 10 | 26600 | 19800 | 74.44% | 2.44 | 24800 | R-410A
214574387 | 2.72 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH837GKA2* | EHD4X48AAL+WALLCON | *96CTN0802120B* | 32600 | 17.5 | 11 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31600 | R-410A
215677165 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *97CMN0602120B* | 55500 | 17.5 | 8.5 | 8.5 | 64000 | 45500 | 71.09% | 1.94 | 57000 | R-454B
212623564 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9E040A10MP12 | 31600 | 17 | 9 | 8.1 | 33400 | 28400 | 85.03% | 2.42 | 25800 | R-410A
212623666 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623682 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623683 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
213927866 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B3G+TXV+TDR | TM9E080C16MP12 | 32200 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
213927861 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A4G+TXV+TDR | TM9E060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.46 | 25800 | R-410A
213367739 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C24+TDR | Y81E100C20SMPS1 | 31400 | 15.9 | 8.5 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213367800 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y81E100C20LMPS1 | 32400 | 16.1 | 8 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213367782 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | YPLC060A12MP13 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28400 | 85.03% | 2.74 | 26000 | R-410A
213367823 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | YP9C120D20MP13 | 31600 | 17 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
216767025 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S9V2B060U4VSB | 31600 | 16 | 11.7 | 8.5 | 31800 | 23800 | 74.84% | 2.08 | 20800 | R-454B
212622976 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | TM9V100C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
212623069 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM9E080B12MP12 | 33000 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623074 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9E080B12MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623076 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9E080B12MP12 | 31200 | 17.3 | 9.7 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623085 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212623092 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212623124 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
213785397 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CAP**3721AL*+UI | 88*TB48070C17*** | 33800 | 19 | 11.7 | 9 | 36600 | 25800 | 70.49% | 2.02 | 31000 | R-410A
213206300 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A090E17**14 | 23800 | 17 | 10.4 | 8.1 | 25800 | 20000 | 77.52% | 2.91 | 18900 | R-410A
215939663 | 2.73 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0401712B* | 32800 | 20 | 11.5 | 9.5 | 34800 | 26600 | 76.44% | 2.02 | 30600 | R-454B
215939763 | 2.77 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0801716A* | 33200 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
215932570 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1352422B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.06 | 29800 | R-454B
213206432 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC2D060E14**12 | 23400 | 17 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213206406 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2D040E14**10 | 23200 | 15.4 | 9.8 | 8.1 | 26000 | 20400 | 78.46% | 2.94 | 19100 | R-410A
213206481 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC5B026E14**10 | 23000 | 16.5 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213206599 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6B060V17**14 | 23600 | 16.5 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.8 | 19100 | R-410A
215932010 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X30M17A*+WALLCON | *97CMN0601714B* | 31800 | 18.5 | 10.5 | 9 | 34600 | 26600 | 76.88% | 1.9 | 30600 | R-454B
215932410 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0451712B* | 33000 | 19.5 | 10.5 | 9 | 35400 | 27200 | 76.84% | 1.9 | 31000 | R-454B
215932480 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0602120B* | 33200 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
216055409 | 3.38 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C20SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
215850665 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CPLC100C16MP13 | 40500 | 17 | 11 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215850699 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216699828 | 2.85 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA361CA* | CA*EA6030*3A* | D*96TC1005CNA* | 34200 | 19 | 11.7 | 9.2 | 32600 | 32600 | 100% | 2 | 31000 | R-32
215850701 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TL8E080C16UH11 | 41500 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
215850818 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850934 | 3.29 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080C16MP12 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215850966 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215851000 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
215851032 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60B3K+TDR | TMLE080C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215851049 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | TMLE100C20MP11 | 42500 | 17 | 11 | 8.5 | 46500 | 35000 | 75.27% | 2 | 35200 | R-454B
215851119 | 3.29 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
212623158 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8E100B12MP11 | 33200 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623183 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623242 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | TL8E080C16UH11 | 31800 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623249 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM9V080C16MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623283 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A34+TDR | TM8Y100C16MP11 | 31800 | 18.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
212623333 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM9V080C16MP12 | 32200 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623351 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9V080C16MP12 | 33000 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623360 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
213206339 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58TP*A045V14**12 | 23600 | 17 | 10.4 | 8.1 | 25600 | 20000 | 78.12% | 2.86 | 18800 | R-410A
213206155 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6B060V14**12 | 22600 | 15.8 | 9.3 | 8.1 | 24400 | 22000 | 90.16% | 2.93 | 19600 | R-410A
215359325 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBC-36HWFN10-MC3E-D |  | 30000 | 16.8 | 11.7 | 10 | 34000 | 32600 | 95.88% | 1.96 | 23800 | R-454B
215939913 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN0802120A* | 34400 | 20.5 | 12 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
216766778 | 4.33 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S9X1D120U5PSB | 52000 | 15.2 | 11.2 | 9 | 50500 | 38500 | 76.24% | 2.22 | 33600 | R-454B
215933380 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *95CSU0802120B* | 33600 | 19 | 11 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
213362041 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG35948 | BGH96M080B3B | 41000 | 16 | 11 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
213184855 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
211656133 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | A(E,F)M374+TDR |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
216770074 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S8X2D120M5PSC | 51500 | 16 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34400 | R-454B
215894240 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBE-24HWFN10-WM3E |  | 24000 | 17.4 | 10.8 | 10.4 | 25000 | 19600 | 78.4% | 1.96 | 20800 | R-454B
213362473 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG35936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213363290 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG32924 | BGH96M060B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
215931630 | 4.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1202422B* | 55500 | 18.5 | 11 | 8.5 | 60500 | 46000 | 76.03% | 2.06 | 47000 | R-454B
213205808 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*A045E14**12 | 23600 | 15.4 | 9.3 | 8.5 | 25600 | 22400 | 87.5% | 2.92 | 20200 | R-410A
213205876 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*A090E17**14 | 23800 | 16 | 9 | 8.1 | 25800 | 22800 | 88.37% | 2.97 | 20400 | R-410A
213205878 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*A090E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.92 | 20400 | R-410A
213205892 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*A090E21**20 | 23800 | 16 | 9 | 8.5 | 25800 | 22800 | 88.37% | 2.86 | 20400 | R-410A
213206173 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6B060V17**14 | 23800 | 15.5 | 9.5 | 8.1 | 25600 | 22400 | 87.5% | 2.89 | 20200 | R-410A
215932320 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CMN0802120B* | 32800 | 19.5 | 11 | 9.5 | 34800 | 26800 | 77.01% | 2.02 | 30600 | R-454B
215932470 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0601714B* | 33000 | 19.5 | 11 | 9.5 | 34000 | 26000 | 76.47% | 2.04 | 29800 | R-454B
213352798 | 1.67 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-20HFN1-MW | MVBM-24A18T3N1 |  | 20000 | 16.3 | 11.7 | 10.2 | 25000 | 20000 | 80% | 2 | 22400 | R-410A
211755902 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
211755919 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TPLC060A12MP13 | 31000 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211755968 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755969 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755971 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211756072 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
216766823 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD04AS3 | S8V2A040M3PCB | 23400 | 17 | 12 | 8.1 | 22400 | 17200 | 76.79% | 1.83 | 15400 | R-454B
216766871 | 1.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9X2B040D3PSB | 22400 | 16 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2 | 15100 | R-454B
216766882 | 1.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9V2B040D3VSB | 22600 | 16 | 12 | 8.7 | 21400 | 17100 | 79.91% | 2.03 | 15200 | R-454B
216764142 | 1.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | *DHMB080CCV3 | 22200 | 16.5 | 11.7 | 9 | 21400 | 17200 | 80.37% | 2 | 15300 | R-454B
216767055 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S8V2A040M3PCB | 32800 | 16 | 11.7 | 8.7 | 32600 | 24200 | 74.23% | 2.13 | 21400 | R-454B
216770099 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S8X2C100M5PTC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216766698 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S9X2D120D5PSB | 51000 | 15.2 | 11 | 8.7 | 51000 | 38500 | 75.49% | 2.19 | 33800 | R-454B
216699808 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*80TC0805C*A* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
215931590 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU1002122B* | 56000 | 18.5 | 11.5 | 8.5 | 60500 | 45500 | 75.21% | 2.08 | 47000 | R-454B
215931770 | 4.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1202422B* | 57000 | 18.5 | 11 | 8.5 | 60500 | 46500 | 76.86% | 2.02 | 48000 | R-454B
215940093 | 2.8 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN1202422A* | 33600 | 19 | 11.5 | 9 | 34600 | 26600 | 76.88% | 1.94 | 30400 | R-454B
215940143 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN0801716A* | 33400 | 19 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 30800 | R-454B
215940313 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CTN0802120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215940563 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *97CTN0802120A* | 34400 | 20.5 | 11.7 | 8.5 | 38500 | 28200 | 73.25% | 2.04 | 32200 | R-454B
215931940 | 2.62 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X24M17A*+WALLCON | *97CMN0601714B* | 31400 | 18.5 | 10 | 9.5 | 35000 | 27000 | 77.14% | 1.98 | 31000 | R-454B
215931990 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X25M17A*+WALLCON | *96CTN0601714B* | 33600 | 19.5 | 11 | 9.5 | 34400 | 26200 | 76.16% | 2.05 | 30200 | R-454B
215932140 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0601714B* | 33200 | 19 | 10.5 | 9.5 | 34600 | 26400 | 76.3% | 2.04 | 30400 | R-454B
215939783 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN1002122A* | 33400 | 20 | 11.7 | 9.5 | 34400 | 26200 | 76.16% | 2.04 | 30200 | R-454B
212367507 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG88960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
214301298 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A98USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212622904 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9E080B12MP12 | 31600 | 17.5 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212622921 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212623056 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM9E080B12MP12 | 30400 | 17 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623073 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9E080B12MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623087 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212623122 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM8E060A12MP11 | 30400 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623154 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623171 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TMLE060A12MP11 | 30400 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
211756102 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
212623898 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
216681537 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3012AL* | 927TA60080V21*** | 23800 | 16 | 10 | 9 | 26000 | 22800 | 87.69% | 1.78 | 19100 | R-410A
216680587 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3012AL* | 927TA48080V17*** | 23800 | 16 | 10 | 9 | 26000 | 22800 | 87.69% | 1.76 | 19100 | R-410A
215065802 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH48A34+TDR | Y81E120C20SMPS1 | 31800 | 17.5 | 9.4 | 8.3 | 33600 | 24600 | 73.21% | 2.12 | 25600 | R-410A
212623233 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.2 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212623251 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM9V080C16MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
213785499 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CAP**4821AL*+UI | 986TD42060C17*** | 33000 | 19 | 11.5 | 9 | 36800 | 26000 | 70.65% | 2 | 31200 | R-410A
213785148 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CAP**4221AL*+UI | 986TD42080C17*** | 23400 | 20 | 13 | 10 | 26600 | 19800 | 74.44% | 2.44 | 24800 | R-410A
213785166 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CAP**4321AL*+UI | 88*TB48070C17*** | 23800 | 20 | 13 | 10.5 | 26400 | 19800 | 75% | 2.52 | 24800 | R-410A
213785517 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CAP**4824AL*+UI | 986TD66120C24*** | 33200 | 19.5 | 12 | 9 | 36400 | 25800 | 70.88% | 2.04 | 31000 | R-410A
213785683 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CSPH*4212AL*+UI | 987MC42060C17*** | 33000 | 18 | 11 | 8.5 | 37000 | 26200 | 70.81% | 2 | 31600 | R-410A
212623308 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | CP9C080C16MP13 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623344 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9V080C16MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623349 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623358 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM9V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623385 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623392 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623394 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TP9C080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623558 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9E040A10MP12 | 31200 | 17 | 9.5 | 8.1 | 33400 | 28400 | 85.03% | 2.42 | 25800 | R-410A
215932240 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CTL0702120B* | 32600 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
215932890 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *95CSU0802120B* | 34400 | 20.5 | 12 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
215932910 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0602120B* | 34200 | 20 | 11.5 | 9 | 34800 | 26400 | 75.86% | 1.92 | 30400 | R-454B
215940863 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *97CTN0802120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
215851201 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851216 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC120C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851236 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
214239416 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EN(A,D,W)4X60L24**+WALLCON | *96CTN1202422B* | 32800 | 17.5 | 11.7 | 8.1 | 32200 | 24600 | 76.4% | 1.96 | 31200 | R-410A
212623713 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM9E060B12MP12 | 29800 | 16.9 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623748 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9E060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623849 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623864 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9V060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623899 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TP9C060B12MP13 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623932 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TL8E060A12UH11 | 32000 | 18 | 9 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212623933 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TL8E060A12UH11 | 32000 | 18 | 9 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212623950 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8E080B12MP11 | 29200 | 17.2 | 8.9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
215940133 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN0601716A* | 33400 | 18.5 | 10.5 | 9 | 35400 | 27200 | 76.84% | 1.92 | 31200 | R-454B
215940283 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CSU0601716B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215940633 | 2.88 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *80CSU0401712B* | 34600 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.04 | 32000 | R-454B
212621544 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B34+TDR | TM8V120C20MP12 | 31600 | 16.5 | 8.9 | 8.5 | 32200 | 27600 | 85.71% | 2.7 | 25000 | R-410A
212621562 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TPLC100C20MP13 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212621603 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TP9C120D20MP13 | 31800 | 17 | 9.4 | 8.1 | 32200 | 28200 | 87.58% | 2.5 | 25400 | R-410A
213206042 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2D100E21**20 | 23800 | 16 | 9 | 8.5 | 26000 | 23000 | 88.46% | 2.91 | 20600 | R-410A
213206044 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2D100E21**20 | 23800 | 16 | 9.5 | 8.5 | 26000 | 23000 | 88.46% | 2.91 | 20600 | R-410A
213184785 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,GE35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
215932950 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN1002122B* | 34400 | 20.5 | 12 | 9.5 | 34200 | 26000 | 76.02% | 2.08 | 29800 | R-454B
215931930 | 2.53 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X24M14A*+WALLCON | *96CTN0401410B* | 30400 | 17 | 10 | 9 | 35000 | 26800 | 76.57% | 1.9 | 30800 | R-454B
212623187 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLE060A12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623189 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TMLE060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623190 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLE060A12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
215675285 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0802120B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
215675385 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CTL0902120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
216766294 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S8V2B060M4PCB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.11 | 21200 | R-454B
213207252 | 2.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC5B080E21**20 | 34400 | 15.5 | 9.8 | 8.1 | 39000 | 31600 | 81.03% | 2.8 | 29200 | R-410A
212367409 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG34936 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215359323 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBC-24HWFN10-MB3E-D |  | 18000 | 19 | 12.5 | 9.7 | 19000 | 18000 | 94.74% | 2 | 15000 | R-454B
213238597 | 3.54 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TPLC080C16MP13 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
212361445 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32936 | BGH96M060B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
215677385 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *95CSU1002122B* | 57000 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 55500 | R-454B
213238599 | 3.54 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TPLC100C16MP13 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
213356016 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | A24VBA+TXV+AEFE4B* |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
212623817 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | CP9C060B12MP13 | 29800 | 16.9 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623876 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623878 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TP9C060B12MP13 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623896 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623987 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9Y080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212623892 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623906 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM8E080B12MP11 | 32200 | 18 | 9.4 | 8.4 | 34000 | 28000 | 82.35% | 2.6 | 25800 | R-410A
215677575 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0701716B* | 55500 | 18 | 9.5 | 9 | 60500 | 43500 | 71.9% | 2.1 | 54500 | R-454B
212623958 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8E080B12MP11 | 30600 | 17.7 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212623972 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8E080B12MP11 | 32600 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
215677675 | 4.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X61M24A*+WALLCON | *95CSU0802120B* | 57500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56500 | R-454B
212361444 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31930 | BGH96M060B3B | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 19000 | R-410A
212361563 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33(1,2)36+TXV | BGH96M060B3B | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.88 | 18400 | R-410A
215932080 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0901716B* | 32200 | 19.5 | 11 | 9.5 | 35200 | 27000 | 76.7% | 2 | 31000 | R-454B
216679462 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X24AAL | *97VTN0601716A* | 23800 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.8 | 19300 | R-410A
216680614 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *97VTN0801716A* | 23400 | 16.5 | 10 | 9 | 26600 | 23800 | 89.47% | 1.82 | 19400 | R-410A
215932200 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0601716A* | 32600 | 20 | 11 | 9.5 | 34800 | 26800 | 77.01% | 2 | 30600 | R-454B
214239634 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CNPV*4217AL*+UI | 88*TB36045C17*** | 31800 | 16.5 | 11 | 8.1 | 33400 | 25000 | 74.85% | 1.86 | 31800 | R-410A
212437656 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36BX** | A97US2V040B12X | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212438154 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A96US2V070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
212438157 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | 36DX** | A97US2V060B12X | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.9 | 13700 | R-410A
216055249 | 3.42 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E100C20UH11 | 41000 | 17 | 11 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
215851366 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES120D20SMPS1 | 43000 | 17.5 | 11.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
215850619 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | CP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32600 | R-454B
215850635 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | CP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
215850703 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E100C20UH11 | 40500 | 17.5 | 11.2 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
215850719 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
215676285 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CSU0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.12 | 46000 | R-454B
215676685 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CSU0601716A* | 48500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215565278 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
215934829 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CTL0702120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
214242626 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CNPV*3017AL*+UI | 986TD42080C17*** | 23400 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
215851300 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
215851335 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
215932460 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0601716B* | 33200 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
215932630 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1202422B* | 34000 | 20.5 | 11.7 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 29800 | R-454B
215932090 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *97CMN0601714B* | 32000 | 19 | 10.5 | 9.5 | 34600 | 26600 | 76.88% | 2 | 30400 | R-454B
213355929 | 4.17 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | A60VHA+TXV+AEFE5* |  | 50000 | 17 | 11.2 | 9.25 | 53000 | 38000 | 71.7% | 1.98 | 42500 | R-410A
212361454 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M080B3A | 41500 | 16 | 11.5 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
212925933 | 2 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL5024N1 | A(E,F)M374+TDR |  | 24000 | 15.5 | 12.5 | 8.2 | 26000 | 19900 | 76.54% | 2.8 | 18800 | R-410A
212361455 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M080B3A | 42000 | 17 | 11.5 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
212361469 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M100C5A | 44000 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
216620296 | 3 | Yes | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBL-36HWFN10-WK3 |  | 36000 | 15.4 | 10.2 | 9.8 | 37000 | 36000 | 97.3% | 1.9 | 31200 | R-454B
215931660 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0701716B* | 56000 | 18 | 11 | 8.5 | 61000 | 45500 | 74.59% | 2.1 | 46500 | R-454B
212367483 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG82936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212367485 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG82936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215359324 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBDM-24HWFN10-WA3-D |  | 18000 | 19 | 12.5 | 10.1 | 18000 | 18600 | 103.3% | 2.12 | 14700 | R-454B
216055605 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES100B12SMPS1 | 20600 | 18.8 | 11.2 | 9 | 22600 | 18000 | 79.65% | 2 | 18300 | R-454B
215565315 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 9 | 23000 | 17700 | 76.96% | 2 | 18200 | R-454B
215850762 | 3.42 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
215850812 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C16MP12 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215850878 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y120C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215850903 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
215850905 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E100C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
215851128 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215851148 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
215851171 | 3.29 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC080C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
213785697 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CSPH*4212AL*+UI | 986TD66120C24*** | 33400 | 18.5 | 11.7 | 8.5 | 36600 | 26000 | 71.04% | 2.02 | 31200 | R-410A
213785699 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CSPH*4812AL*+UI | 88*TB36045C17*** | 33200 | 18 | 11 | 8.5 | 37000 | 26200 | 70.81% | 2 | 31400 | R-410A
210474634 | 2.03 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA3* | EHD4X48AAL+WALLCON | *80CTL0701412A* | 24400 | 17 | 11 | 8.1 | 21200 | 16500 | 77.83% | 2.02 | 20600 | R-410A
216054991 | 1.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES080B12SMPS1 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
215849763 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | CP9C060B12MP13 | 22400 | 17 | 12 | 9 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849814 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TL9E060B12UH11 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215849849 | 1.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215849864 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8E100B12MP11 | 22200 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215849879 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM8V080B12MP12 | 22400 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
214242226 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CNPV*4821AL*+UI | 88*TB48090C17*** | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
215565330 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)61A3J+TDR | TL9E100C20UH11 | 41500 | 17 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
213206359 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*A070V17**16 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
215933160 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU1002122B* | 33400 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30400 | R-454B
215933210 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN1002122B* | 33400 | 19 | 11 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
214389263 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4217AL*+UI | 987MC42060C17*** | 33200 | 18.5 | 11.5 | 9 | 37600 | 26600 | 70.74% | 1.98 | 32000 | R-410A
214389293 | 2.8 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4821AL*+UI | 987MC42080C17*** | 33600 | 19 | 12 | 9 | 36800 | 26200 | 71.2% | 2.02 | 31400 | R-410A
215851351 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES100C20SMPS1 | 41000 | 17.5 | 11.2 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
215932880 | 2.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1352422B* | 34600 | 20.5 | 12 | 9.5 | 34200 | 25800 | 75.44% | 2.06 | 29800 | R-454B
215933330 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0702120B* | 33600 | 19 | 11 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215933630 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU1002122B* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30200 | R-454B
215933680 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN1202422B* | 33800 | 19.5 | 11.5 | 9 | 35000 | 26600 | 76% | 1.92 | 30600 | R-454B
215932190 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0401712A* | 32600 | 20 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2 | 30800 | R-454B
215932390 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0401712A* | 33400 | 20.5 | 11.5 | 9.5 | 34600 | 26400 | 76.3% | 2.04 | 30400 | R-454B
212367494 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG34936 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380865 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P159 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380866 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG8J936 | BGH96M080B3A | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380734 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG82936 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215851207 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215851287 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES120C16SMPS1 | 41000 | 18 | 11.7 | 8.5 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
215851305 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES130D20SMPS1 | 40500 | 17.5 | 11.7 | 8.5 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
214242326 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CNPV*4824AL*+UI | 88*TB60090C21*** | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
215849929 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9E040A10MP12 | 20800 | 16.5 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18400 | R-454B
215849949 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM9E060B12MP12 | 22200 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18600 | R-454B
215850048 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TMLE040A12MP11 | 20800 | 16.5 | 11 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215850114 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TP9C080B12MP13 | 22400 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18400 | R-454B
214239684 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CNPV*4217AL*+UI | 987MC42060C17*** | 31800 | 16.5 | 11 | 8.1 | 33200 | 25000 | 75.3% | 1.88 | 31800 | R-410A
214240034 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CNPV*6024AL*+UI | 88*TB60090C21*** | 32800 | 17.5 | 12 | 8.1 | 32200 | 24600 | 76.4% | 1.96 | 31200 | R-410A
215933780 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0702120B* | 34200 | 19.5 | 11.7 | 9 | 34400 | 26000 | 75.58% | 1.96 | 30000 | R-454B
215933800 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0902120B* | 34200 | 19.5 | 12 | 9 | 34200 | 25800 | 75.44% | 1.96 | 29800 | R-454B
215933850 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU1002122B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 25800 | 75.44% | 1.96 | 29800 | R-454B
215933930 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0801714B* | 34000 | 19.5 | 11.5 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30200 | R-454B
213352801 | 2.33 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30U-30HFN1-MR0(X) | MVBL-30HWFN1-MJ3 |  | 28000 | 18.2 | 11.7 | 8.8 | 30000 | 26000 | 86.67% | 1.8 | 20000 | R-410A
216035487 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | AE*L+CM60A3J+TDR |  | 42500 | 19 | 12 | 9 | 45500 | 39000 | 85.71% | 2.8 | 35200 | R-454B
212984968 | 2.5 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X36L21A* | *92MSN0802120A* | 30000 | 15.2 | 9 | 8.1 | 34400 | 26200 | 76.16% | 1.86 | 23200 | R-410A
215933260 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN1002122B* | 33400 | 19 | 11 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215932640 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1002122B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.06 | 29800 | R-454B
215932860 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0702120B* | 34400 | 20.5 | 12 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
214861587 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBC-24HWFN10-MB3E-D |  | 23000 | 18.3 | 11.7 | 10 | 24000 | 21600 | 90% | 1.87 | 20000 | R-454B
215933460 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0401410B* | 32000 | 17 | 10.5 | 9 | 33800 | 26000 | 76.92% | 1.96 | 30000 | R-454B
216699812 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*96SC0805CUA* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
215565320 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z8ET060A12LMPS1 | 20600 | 18.8 | 11.7 | 9 | 23000 | 17700 | 76.96% | 2 | 18200 | R-454B
215565265 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TPLC080B12MP13 | 22600 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215565272 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | Z9ES060B12SMPS1 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18600 | 81.58% | 2 | 18700 | R-454B
215565297 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM8E040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215565304 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM9E080B12MP12 | 22200 | 17 | 11.7 | 9 | 22800 | 18700 | 82.02% | 2 | 18900 | R-454B
215565313 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TP9C060B12MP13 | 22400 | 17 | 12 | 9 | 23000 | 18000 | 78.26% | 2 | 18400 | R-454B
212623967 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM8E080B12MP11 | 32400 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212623981 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9Y080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212361564 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31(1,2)30+TXV | BGH96M080B3A | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 18400 | R-410A
215677365 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL1102120B* | 57000 | 18.5 | 9.5 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
215677515 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN0802120B* | 56500 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
214239759 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X42L21**+WALLCON | *80CTL0902120B* | 31800 | 17 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.88 | 31200 | R-410A
214239929 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X48L21**+WALLCON | *97CMN1002122B* | 32400 | 17 | 11.7 | 8.1 | 32600 | 24600 | 75.46% | 1.96 | 31400 | R-410A
214240009 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D)4X48L24**+WALLCON | *97CMN1202422B* | 32400 | 17 | 11.5 | 8.1 | 32800 | 24600 | 75% | 1.94 | 31400 | R-410A
214861547 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBC-48HWFN10-MD3E |  | 48000 | 16.5 | 10.5 | 9.5 | 50000 | 46000 | 92% | 1.9 | 37000 | R-454B
215933280 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU0601716A* | 33400 | 19.5 | 11 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215933900 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN1002122B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
212984491 | 2.48 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L21A* | *92MSN0801716A* | 29800 | 15.2 | 9 | 8.1 | 34000 | 27600 | 81.18% | 1.8 | 23400 | R-410A
215932620 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1002122B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.06 | 29800 | R-454B
215934760 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X43M21A*+WALLCON | *97CMN0601714B* | 34400 | 20.5 | 11 | 8.5 | 38000 | 27600 | 72.63% | 2.08 | 31400 | R-454B
215588085 | 3.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**4821AM*+UI | 59TN6C080C17**14 | 46500 | 18 | 11.5 | 10 | 50000 | 50000 | 100% | 2.06 | 48500 | R-454B
215588117 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6121AM*+UI | 58TN*B090C17**16 | 49000 | 19 | 12 | 9.5 | 51500 | 50500 | 98.06% | 2.02 | 49500 | R-454B
216766716 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8V2C100M5PCB | 51000 | 15.2 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.18 | 34000 | R-454B
216770115 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC009AS3 | S8X2C100M5PTC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216764224 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | *UHMB060CCV3 | 32200 | 17.1 | 11.7 | 8.7 | 31800 | 23800 | 74.84% | 2.1 | 21000 | R-454B
216764240 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S9V2B080U4PSC | 33200 | 17.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216764265 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S9V2B080D4PSC | 32600 | 16.5 | 11.7 | 8.2 | 33600 | 24600 | 73.21% | 1.9 | 21600 | R-454B
213828530 | 3.42 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)49D44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
215931540 | 4.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0702120B* | 55500 | 18 | 11 | 8.1 | 60500 | 46500 | 76.86% | 1.95 | 47500 | R-454B
216035496 | 1.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AE*S+CM36B2J+TDR |  | 22000 | 19 | 12 | 9 | 23200 | 20000 | 86.21% | 2.84 | 17900 | R-454B
216683406 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X36AAL | *97VTN1202422A* | 23800 | 16 | 10 | 8.5 | 25400 | 22400 | 88.19% | 1.75 | 18700 | R-410A
214240059 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X60L24**+WALLCON | *80CTL1352422B* | 32800 | 17.5 | 12 | 8.1 | 32200 | 24600 | 76.4% | 1.96 | 31200 | R-410A
214241831 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X36L17**+WALLCON | *97CMN0801714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.9 | 20800 | R-410A
212367497 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG82936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380851 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P149 | BGH96M060B3A | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380899 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG88960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381033 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212381050 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M080C4A | 42000 | 17 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381051 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M080C4B | 42000 | 17 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
216764274 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9V2B060D3PSC | 33000 | 17.1 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2 | 21600 | R-454B
216764276 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9V2B080D4PSC | 33000 | 17.1 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2 | 21400 | R-454B
213184780 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,G36H***D129+AEFE3A* |  | 23000 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
216764290 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S9V2C100U4VSB | 33600 | 17.5 | 12 | 9 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216764292 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S8X1C100M5PSC | 33400 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
215894241 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBE-36HWFN10-WL3E |  | 36000 | 16.7 | 10.2 | 9.3 | 37000 | 29200 | 78.92% | 1.99 | 24800 | R-454B
214861575 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M2X | MVBC-36HWFN10-MC2-D |  | 36000 | 17.2 | 11.7 | 9.5 | 38000 | 38000 | 100% | 2.06 | 28000 | R-454B
216764081 | 4.42 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TEM6D06AV41+TDR |  | 53000 | 17 | 11.7 | 9 | 50500 | 38000 | 75.25% | 2.2 | 33400 | R-454B
216764099 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | L9X1C100U5VSA | 51500 | 16 | 10 | 9 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
215588175 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 59MN7C060C21**20 | 48500 | 17.5 | 10 | 10.5 | 53500 | 53000 | 99.07% | 1.88 | 51500 | R-454B
215588245 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6024XMA*+UI | 58TN*B090C21**20 | 52000 | 19.5 | 12 | 8.5 | 52500 | 46000 | 87.62% | 1.95 | 47500 | R-454B
215588275 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 59CU5B080C21**20 | 52500 | 19.5 | 12 | 8.1 | 53500 | 45500 | 85.05% | 1.9 | 48000 | R-454B
215588359 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6024XMA*+UI | 58TN*B135C24**22 | 52000 | 19.5 | 12 | 8.5 | 52500 | 46000 | 87.62% | 1.95 | 47500 | R-454B
215588411 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6124XMA*+UI | 59MN7C120C24**22 | 52500 | 19.5 | 12 | 8.5 | 53500 | 46500 | 86.92% | 1.95 | 48000 | R-454B
212380739 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG80936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380872 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG8J936 | BGH96M080B3B | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212381056 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M100D5B | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212381058 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M120D5A | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
214241981 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D)4X36L21**+WALLCON | *96CTN1002122B* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.92 | 20800 | R-410A
214242081 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | END4X42L17**+WALLCON | *96CTN0801714B* | 24000 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.98 | 20600 | R-410A
214242351 | 2.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D)4X48L24**+WALLCON | *80CTL1352422B* | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
216682070 | 2.55 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CAP**3721AL* | 927TA60100V21*** | 30600 | 15.2 | 9 | 9 | 33200 | 26000 | 78.31% | 1.8 | 23200 | R-410A
212381084 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG2K948 | BGH96M080C4A | 42000 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381085 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG2K948 | BGH96M080C4B | 42000 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
215933770 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0701716B* | 34000 | 19.5 | 11.5 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30200 | R-454B
215932130 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *96CTN0801714B* | 32200 | 19 | 10.5 | 9.5 | 35400 | 27200 | 76.84% | 1.98 | 31200 | R-454B
216035482 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | AE*L+CM48A4J+TDR |  | 41500 | 18 | 11.7 | 8.5 | 45500 | 39000 | 85.71% | 2.82 | 35200 | R-454B
213301873 | 2.42 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30U-30HFN1-MR0(X) | MVB-36B23T4N1 |  | 29000 | 15.2 | 10 | 8.5 | 31000 | 22600 | 72.9% | 1.8 | 19600 | R-410A
215932250 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CTL0901716B* | 32600 | 20 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2.02 | 30600 | R-454B
215932350 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *96CTN0801714B* | 32600 | 19.5 | 11 | 9.5 | 35200 | 27000 | 76.7% | 2 | 30800 | R-454B
215932380 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X43M21A*+WALLCON | *96CTN0601714B* | 33800 | 19.5 | 11 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 30000 | R-454B
215932430 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0901716B* | 33400 | 20 | 11.5 | 9.5 | 34600 | 26400 | 76.3% | 2.04 | 30400 | R-454B
215932450 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL1102120B* | 33400 | 20.5 | 11.7 | 9.5 | 34400 | 26200 | 76.16% | 2.04 | 30200 | R-454B
215932500 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0802120B* | 33400 | 20 | 11.5 | 9.5 | 34600 | 26400 | 76.3% | 2.02 | 30200 | R-454B
215933000 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X30M12A*+WALLCON | *97CMN0601714B* | 32200 | 18 | 10 | 9 | 34800 | 26800 | 77.01% | 1.9 | 30600 | R-454B
215932400 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU1002120A* | 33400 | 20 | 11.5 | 9.5 | 34600 | 26400 | 76.3% | 2.04 | 30400 | R-454B
215588459 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 59TN7A080C21**20 | 49500 | 18.5 | 11 | 10.5 | 52500 | 53500 | 101.9% | 1.9 | 50500 | R-454B
216764156 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | *DHMB060CCV3 | 23800 | 18 | 12.7 | 8.7 | 22200 | 17400 | 78.38% | 1.9 | 15600 | R-454B
216764181 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S9V2B040U3VSB | 23200 | 17.5 | 12.5 | 9 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
216770042 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8X1D120M5PSC | 43500 | 17.1 | 12 | 8.7 | 44500 | 32800 | 73.71% | 2.22 | 29800 | R-454B
212925895 | 2.67 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
216764201 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | L8V1B080U4VSB | 23600 | 18 | 12.7 | 9 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
212925894 | 1.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | C(A,C,D,E)24B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
214491633 | 1.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA1810A* | CA*EA1818*4B* | D*96VC0403BNA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
214491635 | 1.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA1810A* | CA*EA1818*4B* | D*96VC0803BNA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
215940063 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN0801716A* | 33400 | 18.5 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 31000 | R-454B
213184778 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,G60H210D169+AEFE5* |  | 45000 | 18 | 11.5 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-410A
213184844 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,G48H175D149+AEFE4B* |  | 44000 | 17 | 11 | 8.9 | 45500 | 33200 | 72.97% | 1.9 | 39000 | R-410A
216699816 | 1.95 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CA*EA4830*3A* | D*97MC1005CNA* | 23400 | 19.2 | 11.7 | 9.2 | 22000 | 22000 | 100% | 2 | 22000 | R-32
216774284 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | A60VHA*+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.4 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
213207094 | 2.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*A090E21**16 | 34600 | 16 | 9.8 | 8.1 | 39000 | 31200 | 80% | 2.74 | 29000 | R-410A
212621612 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | CPLC120C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212621621 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM8V120C20MP12 | 29600 | 15.9 | 8 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
212621623 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8V120C20MP12 | 29600 | 15.9 | 8 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
212621664 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | CPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621739 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621805 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9Y120D20MP11 | 29800 | 15.9 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212621807 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9Y120D20MP11 | 29800 | 15.9 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212621830 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9Y120D20MP11 | 30600 | 16.1 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
213205824 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*A070E14**12 | 23800 | 16 | 9 | 8.1 | 25600 | 22400 | 87.5% | 2.86 | 20200 | R-410A
212621837 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM9V120D20MP12 | 29800 | 16.4 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.79 | 25200 | R-410A
212621855 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | CP9C120D20MP13 | 32600 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621862 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CP9C120D20MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621871 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9V120D20MP12 | 32000 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212621889 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9V120D20MP12 | 32800 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212621898 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621991 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9E100C20MP12 | 32400 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212622064 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8Y060A12MP11 | 29400 | 17.3 | 9.4 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
216800661 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V60H210P19*+TXV | BGH96M080C4C | 42500 | 16 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.8 | 34000 | R-454B
212622089 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8Y060A12MP11 | 33200 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622096 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B24+TDR | TM8Y120C20MP11 | 32200 | 18 | 9.5 | 8.1 | 33400 | 29800 | 89.22% | 2.72 | 26600 | R-410A
212622130 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y080B12MP11 | 32800 | 18 | 10 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212622280 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A24+TDR | TM9V080B12MP12 | 30600 | 17 | 9.3 | 8.1 | 33600 | 29400 | 87.5% | 2.63 | 26400 | R-410A
212622314 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212622380 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A24+TDR | TM8E080B12MP11 | 29800 | 17.4 | 9 | 8.3 | 33600 | 28000 | 83.33% | 2.59 | 25600 | R-410A
212622398 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212622414 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | TM9Y080C16MP11 | 31200 | 18.3 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.6 | 25600 | R-410A
215565267 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | Z8ES060A12SMPS1 | 21200 | 17.5 | 11.7 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215565319 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z8ES100B12SMPS1 | 20600 | 18.8 | 11.2 | 9.5 | 23000 | 18000 | 78.26% | 2 | 18500 | R-454B
216680590 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X30AAL | *97VTN0801716A* | 23800 | 16 | 10 | 9 | 26000 | 22800 | 87.69% | 1.76 | 19100 | R-410A
213204363 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN1002120A* | 23800 | 16 | 9.5 | 8.1 | 25000 | 26000 | 104% | 2.77 | 25200 | R-410A
213753119 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 58S(B,C)*B070M17**16 | 29400 | 15.2 | 8.9 | 8.5 | 33600 | 23800 | 70.83% | 2.79 | 23200 | R-410A
212925885 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | D(A,C,E)60D44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215678195 | 1.9 | No | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CSU0601716B* | 22800 | 16.5 | 10 | 8.5 | 24000 | 16800 | 70% | 1.96 | 20200 | R-454B
215678345 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *80CSU0401712B* | 23800 | 17 | 10 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
213238541 | 3.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM8E120C20MP11 | 43000 | 16 | 11.5 | 8.2 | 44500 | 31200 | 70.11% | 3.06 | 30600 | R-410A
213238574 | 3.71 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM9E100C20MP12 | 44500 | 16.3 | 11.7 | 8.5 | 45000 | 31600 | 70.22% | 3.16 | 31000 | R-410A
213238591 | 3.5 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9Y100C16MP11 | 42000 | 15.9 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.12 | 30400 | R-410A
215931790 | 4.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN1202422B* | 57000 | 18.5 | 11.5 | 8.5 | 60500 | 46500 | 76.86% | 2.02 | 47500 | R-454B
216762900 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | A48VGC*+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-454B
216774366 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | PL48H175P38*+TXV+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
215669137 | 2.8 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0701716B* | 33600 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
214238864 | 2.62 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CNPV*3621AL*+UI | 88*TB60090C21*** | 31400 | 16.5 | 11 | 8.1 | 33000 | 24000 | 72.73% | 1.82 | 31000 | R-410A
214056972 | 3.92 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | C(A,C,D,E)48C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
216764333 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TEM6B03AV21+TDR |  | 32000 | 17.1 | 11.7 | 9 | 33600 | 24400 | 72.62% | 2.1 | 21600 | R-454B
216764376 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9V2B080U4VSB | 33400 | 17.5 | 12 | 9 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216764399 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC007AS3 | S9V2C080U5PSC | 33800 | 18 | 12 | 9 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216764406 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC009AS3 | L8V1C100U5VSB | 34200 | 18 | 12.5 | 9 | 32200 | 23800 | 73.91% | 2.2 | 21200 | R-454B
216764415 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCD008AS3 | *UHMD120CCV5 | 33600 | 17.5 | 12 | 9 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216764431 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*CD09AS3 | S8X1C100M5PSC | 43500 | 17 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.1 | 29400 | R-454B
212622439 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | TL8E100C20UH11 | 31200 | 17.4 | 9.8 | 8.3 | 33600 | 27200 | 80.95% | 2.63 | 25200 | R-410A
212622448 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9E100C16MP12 | 32600 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212622450 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM9E100C16MP12 | 30000 | 17.4 | 9.5 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212622464 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM9E100C16MP12 | 30400 | 17.5 | 9 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212622473 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A24+TDR | TL9E080C16UH11 | 29600 | 16.9 | 9 | 8.4 | 33600 | 27600 | 82.14% | 2.64 | 25400 | R-410A
212622650 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.66 | 25800 | R-410A
212622766 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9E060A10MP12 | 31800 | 17.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212622768 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9E060A10MP12 | 32600 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
216620307 | 3 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBM-36C24T4N10 |  | 36000 | 15.8 | 10.7 | 9.4 | 38000 | 36000 | 94.74% | 1.9 | 29200 | R-454B
213205868 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*A070E21**16 | 23800 | 16 | 9 | 8.1 | 25400 | 22600 | 88.98% | 2.97 | 20200 | R-410A
213205834 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A070E14**12 | 23800 | 16 | 9.5 | 8.1 | 25600 | 22400 | 87.5% | 2.94 | 20200 | R-410A
213205851 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*A070E17**16 | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 22800 | 87.02% | 2.92 | 20600 | R-410A
213205883 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A090E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.92 | 20400 | R-410A
213205885 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*A090E21**20 | 23800 | 16 | 9 | 8.5 | 25800 | 22800 | 88.37% | 2.92 | 20400 | R-410A
213205902 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*A110E21**20 | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 22800 | 87.02% | 2.85 | 20600 | R-410A
213205953 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*A090V21**20 | 23800 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.98 | 20000 | R-410A
213206020 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2D080E17**16 | 23800 | 16.5 | 9 | 8.1 | 25400 | 22600 | 88.98% | 2.91 | 20200 | R-410A
214389410 | 2.73 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*4221AL*+UI | 88*TB48090C17*** | 32800 | 19 | 12 | 9 | 38000 | 26600 | 70% | 1.98 | 32200 | R-410A
213206450 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2D080E17**16 | 23800 | 17.5 | 10.4 | 8.1 | 25600 | 20000 | 78.12% | 2.86 | 18800 | R-410A
213206568 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6B040V14**10 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.63 | 19000 | R-410A
213206582 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59TP6B040V17**12 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.69 | 19000 | R-410A
213206589 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6B060V14**12 | 23200 | 16.5 | 10 | 8.1 | 26400 | 20400 | 77.27% | 2.69 | 19300 | R-410A
211618664 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | LEM48B4 |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
212622791 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.68 | 25800 | R-410A
212622807 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.2 | 33800 | 28600 | 84.62% | 2.71 | 26000 | R-410A
212622850 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9Y100C16MP11 | 32000 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212622900 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B34+TDR | TM9E080B12MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212622934 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM8E080C16MP11 | 32200 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.73 | 26000 | R-410A
212622943 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.2 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212622993 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM8E100B12MP11 | 32400 | 18 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212623034 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM9E080B12MP12 | 30000 | 16.9 | 9.5 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
213206566 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6B040V14**10 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.63 | 19000 | R-410A
213206618 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59TP6B080V17**16 | 23400 | 17 | 10.3 | 8.1 | 25600 | 19900 | 77.73% | 2.66 | 18700 | R-410A
213206641 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59TP6B100V21**20 | 23000 | 17 | 10.3 | 8.1 | 25200 | 19900 | 78.97% | 2.7 | 18600 | R-410A
214389390 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*3621AL*+UI | 88*TB60110C21*** | 32400 | 18.5 | 11.7 | 9 | 38500 | 27000 | 70.13% | 1.92 | 32800 | R-410A
213495364 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES120C16SMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
213495409 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ET100C20LMPS1 | 32200 | 18.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
213238583 | 3.54 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9V100C20MP12 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
212623949 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8E080B12MP11 | 32000 | 18 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
216764474 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCD008AS3 | *UHMD120CCV5 | 43500 | 16 | 11.5 | 9 | 45500 | 33200 | 72.97% | 2.1 | 30400 | R-454B
216764485 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCD010AS3 | S9V2C080U5PSC | 43500 | 17.1 | 12 | 9 | 44000 | 32000 | 72.73% | 2.2 | 29200 | R-454B
216764490 | 4.21 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | L9X1C100U5VSA | 50500 | 15.5 | 10 | 8.7 | 52000 | 39500 | 75.96% | 2.1 | 34800 | R-454B
216764492 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | S9V2D120U5VSB | 51500 | 16 | 11 | 9 | 51500 | 39000 | 75.73% | 2.1 | 34200 | R-454B
215676935 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN1202422B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
215676485 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL1102120B* | 48000 | 19 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
212925892 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215675645 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0801714B* | 48000 | 18.5 | 10 | 9 | 50000 | 36200 | 72.4% | 2.02 | 45500 | R-454B
213493859 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES040A12LMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
214242451 | 1.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D)4X24L17**+WALLCON | *80CTL0901716B* | 23200 | 16 | 10.5 | 8.1 | 22000 | 16900 | 76.82% | 1.92 | 21200 | R-410A
214242601 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D)4X30L17**+WALLCON | *97CMN0801714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213785230 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CSPH*3612AL*+UI | 987MC42060C17*** | 23600 | 18.5 | 12.5 | 10 | 26600 | 19900 | 74.81% | 2.44 | 25000 | R-410A
215676545 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676575 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *96CTN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
212623107 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8E060A12MP11 | 29400 | 17.2 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623182 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623184 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TMLE060A12MP11 | 30400 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
215940733 | 2.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X48M24A*+WALLCON | *96CTN0802120B* | 35000 | 21 | 12 | 8.5 | 38500 | 28400 | 73.77% | 2.04 | 32600 | R-454B
213362042 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG35948 | BGH96M080C4B | 41000 | 16 | 11 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213828554 | 3.38 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-48U3SP | D(A,C,E)61A44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213205948 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*A090V21**20 | 23800 | 16 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.94 | 20000 | R-410A
214861536 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN10-M1 | MVBC-24HWFN10-MB1 |  | 24000 | 19.8 | 11.7 | 9 | 25000 | 18000 | 72% | 2.2 | 17600 | R-454B
213205989 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2D040E17**12 | 23800 | 15.2 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.87 | 20000 | R-410A
213205991 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59SC2D040E17**12 | 23800 | 15.2 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.88 | 20000 | R-410A
214861541 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBC-24HWFN10-MB3E |  | 23000 | 18.4 | 11.7 | 10 | 24000 | 21600 | 90% | 1.87 | 20000 | R-454B
214056971 | 2.67 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 15000 | R-410A
216681111 | 3.03 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EHD4X48AAL | *97VTN0802120A* | 36400 | 15.5 | 10 | 8.5 | 38500 | 34400 | 89.35% | 1.84 | 29200 | R-410A
213206046 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2D100E21**20 | 23800 | 16 | 9.5 | 8.5 | 26000 | 23000 | 88.46% | 2.92 | 20600 | R-410A
213206214 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6B100V21**22 | 23600 | 16.5 | 10 | 8.1 | 24800 | 22200 | 89.52% | 2.89 | 19800 | R-410A
213238545 | 3.54 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM8V080C16MP12 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
214056973 | 4.21 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215676525 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0602120B* | 47500 | 18.5 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215676725 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0702120B* | 48500 | 19 | 10.5 | 9 | 50000 | 37000 | 74% | 2 | 47000 | R-454B
212623250 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9V080C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623302 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CP9C080C16MP13 | 30800 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
213206216 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6B100V21**22 | 23600 | 16.5 | 10 | 8.1 | 24800 | 22200 | 89.52% | 2.89 | 19800 | R-410A
213206223 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59TP6B100V21**22 | 23800 | 16.5 | 10 | 8.1 | 24800 | 22200 | 89.52% | 2.97 | 19800 | R-410A
212623309 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212623316 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | CP9C080C16MP13 | 30400 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
215676425 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU1002120A* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676695 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CSU1002120A* | 48500 | 19 | 10 | 9 | 50000 | 37000 | 74% | 2 | 47000 | R-454B
216800680 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG84*60+TXV | BGH96M080C4C | 43000 | 16 | 10.5 | 8.5 | 43000 | 31200 | 72.56% | 1.85 | 32000 | R-454B
216774304 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | A60VHA*+TXV+AEFE5* |  | 46000 | 17 | 11.7 | 8.45 | 45000 | 33200 | 73.78% | 1.86 | 37000 | R-454B
216800678 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | A60VGA*+TXV | BGH96M080C4C | 43000 | 16 | 10.5 | 8.5 | 43000 | 31200 | 72.56% | 1.85 | 32000 | R-454B
213205899 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*A110E21**20 | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 22800 | 87.02% | 2.86 | 20600 | R-410A
216774302 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | A48VGA*+TXV+AEFE5* |  | 45500 | 17 | 11.5 | 8.35 | 45000 | 33200 | 73.78% | 1.84 | 37000 | R-454B
212380755 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P199 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380757 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG86960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380900 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P179 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381032 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M100C5A | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212380764 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P179 | BGH96M100C5A | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
216774282 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | A48VGA*+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-454B
213311141 | 1.97 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129+CBPE4B* |  | 23600 | 18 | 10 | 8.65 | 24800 | 22600 | 91.13% | 1.86 | 18200 | R-410A
216800803 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V48H210P19*+TXV | BGH96M080C4C | 43000 | 16 | 10.5 | 8.5 | 43000 | 31200 | 72.56% | 1.85 | 32000 | R-454B
216800805 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V48H210P19*+TXV | BGH96M100C5C | 44500 | 16 | 10.5 | 8.5 | 45000 | 32600 | 72.44% | 1.85 | 33000 | R-454B
213184692 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P169+AEFE5* |  | 45000 | 18 | 11.5 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-410A
213355884 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG9J936+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213363288 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG32924 | BGH96M060B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
216800801 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V48H210P19*+TXV | BGH96M080C4C | 42500 | 16 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.8 | 34000 | R-454B
216800665 | 4.25 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG84*60+TXV | BGH96M100C5C | 51000 | 17 | 11 | 8.5 | 51500 | 37200 | 72.23% | 1.8 | 37000 | R-454B
213184775 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,G36H***D129+AEFE3A* |  | 23000 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
212927485 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CE3005C+TXV |  | 23200 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
212380737 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG8J936 | BGH96M060B3B | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212623903 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TP9C060B12MP13 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623935 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TL8E060A12UH11 | 32800 | 18 | 9.5 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212623953 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM8E080B12MP11 | 32400 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212623960 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8E080B12MP11 | 32000 | 18 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212623969 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8E080B12MP11 | 32800 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
213493945 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100C16SMPS1 | 32200 | 18 | 9.4 | 8.5 | 33200 | 28200 | 84.94% | 2.7 | 25600 | R-410A
212623336 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9V080C16MP12 | 32600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623350 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9V080C16MP12 | 32200 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212623368 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212367482 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG34936 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215850501 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C16MP11 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215850564 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES080B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216760260 | 2.77 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG33*36+TXV+AEFE3A* |  | 33200 | 16 | 11 | 8.25 | 32400 | 33800 | 104.3% | 1.76 | 33200 | R-454B
216762917 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG37*36+TXV+AEFE4B* |  | 44500 | 16 | 11 | 8.25 | 45000 | 33200 | 73.78% | 1.82 | 37000 | R-454B
216788588 | 4.58 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG88*60+TXV+AEFE5* |  | 55000 | 16 | 10 | 8.4 | 54000 | 39000 | 72.22% | 1.85 | 38000 | R-454B
213356019 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | A24VBA+TXV+AEFE4B* |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
213363289 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG32924 | BGH96M080B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
215934140 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU1002120A* | 45000 | 21 | 11 | 9.5 | 48500 | 37000 | 76.29% | 2 | 40000 | R-454B
215588235 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6021XMA*+UI | 59MN7C080C21**20 | 52000 | 19 | 11.5 | 8.1 | 53500 | 45500 | 85.05% | 1.9 | 48500 | R-454B
212623978 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM9Y080B12MP11 | 29400 | 17.2 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
213367798 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)48C24+TDR | Y81E100C16LMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
212925931 | 2 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL5024N1 | A(E,F)M314+TDR |  | 24000 | 15.5 | 12.5 | 8.2 | 26000 | 19900 | 76.54% | 2.8 | 18800 | R-410A
212380862 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG80936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380750 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P459 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213363291 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG32924 | BGH96M080B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
216800679 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V60H210P19*+TXV | BGH96M080C4C | 43000 | 16 | 10.5 | 8.5 | 43000 | 31200 | 72.56% | 1.85 | 32000 | R-454B
212380751 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG80936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214861528 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M1X | MVBC-18HWFN10-MB1 |  | 18000 | 18.2 | 12 | 10.1 | 19500 | 18000 | 92.31% | 2.2 | 14000 | R-454B
212380853 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P159 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215676785 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *95CSU1002122B* | 48500 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
215676835 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN1002122B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
214861535 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M1 | MVBC-18HWFN10-MB1 |  | 18000 | 18.5 | 12.2 | 9.8 | 18000 | 13000 | 72.22% | 2.3 | 13200 | R-454B
212623510 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A24+TDR | TL8E100C20UH11 | 29200 | 16.7 | 9.4 | 8.5 | 33800 | 27200 | 80.47% | 2.69 | 25200 | R-410A
212623533 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | CP9C100C20MP13 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
212623637 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CPLC080B12MP13 | 31600 | 17 | 9 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623642 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8V080B12MP12 | 31200 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623644 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8V080B12MP12 | 31600 | 17 | 9 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623669 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TL9E060B12UH11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
215676535 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0801714B* | 47500 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 1.98 | 47000 | R-454B
211708463 | 3.71 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM9E060B12MP12 | 44500 | 15.5 | 11 | 8.1 | 44500 | 31200 | 70.11% | 3 | 30600 | R-410A
215412965 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG8J936+AEFE3A* |  | 23400 | 19 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215412966 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V,R36H175P459+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216093487 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG84*60+TXV+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-454B
213206364 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*A090V17**16 | 23800 | 17 | 10 | 8.1 | 26000 | 20200 | 77.69% | 2.82 | 19000 | R-410A
213146611 | 1.98 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139+AEFE3A* |  | 23800 | 18 | 10 | 8.75 | 25000 | 22600 | 90.4% | 1.88 | 18300 | R-410A
211708437 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM8E100C20MP11 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
215934299 | 3.79 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU1002120A* | 45500 | 21 | 11 | 9.5 | 48500 | 36800 | 75.88% | 2 | 40000 | R-454B
213184693 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P169+AEFE5* |  | 45000 | 18 | 11.5 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-410A
213281158 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | PL36H***P219+AEFE3A* |  | 23600 | 19 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216055830 | 2.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
213206194 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6B080V21**20 | 23800 | 16 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213613358 | 1.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24A4 |  | 22000 | 15.3 | 9.3 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213752158 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*B045M14**12 | 23000 | 16.4 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213752191 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M17**16 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752290 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*B070V14**12 | 23800 | 16.5 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.87 | 20000 | R-410A
213205919 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58TP*A070V14**12 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.85 | 20400 | R-410A
213205936 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*A090V17**16 | 23600 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
213205967 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58TP*A110V21**22 | 23800 | 16.5 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.94 | 19900 | R-410A
213206169 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6B060V17**14 | 23800 | 15.5 | 9.5 | 8.1 | 25600 | 22400 | 87.5% | 2.89 | 20200 | R-410A
213206201 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6B100V21**20 | 23600 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.9 | 20000 | R-410A
213752233 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M17**14 | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213295993 | 1.83 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4A6V0X24A1 | D(A,C,E)36A44+JMET12BS2N1+TDR |  | 22000 | 18.9 | 12.3 | 8.3 | 21400 | 19200 | 89.72% | 2.42 | 17100 | R-410A
212380869 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG82936 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212624031 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TMLE080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624050 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLE080B12MP11 | 33200 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624114 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLV060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
211708421 | 3.71 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TL9E060B12UH11 | 44500 | 15.5 | 11 | 8.1 | 44500 | 31600 | 71.01% | 3.01 | 30800 | R-410A
211708422 | 3.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TL9E080C16UH11 | 45000 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.1 | 30400 | R-410A
211708424 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TL9E100C20UH11 | 45500 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.08 | 30600 | R-410A
212361447 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31930 | BGH96M080B3A | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 19000 | R-410A
216800662 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG84*60+TXV | BGH96M080C4C | 42500 | 16 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.8 | 34000 | R-454B
216800663 | 4.17 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | A60VGA*+TXV | BGH96M100C5C | 50000 | 17 | 11 | 8.5 | 51500 | 37200 | 72.23% | 1.8 | 37000 | R-454B
215933100 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0901716B* | 33200 | 19 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30800 | R-454B
215933250 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0801714B* | 33000 | 18.5 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 31000 | R-454B
212380759 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P179 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380775 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P179 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213753117 | 2.42 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M17**16 | 29000 | 15.2 | 8.9 | 8.5 | 33600 | 23800 | 70.83% | 2.79 | 23200 | R-410A
213493992 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES120C20SMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
213494007 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ET080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.74 | 26400 | R-410A
216768269 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | FE*TT1*37+TXV |  | 34200 | 17 | 11.7 | 8.5 | 32600 | 33800 | 103.7% | 1.8 | 33200 | R-454B
216012147 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | CE2403C*+TXV |  | 22800 | 17 | 11 | 8.2 | 22400 | 16800 | 75% | 1.78 | 18000 | R-454B
214264216 | 1.98 | No | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP22LX124P-**A | H,A,DG9J(1,2)36+TXV | A98USMV070B12 | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215932670 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716A* | 34400 | 20.5 | 11.7 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
215932970 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X24M12A*+WALLCON | *97CMN0601714B* | 32000 | 17.5 | 10 | 9 | 35000 | 27000 | 77.14% | 1.9 | 31000 | R-454B
212380738 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P459 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380861 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P459 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216774287 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | A36VDA*+TXV+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
213771515 | 2.03 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4321AL*+UI | 59MN7C100C21**22 | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
214861592 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBC-36HWFN10-MC3E-D |  | 36000 | 17.4 | 11.7 | 10.3 | 37000 | 39000 | 105.4% | 1.9 | 31800 | R-454B
212623976 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8E080B12MP11 | 33400 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
213352799 | 2 | Yes | Yes | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOD30-24HFN1-MW | MVBM-24A18T3N1 |  | 24000 | 16.1 | 10.7 | 9.8 | 25000 | 20000 | 80% | 2 | 22400 | R-410A
213362043 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380712 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P179 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212380903 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG84960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361463 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M080C4A | 42000 | 17 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361478 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M100D5A | 45000 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212361562 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32(1,2)36+TXV | BGH96M060B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 18400 | R-410A
213613359 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24B4 |  | 22800 | 15.5 | 9.4 | 8.8 | 25400 | 22600 | 88.98% | 2.84 | 20200 | R-410A
213613360 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24C4 |  | 23400 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
215677485 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *95CSU0802120B* | 56500 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
215588253 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6024XMA*+UI | 59CU5B100C21**22 | 52000 | 19 | 12 | 8.1 | 52500 | 46000 | 87.62% | 1.85 | 47500 | R-454B
213356194 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | A48VGA+TXV+AEFE5* |  | 46000 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
213184856 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG48960+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
215438139 | 1.92 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*E32*30+TXV |  | 23000 | 15.2 | 11.7 | 8.8 | 22400 | 16400 | 73.21% | 1.86 | 18400 | R-454B
215588333 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 59TN6C120C24**22 | 52000 | 19 | 12 | 8.1 | 52500 | 46500 | 88.57% | 1.9 | 48000 | R-454B
215588367 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6024XMA*+UI | 59MN7C100C21**22 | 52000 | 19 | 11.5 | 8.1 | 52500 | 46500 | 88.57% | 1.85 | 48000 | R-454B
212509296 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | F,PE*SS9948 |  | 44000 | 16 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
216800681 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | A60VGA*+TXV | BGH96M100C5C | 44500 | 16 | 10.5 | 8.5 | 45000 | 32600 | 72.44% | 1.85 | 33000 | R-454B
213495279 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ES080C16SMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
213495394 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ET080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.74 | 26400 | R-410A
213238556 | 3.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM8Y080C16MP11 | 44000 | 16.2 | 11 | 8.1 | 44500 | 31600 | 71.01% | 3.18 | 30800 | R-410A
216800668 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG35*36+TXV | BGH96M060B3C | 24000 | 18 | 12 | 9 | 22400 | 16800 | 75% | 1.9 | 19000 | R-454B
213184842 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,GE35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213752182 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*B070M17**12 | 23400 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.87 | 19800 | R-410A
216774286 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | A24VBA*+TXV+AEFE3A* |  | 23200 | 20 | 12.5 | 9.25 | 22400 | 17000 | 75.89% | 1.96 | 21400 | R-454B
216775704 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | A36VEA*+TXV+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
212367401 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84948 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
212380687 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P179 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
215931910 | 4.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1002122B* | 56500 | 18 | 11 | 8.1 | 61000 | 46000 | 75.41% | 1.95 | 47500 | R-454B
213752254 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M21**20 | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
214861546 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-36HFN10-M3X | MVBC-36HWFN10-MC3E |  | 36000 | 17.4 | 11.7 | 10.3 | 37000 | 39000 | 105.4% | 1.9 | 31800 | R-454B
214242701 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D,W)4X36L17**+WALLCON | *97CMN0801714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
214243101 | 2.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D,W)4X48L21**+WALLCON | *80CTL0901716B* | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
214240079 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X60L24**+WALLCON | *97CMN1202422B* | 32800 | 17.5 | 11.7 | 8.1 | 32200 | 24600 | 76.4% | 1.96 | 31200 | R-410A
214312427 | 2.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H210P299+TD |  | 30000 | 15.5 | 11.3 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
212361449 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33936 | BGH96M080B3A | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214279020 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*G32925 |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
216732371 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | PL36H175P15*+TXV+AEFE4B* |  | 34200 | 17 | 11.7 | 8.5 | 32600 | 33800 | 103.7% | 1.8 | 33200 | R-454B
216093471 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG32*24+TXV+AEFE3A* |  | 23000 | 20 | 12.5 | 9.2 | 22400 | 17000 | 75.89% | 1.94 | 21400 | R-454B
214802104 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG8J936+AEFE3A* |  | 23400 | 19.5 | 12.7 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
211708494 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9Y120D20MP11 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.1 | 30400 | R-410A
215676205 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *80CTL0902120B* | 47000 | 19 | 10 | 9 | 50000 | 36200 | 72.4% | 2 | 45500 | R-454B
213207257 | 2.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC5B080E21**20 | 34800 | 15.5 | 9.9 | 8.1 | 39000 | 31600 | 81.03% | 2.8 | 29200 | R-410A
214521923 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES080C20SMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 28200 | 85.45% | 2.67 | 25600 | R-410A
215407285 | 1.83 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3J+TDR |  | 22000 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.67 | 18600 | R-454B
214242175 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CNPV*4221AL*+UI | 59TN6C060C17**14 | 23600 | 16 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.94 | 20800 | R-410A
214521924 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ES080C20SMPS1 | 31800 | 17.9 | 9.9 | 8.4 | 33200 | 28200 | 84.94% | 2.69 | 25600 | R-410A
214521940 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100C20LMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
213238540 | 3.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM8E120C16MP11 | 44000 | 16.2 | 11 | 8.4 | 44500 | 31200 | 70.11% | 3.21 | 30600 | R-410A
213238595 | 3.54 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9Y120D20MP11 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.1 | 30400 | R-410A
213238529 | 3.5 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM8E080C16MP11 | 42000 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.11 | 30200 | R-410A
213184858 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG88948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
212361457 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M080B3B | 41000 | 16 | 11 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
213238554 | 3.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM8Y080B12MP11 | 43500 | 16.1 | 11 | 8.1 | 44500 | 31200 | 70.11% | 3.17 | 30600 | R-410A
213238570 | 3.71 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM9E080C20MP12 | 44500 | 16.3 | 11.7 | 8.5 | 45000 | 31600 | 70.22% | 3.16 | 31000 | R-410A
212361459 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M080B3B | 42000 | 17 | 11.5 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
214861572 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M1X | MVBC-18HWFN10-MB1-D |  | 18000 | 18 | 12 | 10 | 19500 | 18000 | 92.31% | 2.2 | 14000 | R-454B
214861591 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3X | MVBDM-36HWFN10-WB3-D |  | 36000 | 17.7 | 12 | 10 | 36000 | 32600 | 90.56% | 2.06 | 24600 | R-454B
216800653 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG9J936+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213184777 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,GE35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213184779 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,GE48960+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
216799571 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*TT3937 |  | 34200 | 19 | 12 | 9.5 | 32600 | 23600 | 72.39% | 1.9 | 27000 | R-410A
216800684 | 2.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*SS9*37+TXV |  | 33800 | 19 | 11.7 | 9.4 | 32600 | 24000 | 73.62% | 1.98 | 27000 | R-454B
215438141 | 1.95 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*G34*30+TXV |  | 23400 | 15.2 | 12 | 9 | 22400 | 16400 | 73.21% | 1.9 | 18400 | R-454B
214861593 | 3.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-42HFN10-M3X-D | MVBC-42HWFN10-MD3E-DD |  | 42000 | 16.7 | 11.7 | 9.5 | 50000 | 46000 | 92% | 1.9 | 37000 | R-454B
213752375 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2E060M14**12 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.9 | 20200 | R-410A
213752389 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2E060M17**14 | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
212361462 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M080C4A | 41500 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361581 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 33400 | R-410A
213752423 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2E100M21**20 | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752575 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6C040V17**12 | 23400 | 15.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.82 | 19900 | R-410A
213752591 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6C080V17**16 | 23200 | 16 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.84 | 19800 | R-410A
213281362 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H***P219+AEFE3A* |  | 23600 | 19 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213238535 | 3.5 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM8E100C16MP11 | 42000 | 15.9 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.12 | 30400 | R-410A
214861542 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBDM-24HWFN10-WA3 |  | 24000 | 18.7 | 12 | 10 | 24000 | 20600 | 85.83% | 2.14 | 19000 | R-454B
215934750 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X42M21A*+WALLCON | *96CTN0601714B* | 34000 | 20.5 | 11 | 8.1 | 38000 | 27000 | 71.05% | 1.95 | 30400 | R-454B
213238569 | 3.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9E080C20MP12 | 43000 | 16 | 11.5 | 8.2 | 44500 | 31600 | 71.01% | 3.07 | 30800 | R-410A
215213867 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,G,JG88960+AEFE5* |  | 51500 | 17 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
216800669 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | A36VDA*+TXV | BGH96M080B3C | 24000 | 18 | 12 | 9 | 22400 | 16800 | 75% | 1.9 | 19000 | R-454B
216800670 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V36H175P15*+TXV | BGH96M080B3C | 24000 | 18 | 12 | 9 | 22400 | 16800 | 75% | 1.9 | 19000 | R-454B
213752249 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*B090M21**20 | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213752283 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*B070V14**12 | 23800 | 16.5 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.87 | 20000 | R-410A
213752332 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*B090V21**20 | 23800 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213752350 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2E040M17**12 | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
215676665 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN1202422B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
214861582 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN10-M1 | MVBC-24HWFN10-MB1-D |  | 24000 | 19.7 | 11.7 | 9 | 25000 | 18000 | 72% | 2.2 | 17600 | R-454B
216774291 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG8J*36+TXV+AEFE3A* |  | 23600 | 20 | 12.5 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
213753676 | 2.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M21**16 | 34800 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.52 | 29400 | R-410A
213753712 | 2.88 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58TP*B045V14**12 | 34600 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.64 | 29400 | R-410A
213771545 | 2.03 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4321AL*+UI | 59TN6C100C21**22 | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
214861531 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-48HFN10-M2X | MVBC-48HWFN10-MD2 |  | 48000 | 17 | 10.1 | 10.2 | 50000 | 46000 | 92% | 2 | 40000 | R-454B
213613361 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24D4 |  | 23800 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213281365 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H***P429+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
212623989 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9Y080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
213493976 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES120C16SMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
216800671 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG35*36+TXV | BGH96M080B3C | 24000 | 18 | 12 | 9 | 22400 | 16800 | 75% | 1.9 | 19000 | R-454B
215438137 | 1.88 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*E31*24+TXV |  | 22600 | 15.2 | 11.7 | 8.65 | 22200 | 16400 | 73.87% | 1.84 | 18400 | R-454B
212361453 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M080B3A | 41000 | 16 | 11 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
212361589 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34000 | R-410A
215588079 | 3.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**4821AM*+UI | 59CU5B060C17**16 | 47000 | 17.5 | 11 | 10.5 | 51500 | 50500 | 98.06% | 2.04 | 49500 | R-454B
215588097 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6024AM*+UI | 58TN*B135C24**22 | 49500 | 19.5 | 11.5 | 10.5 | 52000 | 53000 | 101.9% | 1.98 | 50500 | R-454B
215412962 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V,R36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213386476 | 2.92 | Yes | No | MDV | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | MOX630-36HFN1-M3X | MAC-36HWDN1-MN0 |  | 35000 | 15.2 | 10 | 8.5 | 36000 | 30000 | 83.33% | 1.8 | 27000 | R-410A
214312432 | 2.47 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG36936+TD |  | 29600 | 15.5 | 11.2 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
214442622 | 2.43 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RE9J936+TD |  | 29200 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
216054949 | 1.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ES100B12SMPS1 | 19500 | 18 | 11 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
216800667 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V36H175P15*+TXV | BGH96M060B3C | 24000 | 18 | 12 | 9 | 22400 | 16800 | 75% | 1.9 | 19000 | R-454B
215438138 | 1.92 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*G32*25+TXV |  | 23000 | 15.2 | 11.7 | 8.8 | 22400 | 16400 | 73.21% | 1.86 | 18400 | R-454B
215438140 | 2.58 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*G34*36+TXV |  | 31000 | 15.2 | 10.5 | 9 | 32600 | 23600 | 72.39% | 1.85 | 23600 | R-454B
213362052 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG35948 | BGH96M080C4B | 41000 | 16 | 11 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213184848 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
215399920 | 2.55 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR |  | 30600 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.56 | 27000 | R-454B
213752162 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M14**12 | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213752260 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*B110M21**20 | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213752346 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*B110V21**22 | 23800 | 16 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213752410 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2E080M21**20 | 23800 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213752446 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC6A040M17**12 | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213752564 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6C040V14**10 | 23000 | 15.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213752569 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C040V17**12 | 23400 | 15.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.82 | 19900 | R-410A
213752625 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6C100V21**22 | 23800 | 16.5 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
216774289 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG8J*36+TXV+AEFE4B* |  | 23600 | 20 | 12.5 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
216679963 | 2.95 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4221AL* | 927TA48080V17*** | 35400 | 15.2 | 10 | 8.5 | 39000 | 34800 | 89.23% | 1.75 | 29400 | R-410A
212927496 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CE2505C+TXV |  | 23200 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213281148 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213145611 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | PL36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214861614 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBDM-48HWFN10-WC3-D |  | 48000 | 17.5 | 12 | 9.5 | 48000 | 48000 | 100% | 2 | 34000 | R-454B
215676855 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *80CSU1002120A* | 48500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
215676805 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN0801714B* | 48000 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 1.98 | 47500 | R-454B
213238558 | 3.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM8Y100C16MP11 | 44000 | 16.2 | 11 | 8.1 | 44500 | 31600 | 71.01% | 3.18 | 30800 | R-410A
213238573 | 3.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48B44+TDR | TM9E100C20MP12 | 43000 | 16 | 11.5 | 8.2 | 44500 | 31600 | 71.01% | 3.07 | 30800 | R-410A
213184845 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,GE35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
215679295 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *80CSU0601716B* | 34600 | 17.5 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
212361484 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M100D5B | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212380763 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG86960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380904 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG86960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213612278 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,T60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
214861577 | 4.5 | Yes | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M2X | MVBC-60HWFN10-MD2-D |  | 54000 | 15.2 | 10 | 9.2 | 59000 | 53000 | 89.83% | 2 | 41000 | R-454B
213206180 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6B080V17**16 | 23800 | 16 | 9 | 8.1 | 25400 | 22600 | 88.98% | 2.92 | 20200 | R-410A
213753730 | 2.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58TP*B090V17**16 | 34800 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.67 | 29200 | R-410A
213753743 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58TP*B135V24**22 | 35200 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
213752156 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*B045M14**12 | 23400 | 16.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213752207 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M21**16 | 23600 | 16.5 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213752222 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*B090M17**14 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752326 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*B090V21**20 | 23400 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213752341 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*B110V21**22 | 23800 | 16 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
212380894 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P179 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380896 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P199 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381053 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213281314 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213281446 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V60H210P299+AEFE5* |  | 45500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
215431131 | 1.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG8J936+AEFE3A* |  | 21600 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
215383031 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG74960+TD |  | 41000 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
212361438 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M100D5B | 45000 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212361456 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M080B3A | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
212361471 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M100C5A | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212361487 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M120D5A | 45000 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361588 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M100C5B | 44000 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34000 | R-410A
213752329 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*B090V21**20 | 23400 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213752338 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*B110V21**22 | 23800 | 16 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213752363 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2E040M17**12 | 23400 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
213752413 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2E080M21**20 | 23600 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
213752454 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC6A040M17**12 | 23400 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213753658 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B070M17**12 | 33800 | 16.5 | 9.9 | 8.1 | 37800 | 31800 | 84.13% | 2.73 | 29000 | R-410A
213753681 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M21**20 | 35200 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
213752612 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6C100V21**20 | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213752628 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6C100V21**22 | 23800 | 16.5 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
214771865 | 2.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RE34936+TD |  | 29000 | 15.2 | 11 | 9.35 | 28400 | 23800 | 83.8% | 2.06 | 22000 | R-410A
215383032 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG86948+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215405106 | 1.92 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436AA* | HG7J924+AEFE3A* |  | 23000 | 20 | 12.5 | 9.25 | 22400 | 19200 | 85.71% | 2.06 | 21400 | R-410A
213184841 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,G48H175D149+AEFE4B* |  | 44000 | 17 | 11 | 8.9 | 45500 | 33200 | 72.97% | 1.9 | 39000 | R-410A
212361483 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M100D5B | 45000 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
213206008 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2D060E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.87 | 20400 | R-410A
214802103 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG8J936+AEFE4B* |  | 23600 | 20 | 12.7 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216035498 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | AE*S+CM48A3J+TDR |  | 31600 | 19 | 11.7 | 9 | 31800 | 30200 | 94.97% | 2.66 | 26200 | R-454B
216035533 | 2.6 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)48B3K+TDR |  | 31200 | 15.2 | 10 | 8.5 | 31000 | 31600 | 101.9% | 2.53 | 27000 | R-454B
215933970 | 2.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | FCMA5B60L0D*+WALLCON |  | 35000 | 22 | 13 | 9.5 | 33400 | 25200 | 75.45% | 2.08 | 29200 | R-454B
213184786 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,G60H210D169+AEFE5* |  | 45000 | 18 | 11.5 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-410A
213146781 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213238584 | 3.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM9V100C20MP12 | 44000 | 16.2 | 11 | 8.4 | 44500 | 31200 | 70.11% | 3.22 | 30600 | R-410A
213828550 | 2.47 | Yes | No | HISENSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUWR-36U3SA | D(A,C,E)31E34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215382878 | 1.61 | No | No | AMERISTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | E4HL5018A1000A | F,PE*E32924 |  | 19300 | 15.2 | 9.5 | 8.25 | 18300 | 17600 | 96.17% | 1.86 | 14000 | R-410A
213752358 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2E040M17**12 | 23600 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.84 | 20000 | R-410A
215382877 | 4 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | F,PE*TT7960 |  | 48000 | 17 | 10 | 8.45 | 45000 | 32600 | 72.44% | 1.9 | 30000 | R-410A
215383027 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG53948+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215383028 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG49948+TD |  | 41000 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
216800660 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | A60VGA*+TXV | BGH96M080C4C | 42500 | 16 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.8 | 34000 | R-454B
213753159 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 58S(B,C)*B090M21**16 | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213752479 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC6A080M21**20 | 23600 | 16 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213752536 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SP6A080V17**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213752588 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C080V17**16 | 23400 | 16 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.84 | 19800 | R-410A
213752606 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6C080V21**20 | 23800 | 16 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213752620 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C100V21**22 | 23800 | 16.5 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
216800800 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG37*48+TXV | BGH96M080C4C | 42000 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.8 | 34000 | R-454B
213753096 | 2.42 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M14**12 | 29000 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
213753162 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M21**16 | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213187955 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | V,T36H210P479+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
213753389 | 2.42 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)42B34+TDR | 59SC2E080M21**20 | 29000 | 15.4 | 8.8 | 8.3 | 33200 | 24000 | 72.29% | 2.76 | 23200 | R-410A
215412954 | 3.92 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG84948+AEFE5* |  | 47000 | 17 | 9.5 | 8.4 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
215383029 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG49960+TD |  | 41000 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
216678762 | 2.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CSPH*4212AL* | 59TP7A060V17**16 | 35800 | 15.2 | 9.8 | 8.5 | 38500 | 34600 | 89.87% | 1.82 | 29200 | R-410A
213146782 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213146783 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
213613362 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24E4 |  | 23200 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213771645 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4821AL*+UI | 59TN6C060C17**14 | 24000 | 16.5 | 10.5 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
213281325 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P299+AEFE5* |  | 45500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
214312436 | 2.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG81936+TD |  | 30000 | 15.5 | 11.3 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
215588147 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*4812AM*+UI | 59MN7C080C21**20 | 48500 | 18 | 10.5 | 10.5 | 52500 | 52000 | 99.05% | 1.94 | 50500 | R-454B
215588163 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 58TN*B090C17**16 | 48500 | 18.5 | 12 | 9.5 | 51000 | 50000 | 98.04% | 1.98 | 49000 | R-454B
215588263 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6024XMA*+UI | 59TN6C100C21**22 | 52000 | 19 | 11.5 | 8.1 | 53000 | 46500 | 87.74% | 1.85 | 48000 | R-454B
215588331 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 59TN6C100C21**22 | 52000 | 19 | 11.5 | 8.1 | 52500 | 46500 | 88.57% | 1.85 | 48000 | R-454B
215308395 | 2 | Yes | No | AMERISTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | E4HL5036A1000A | F,PE*G32925 |  | 24000 | 15.2 | 11 | 8.5 | 22400 | 17600 | 78.57% | 1.9 | 18100 | R-410A
213206120 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC5B080E21**20 | 23800 | 15.5 | 9 | 8.5 | 26000 | 22600 | 86.92% | 2.88 | 20400 | R-410A
215431170 | 3.92 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG84960+AEFE5* |  | 47000 | 17 | 9.5 | 8.4 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
215405107 | 3.71 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-4860AA* | HG49960+AEFE5* |  | 44500 | 18 | 11.7 | 9.45 | 46000 | 34000 | 73.91% | 2.1 | 39000 | R-410A
212927495 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CE3005C+TXV |  | 23200 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
212624150 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624182 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9Y100C20MP11 | 32400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624184 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM9Y100C20MP11 | 32800 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624231 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLE040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
213281366 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H175P789+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213281149 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216619285 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG48960+AEFE5* |  | 46000 | 17 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
214312438 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG51948+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214312429 | 2.45 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG35936+TD |  | 29400 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
214776253 | 2.85 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436A | HG82936+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 34400 | 24800 | 72.09% | 2 | 27000 | R-410A
213187958 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | H,TG80936+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
213752299 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*B070V17**16 | 23400 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.9 | 20000 | R-410A
213752383 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2E060M17**14 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752398 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2E080M17**16 | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.87 | 19800 | R-410A
213752401 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2E080M17**16 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.87 | 19800 | R-410A
213752434 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC6A026M14**10 | 23400 | 15.5 | 9 | 8.1 | 25200 | 22600 | 89.68% | 2.86 | 20200 | R-410A
213752451 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC6A040M17**12 | 23600 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
213752467 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC6A080M17**16 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.88 | 20200 | R-410A
213752549 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SP6A100V21**20 | 23600 | 16 | 9 | 8.1 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
212380742 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P159 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213753687 | 2.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M24**20 | 34800 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213753869 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59TP6C100V21**20 | 35200 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.61 | 29400 | R-410A
213281326 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL48H175P159+AEFE4B* |  | 44500 | 18 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
214242776 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CNPV*3621AL*+UI | 88*TB60110C21*** | 23600 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
212361461 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M080C4A | 41000 | 16 | 11 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361597 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M120D5B | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34000 | R-410A
214779003 | 4.46 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-4860A | HG52960+AEFE5* |  | 53500 | 18 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 1.9 | 42500 | R-410A
212381094 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG2K948 | BGH96M100C5A | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213184857 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG48948+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213752202 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M17**16 | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213752213 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M21**16 | 23800 | 16.5 | 9.5 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213752318 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*B090V17**16 | 23400 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.87 | 20000 | R-410A
211708438 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM8E120C16MP11 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
215850334 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E120C16MP11 | 30600 | 18 | 11 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
215850383 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y100C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
215850448 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
213752343 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*B110V21**22 | 23800 | 16 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213752472 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC6A080M17**16 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.88 | 20200 | R-410A
213752477 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC6A080M21**20 | 23600 | 16 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213752513 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SP6A060V14**12 | 23200 | 16 | 9.4 | 8.1 | 24400 | 22000 | 90.16% | 2.87 | 19600 | R-410A
212985802 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96MSN0261410A* | 23400 | 16.5 | 10 | 8.5 | 26200 | 24400 | 93.13% | 2.02 | 19100 | R-410A
214312431 | 2.47 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H210P169+TD |  | 29600 | 15.5 | 11.2 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
213753154 | 2.42 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B090M21**16 | 29000 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
212367420 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84948 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
214862794 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84(1,2)60+TXV | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
214312416 | 2.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H175P149+TD |  | 29000 | 15.2 | 11 | 9.35 | 28400 | 23800 | 83.8% | 2.06 | 22000 | R-410A
214312417 | 2.45 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H175P159+TD |  | 29400 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
214312418 | 2.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG34936+TD |  | 29000 | 15.2 | 11 | 9.35 | 28400 | 23800 | 83.8% | 2.06 | 22000 | R-410A
214312419 | 2.48 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG37936+TD |  | 29800 | 15.5 | 11.3 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
215389768 | 2.57 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-2436A | HG35936+TD |  | 30800 | 15.2 | 10.5 | 8.8 | 32000 | 23200 | 72.5% | 1.9 | 24600 | R-410A
214239803 | 2.65 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CNPV*4221AL*+UI | 59MN7C100C21**22 | 31800 | 16.5 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.88 | 31200 | R-410A
215389769 | 2.52 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-2436A | M36E589+TD |  | 30200 | 15.2 | 10.5 | 8.75 | 32000 | 23200 | 72.5% | 1.9 | 23200 | R-410A
213187951 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | PL36H175P789+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
213187952 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | V,T36H175P789+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
213187953 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | V,T36H***P229+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
215678045 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU1002120A* | 55500 | 17 | 8.5 | 8.5 | 60000 | 42000 | 70% | 1.9 | 51500 | R-454B
214312441 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | V,R60H245P799+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214312442 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG52948+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215383026 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG55960+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215383025 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG55948+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
212623760 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623826 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | CP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623835 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | CP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623842 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | CP9C060B12MP13 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623860 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623862 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM9V060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623869 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM9V060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623871 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9V060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
213088240 | 1.97 | Yes | Yes | ARCOAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32924+AEFE3A* |  | 23600 | 17 | 10 | 9 | 25600 | 25200 | 98.44% | 2.14 | 18600 | R-410A
215412953 | 3.92 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG50960+AEFE5* |  | 47000 | 17 | 9.5 | 8.35 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
215412955 | 3.92 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG84948+AEFE4B* |  | 47000 | 17 | 9.5 | 8.4 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
214312421 | 2.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG80936+TD |  | 30000 | 15.5 | 11.3 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
214312428 | 2.48 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H175P789+TD |  | 29800 | 15.5 | 11.3 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
215942432 | 2.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL0702120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215942382 | 2.93 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
216732369 | 4.33 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | PL60H210P19*+TXV+AEFE5* |  | 52000 | 18 | 11.7 | 9.4 | 53000 | 38000 | 71.7% | 2 | 42000 | R-454B
216760256 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,RG48*48+TXV+AEFE4B* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
215308397 | 2 | Yes | No | AMERISTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | E4HL5036A1000A | F,PE*G33925 |  | 24000 | 15.2 | 11 | 8.5 | 22400 | 17600 | 78.57% | 1.9 | 18100 | R-410A
214776254 | 2.85 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436A | HG82936+AEFE3A* |  | 34200 | 19 | 12 | 9.5 | 34400 | 24800 | 72.09% | 2 | 27000 | R-410A
216788569 | 4.04 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,RG84*48+TXV+AEFE4B* |  | 48500 | 19 | 12 | 10 | 46500 | 48000 | 103.2% | 2.1 | 47500 | R-454B
216760241 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,GE48*60+TXV+AEFE5* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
216761996 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HE35*48+TXV+AEFE4B* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
214779004 | 4.42 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-4860A | HG88960+AEFE5* |  | 53000 | 18 | 11.5 | 9.5 | 53000 | 38000 | 71.7% | 1.9 | 42500 | R-410A
213187959 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | H,TG81936+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
215933620 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU0802120B* | 33600 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215933670 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0802120B* | 33800 | 19.5 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30400 | R-454B
212623885 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
213184799 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213281445 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
215387294 | 1.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*G33925 |  | 21600 | 16 | 10 | 8.85 | 21400 | 16500 | 77.1% | 2.02 | 15000 | R-410A
215677355 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0902120B* | 57000 | 18.5 | 9.5 | 9 | 63500 | 44500 | 70.08% | 2.08 | 55500 | R-454B
213205822 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A045E17**12 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.86 | 20200 | R-410A
213205829 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*A070E14**12 | 23800 | 16 | 9.5 | 8.1 | 25600 | 22400 | 87.5% | 2.94 | 20200 | R-410A
215213869 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,YG9J936+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215431161 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | V,R48H175P389+AEFE4B* |  | 46000 | 16 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
214810870 | 2.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,GG34936+TD |  | 29000 | 15.2 | 11 | 9.35 | 28400 | 23800 | 83.8% | 2.06 | 22000 | R-410A
215431163 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | PL60H210P179+AEFE5* |  | 46000 | 17 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
213270508 | 2 | Yes | No | AMERISTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | E4HL5030A1000A | CE3005C+TXV |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
215850528 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLV100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215850546 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216800655 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V60H210P19*+TXV | BGH96M080C4C | 43500 | 16 | 11.7 | 9.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
214521991 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z9ES100C20SMPS1 | 32200 | 17.5 | 9.4 | 8.4 | 33400 | 27600 | 82.63% | 2.67 | 25400 | R-410A
213205897 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*A110E21**20 | 23800 | 15.5 | 9 | 8.5 | 26200 | 22800 | 87.02% | 2.86 | 20600 | R-410A
213205904 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*A110E21**20 | 23800 | 15.5 | 9 | 8.5 | 26200 | 22800 | 87.02% | 2.85 | 20600 | R-410A
213206099 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC5B060E17**14 | 23200 | 15.2 | 9.2 | 8.3 | 25200 | 22600 | 89.68% | 2.89 | 20200 | R-410A
213206199 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59TP6B080V21**20 | 23800 | 16 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.96 | 19800 | R-410A
212361567 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31(1,2)30+TXV | BGH96M080B3B | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 18400 | R-410A
215677505 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN0602120B* | 55500 | 17.5 | 8.5 | 8.5 | 64000 | 45500 | 71.09% | 1.94 | 57000 | R-454B
215677805 | 4.54 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU0802120B* | 54500 | 18 | 8.5 | 8.5 | 59500 | 42000 | 70.59% | 1.9 | 51000 | R-454B
215412947 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG9J936+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
215431156 | 2.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,RG80936+AEFE3A* |  | 34000 | 17 | 10 | 9.5 | 33400 | 25600 | 76.65% | 2.05 | 23000 | R-410A
216618740 | 2.78 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,GE8J936+AEFE4B* |  | 33400 | 18 | 10 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
213753600 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 59TP6C080V21**20 | 29400 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.8 | 23200 | R-410A
216800659 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG84*60+TXV | BGH96M100C5C | 51500 | 18 | 11.7 | 9.5 | 53000 | 47500 | 89.62% | 1.94 | 51000 | R-454B
213145623 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | PL36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
211756120 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | YPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
212628094 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | CP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
215389777 | 2.9 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L17A* | *96VTN0601716B* | 34800 | 15.2 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.8 | 29600 | R-410A
215431123 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | V,R36H175P149+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.04 | 15000 | R-410A
212628095 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CP9C100C20MP13 | 33400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627961 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8Y100C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212361474 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M100C5B | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212361476 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212361460 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
216800656 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG84*60+TXV | BGH96M080C4C | 43500 | 16 | 11.7 | 9.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
216800658 | 4.33 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V60H210P19*+TXV | BGH96M100C5C | 52000 | 18 | 11.7 | 9.5 | 53000 | 47500 | 89.62% | 1.94 | 51000 | R-454B
216800799 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V48H210P19*+TXV | BGH96M080C4C | 43500 | 16 | 11.7 | 9.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
214861585 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBC-18HWFN10-MB3E-D |  | 18000 | 19 | 12.5 | 9.7 | 19000 | 18000 | 94.74% | 2 | 15000 | R-454B
215412961 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V,R36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215412936 | 2.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H***P219+TD |  | 29000 | 15.2 | 11 | 9.35 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
216017478 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG48948+AEFE4B* |  | 46000 | 16 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
215412956 | 4 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG88960+AEFE5* |  | 48000 | 17 | 10 | 8.5 | 45000 | 32600 | 72.44% | 1.9 | 30000 | R-410A
215419938 | 3.38 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,GG48960+TD |  | 40500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
212627975 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8Y100C16MP11 | 31000 | 18.2 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628008 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TP9C100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628010 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628027 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TL9E100C20UH11 | 32800 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
215413744 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212628042 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8Y120C20MP11 | 33000 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628043 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
215933890 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0802120B* | 34200 | 19.5 | 11.7 | 9 | 34400 | 26000 | 75.58% | 1.94 | 30000 | R-454B
215412971 | 1.77 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG32924+AEFE3A* |  | 21200 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
215679365 | 2.77 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0601716B* | 33200 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.84 | 31000 | R-454B
213752449 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC6A040M17**12 | 23200 | 15.2 | 9 | 8.1 | 24800 | 22600 | 91.13% | 2.85 | 20000 | R-410A
214777843 | 3.96 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | F,PE*CC4960 |  | 47500 | 17 | 10 | 8.4 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
215382916 | 3.38 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG48948+TD |  | 40500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215382917 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG54948+TD |  | 41000 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
216679522 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *97VTN0601716A* | 23600 | 16.5 | 10 | 9 | 25800 | 23600 | 91.47% | 1.76 | 18900 | R-410A
214312434 | 2.43 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG9J936+TD |  | 29200 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
216699791 | 2 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH9VSA241CA* | CAHEA3630C3A*+MBVK16CH*X00A* |  | 24000 | 21 | 12.2 | 10 | 24000 | 24000 | 100% | 2.4 | 24000 | R-32
212361465 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M080C4B | 41000 | 16 | 11 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
215932360 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *96CTN1002122B* | 32800 | 20 | 11.5 | 9.5 | 34800 | 26600 | 76.44% | 2 | 30600 | R-454B
215431145 | 2.78 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | PL36H175P149+AEFE4B* |  | 33400 | 18 | 10 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
214312440 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | V,R48H210P199+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214931584 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG54960+TD |  | 41000 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
216618340 | 1.82 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG8J*36+TXV+AEFE4B* |  | 21800 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
216019493 | 1.77 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*G32924 |  | 21200 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
215382876 | 3.79 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | F,PE*CC6960 |  | 45500 | 17 | 9.5 | 8.2 | 45000 | 32600 | 72.44% | 1.84 | 30000 | R-410A
214312425 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG88948+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
212628059 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TL8E100C20UH11 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628076 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628077 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628078 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | CP9C100C20MP13 | 29600 | 16.9 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628093 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627943 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
216800798 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG37*48+TXV | BGH96M080C4C | 43000 | 16 | 11.5 | 9.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
216619284 | 2.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,RG37936+AEFE4B* |  | 34000 | 18 | 10 | 9.5 | 33400 | 25600 | 76.65% | 2.05 | 23000 | R-410A
215431153 | 2.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | V,R36H***P449+AEFE3A* |  | 33600 | 17 | 10 | 9.45 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
214312439 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG51960+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
216051830 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*TT3931 |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
214312437 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG50948+TD |  | 41500 | 15.5 | 11.3 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214567069 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RE84948+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215407207 | 1.78 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | CE3005A+TXV |  | 21400 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
214243171 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EN(A,D,W)4X48L21**+WALLCON | *96CTN0601714B* | 24000 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20600 | R-410A
214861581 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M1 | MVBC-18HWFN10-MB1-D |  | 18000 | 18.5 | 12.1 | 9.8 | 18000 | 13000 | 72.22% | 2.3 | 13200 | R-454B
214771633 | 1.92 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436A | HG7J924+AEFE3A* |  | 23000 | 20 | 12.5 | 9.25 | 22400 | 19200 | 85.71% | 2.06 | 21400 | R-410A
214861548 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBDM-48HWFN10-WC3 |  | 48000 | 17.5 | 12 | 9.5 | 48000 | 48000 | 100% | 2 | 34000 | R-454B
214779005 | 4.46 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-4860AA* | HG52960+AEFE5* |  | 53500 | 18 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 1.9 | 42500 | R-410A
216788578 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | H,RG34*36+TXV+AEFE4B* |  | 23800 | 20 | 13 | 9.45 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
214312424 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG52960+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214312426 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG88960+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214295812 | 2.7 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | F,PE*G32936 |  | 32400 | 18 | 11 | 9.05 | 32200 | 23600 | 73.29% | 1.82 | 27000 | R-410A
214295814 | 2.7 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*G32936 |  | 32400 | 18 | 11 | 9.05 | 32200 | 23600 | 73.29% | 1.82 | 27000 | R-410A
215431150 | 2.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | V,R36H175P159+AEFE4B* |  | 34000 | 18 | 10 | 9.45 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
215412948 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG9J936+AEFE3A* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
215389835 | 1.93 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-2436A | PL36H***P449+TD |  | 23200 | 15.2 | 11.7 | 8.8 | 21400 | 18200 | 85.05% | 1.9 | 20000 | R-410A
216767043 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X1B080D4PSB | 31600 | 15.2 | 11.2 | 8.7 | 31800 | 23800 | 74.84% | 2.13 | 21000 | R-454B
215565251 | 2.63 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)49B3J+TDR |  | 31600 | 15.2 | 10 | 8.5 | 31000 | 31600 | 101.9% | 2.56 | 27000 | R-454B
214777842 | 2.77 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | F,PE*E34936 |  | 33200 | 17 | 9.5 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
215431148 | 2.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | PL36H175P159+AEFE4B* |  | 34000 | 18 | 10 | 9.45 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
216800654 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | A60VGA*+TXV | BGH96M080C4C | 43500 | 16 | 11.7 | 9.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
216093482 | 4.04 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | FE*TT4*60+TXV |  | 48500 | 19 | 12 | 10 | 46500 | 48000 | 103.2% | 2.1 | 47500 | R-454B
214238984 | 2.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CNPV*4217AL*+UI | 88*TB48090C17*** | 32000 | 17 | 11.5 | 8.1 | 33000 | 24600 | 74.55% | 1.9 | 31400 | R-410A
215387295 | 3.79 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | F,PE*TT6960 |  | 45500 | 17 | 9.5 | 8.2 | 45000 | 32600 | 72.44% | 1.84 | 30000 | R-410A
216800802 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG37*48+TXV | BGH96M080C4C | 42500 | 16 | 10 | 8.5 | 43000 | 31200 | 72.56% | 1.85 | 32000 | R-454B
216981047 | 3.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG84*60+TXV | TM9V100C16MP12 | 43500 | 18 | 11.7 | 9 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
214312423 | 3.5 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | V,R60H210P199+TD |  | 42000 | 15.5 | 11.4 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215383030 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG74948+TD |  | 41000 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
216619286 | 3.96 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,RG86960+AEFE5* |  | 47500 | 17 | 10 | 8.45 | 45000 | 32600 | 72.44% | 1.9 | 30000 | R-410A
215407205 | 1.75 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | CE2403C+TXV |  | 21000 | 16 | 9.5 | 8.7 | 21400 | 16500 | 77.1% | 1.98 | 15000 | R-410A
215851307 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215711557 | 3.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | BV**C4*48+TXV |  | 46000 | 19 | 12 | 9 | 44000 | 33600 | 76.36% | 2.1 | 34600 | R-454B
215727924 | 4.38 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36(1,2)60+TXV | TM8E130D20MP11 | 52500 | 18 | 10.5 | 8.3 | 53000 | 39500 | 74.53% | 1.96 | 37000 | R-454B
215677225 | 4.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL0702120B* | 57000 | 18.5 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56500 | R-454B
215431166 | 3.96 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | PL60H210P199+AEFE5* |  | 47500 | 17 | 10 | 8.45 | 45000 | 32600 | 72.44% | 1.9 | 30000 | R-410A
215387296 | 3.88 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | F,PE*TT9960 |  | 46500 | 17 | 9.5 | 8.35 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
216800200 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,YG9J936+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
203449864 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CP3005A+TXV+TD |  | 22800 | 17 | 12 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
215431151 | 2.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | PL36H***P449+AEFE3A* |  | 33600 | 17 | 10 | 9.45 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
211782038 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE22936 | *92ESN0601714A* | 23000 | 16 | 9.5 | 8.5 | 25200 | 23000 | 91.27% | 1.94 | 18400 | R-410A
215412963 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V,R36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
203449870 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CE3005A+TXV |  | 23200 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
216618735 | 1.77 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | V,G36H***D129+AEFE3A* |  | 21200 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
215387293 | 1.78 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*G32925 |  | 21400 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
213258291 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31930 | *96VSN0401410A* | 23000 | 15.2 | 9.5 | 8.5 | 25000 | 23600 | 94.4% | 1.96 | 18500 | R-410A
213258293 | 1.88 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32936 | *96VSN0401410A* | 22600 | 16 | 9.5 | 8.5 | 24200 | 23800 | 98.35% | 2.02 | 18000 | R-410A
213258325 | 1.93 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE30924 | *96VSN0601714A* | 23200 | 16 | 9.5 | 8.5 | 25200 | 23600 | 93.65% | 1.98 | 18500 | R-410A
203449868 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CE2403C+TXV |  | 22800 | 19 | 12 | 9.2 | 22200 | 17200 | 77.48% | 1.94 | 21400 | R-410A
216618341 | 1.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG8J*36+TXV+AEFE3A* |  | 21600 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
215412964 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG8J936+AEFE4B* |  | 23600 | 20 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215413746 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213753689 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B090M24**20 | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
216992525 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | H,PG48*60+TXV | 88*TB48090C17*** | 44000 | 20 | 11.5 | 9 | 47000 | 35400 | 75.32% | 1.86 | 37400 | R-454B
215431147 | 2.78 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | V,R36H175P149+AEFE4B* |  | 33400 | 18 | 10 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
215932660 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712A* | 34400 | 20.5 | 11.7 | 9 | 34600 | 26200 | 75.72% | 1.94 | 30200 | R-454B
215932760 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0802120B* | 34400 | 20 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.96 | 30000 | R-454B
215677695 | 4.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN0802120B* | 57500 | 18.5 | 9 | 9 | 64000 | 45000 | 70.31% | 2.06 | 56500 | R-454B
215677345 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0702120B* | 56500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.06 | 56500 | R-454B
215677395 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0602120B* | 55500 | 17.5 | 8.5 | 8.5 | 64000 | 46000 | 71.88% | 1.94 | 57000 | R-454B
215677045 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN0602120B* | 55500 | 17.5 | 8.5 | 8.5 | 65000 | 46000 | 70.77% | 1.94 | 57000 | R-454B
214803070 | 3.88 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | BV**C4948 |  | 46500 | 16 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
215431158 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | A48VGA+TXV+AEFE5* |  | 46000 | 17 | 9.5 | 8.25 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
216581445 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | CAP**6024AL*+UI | 987TA66100C21*** | 44500 | 21 | 11 | 9 | 45500 | 35800 | 78.68% | 2 | 43000 | R-410A
215405105 | 1.93 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436AA* | HG7J924+AEFE4B* |  | 23200 | 20 | 12.5 | 9.25 | 22400 | 19200 | 85.71% | 2.06 | 21400 | R-410A
215431126 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | V,R36H175P159+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
213753379 | 2.35 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30B34+TDR | 59SC2E080M21**20 | 28200 | 15.2 | 8.7 | 8.3 | 33200 | 24000 | 72.29% | 2.76 | 23200 | R-410A
213281368 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215727951 | 4.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48(1,2)60+TXV | TM9E120D20MP12 | 53000 | 18 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36800 | R-454B
215727969 | 3.71 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48(1,2)60+TXV | Z8ES080C16SMPS1 | 44500 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
215727983 | 3.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48(1,2)60+TXV | Z9ES080C16SMPS1 | 45000 | 18 | 11.7 | 8.5 | 45000 | 33400 | 74.22% | 2 | 32200 | R-454B
215728019 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE7J(1,2)36+TXV | TM9V080B12MP12 | 22400 | 17 | 11.5 | 8.8 | 21400 | 17300 | 80.84% | 1.96 | 17100 | R-454B
215728028 | 1.82 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE31(1,2)30+TXV | Z8ES080B12SMPS1 | 21800 | 18 | 11 | 8.95 | 21200 | 17500 | 82.55% | 1.9 | 17200 | R-454B
209880025 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF98MV306017UPS*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
216030933 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBDM-24HWFN10-WA3-MAS |  | 24000 | 18.6 | 12 | 10 | 24000 | 20600 | 85.83% | 2.14 | 19000 | R-454B
213258950 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VTN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 24200 | 97.58% | 2.04 | 18300 | R-410A
215383024 | 3.38 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG72960+TD |  | 40500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
213752554 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SP6A100V21**20 | 23800 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
215935100 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0801714B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33400 | R-454B
216990367 | 4.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | A60VHA*+TXV | 88*TB60090C21*** | 56000 | 19 | 9 | 9 | 57500 | 41000 | 71.3% | 2.02 | 50000 | R-454B
213753715 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58TP*B045V14**12 | 35200 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.64 | 29400 | R-410A
213753758 | 2.82 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC2E080M17**16 | 33800 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.74 | 29000 | R-410A
215413740 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | A24VBA+TXV+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
215382879 | 2 | No | No | AMERISTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | E4HL5024A1000A | F,PE*G32925 |  | 24000 | 15.2 | 9 | 8.1 | 22400 | 17600 | 78.57% | 1.94 | 18100 | R-410A
215431121 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | PL36H175P149+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.04 | 15000 | R-410A
216800682 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V60H210P19*+TXV | BGH96M100C5C | 44500 | 16 | 10.5 | 8.5 | 45000 | 32600 | 72.44% | 1.85 | 33000 | R-454B
213214822 | 1.52 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430U-24HFN1-MR0 | MVC-18HWFN1-M |  | 18200 | 18.4 | 12.5 | 9.8 | 22200 | 16600 | 74.77% | 1.9 | 13600 | R-410A
211780574 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31930 | *92ESN0601714A* | 23800 | 16 | 10 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
212391591 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31(1,2)24+TXV | *92ESN0801716A* | 23800 | 17 | 10 | 8.5 | 25200 | 23400 | 92.86% | 1.96 | 18400 | R-410A
215565314 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TP9C080B12MP13 | 22200 | 17 | 12 | 9 | 23000 | 18300 | 79.57% | 2 | 18600 | R-454B
215934720 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X36M17A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
215934740 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X42M21A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27000 | 71.05% | 2 | 30600 | R-454B
215934770 | 2.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X43M21A*+WALLCON | *96CTN0601714B* | 34600 | 20.5 | 11.5 | 8.5 | 38000 | 27600 | 72.63% | 2.06 | 31200 | R-454B
215934820 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CTL0701716B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33000 | R-454B
215852714 | 2.77 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,GE8J936+AEFE3A* |  | 33200 | 17 | 9.5 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
215382874 | 2.77 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | F,PE*G34936 |  | 33200 | 17 | 9.5 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
214242628 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EN(A,D)4X30L17**+WALLCON | *96CTN0801714B* | 23400 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
215850130 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215281575 | 2.7 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | SM6937 |  | 32400 | 17 | 10 | 9.35 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
216618739 | 2.78 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | V,G36H175D149+AEFE4B* |  | 33400 | 18 | 10 | 9.3 | 33400 | 25600 | 76.65% | 2.02 | 23000 | R-410A
214826157 | 2 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | V,Y36H***P21*+TXV+AEFE3A* |  | 24000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
214242225 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CNPV*4821AL*+UI | 58TN*B090C17**16 | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
216619277 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | C60A***L16*+TXV | 59MN7C080C21**20 | 43500 | 21 | 11.7 | 9 | 44500 | 36000 | 80.9% | 2.26 | 42500 | R-410A
215224762 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG48960 | 59MN7C060C21**20 | 44000 | 20 | 11.5 | 9 | 44500 | 36400 | 81.8% | 2.22 | 43000 | R-410A
214271745 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | C48A***L539 | 58TN*B070C17**16 | 45000 | 21 | 11 | 9.5 | 44500 | 36400 | 81.8% | 2.32 | 43000 | R-410A
214271850 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | PL36H175P149 | 58TN*B045C17**12 | 23600 | 16 | 10.5 | 8.1 | 20000 | 16300 | 81.5% | 1.94 | 19800 | R-410A
214271870 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | C36A***L159 | 58TN*B070C14**12 | 24000 | 17 | 10.5 | 8.1 | 19600 | 16200 | 82.65% | 2.02 | 19600 | R-410A
212623997 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM9Y080B12MP11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212623998 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM9Y080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624048 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TMLE080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624101 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9Y100C16MP11 | 32400 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.75 | 26000 | R-410A
212624117 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TPLC060A12MP13 | 31600 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624132 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | CP9C080B12MP13 | 31400 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624183 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9Y100C20MP11 | 32400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
216619282 | 1.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG33936+AEFE4B* |  | 21600 | 16 | 10 | 8.85 | 21400 | 16500 | 77.1% | 2.02 | 15000 | R-410A
214861596 | 4.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBC-60HWFN10-MD3E-D |  | 54000 | 16 | 10 | 9 | 56000 | 52000 | 92.86% | 1.8 | 45000 | R-454B
215438144 | 3.63 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | FE*TT7*60+TXV |  | 43500 | 15.2 | 11.7 | 8.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
215934840 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CTL0901716B* | 35600 | 22 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
215934890 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *95CSU1002122B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.02 | 32600 | R-454B
216992532 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | H,PG35*48+TXV | 986TD60080C21*** | 43500 | 20 | 10.5 | 9.5 | 46000 | 36200 | 78.7% | 2 | 38500 | R-454B
216992550 | 3.58 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | H,PG35*48+TXV | 987TA66120C24*** | 43000 | 21 | 10.5 | 9.35 | 46500 | 36200 | 77.85% | 1.98 | 38500 | R-454B
216764649 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C005AS3 | S8X2C080M5PTC | 33000 | 17.1 | 11.7 | 8.7 | 32800 | 24200 | 73.78% | 2.1 | 21600 | R-454B
216764699 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD09AS3 | S8X2C080M5PTC | 34200 | 17.1 | 12.5 | 9 | 32200 | 24000 | 74.53% | 2.1 | 21200 | R-454B
216035494 | 1.92 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AE*S+CM30A3J+TDR |  | 23000 | 19 | 12 | 9 | 22800 | 19900 | 87.28% | 2.67 | 17700 | R-454B
209880034 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF96TV510021M4S*A | 34200 | 18 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
214272322 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | V,C36H175P459 | 59MN7C080C17**14 | 32800 | 17 | 11 | 8.5 | 31400 | 25000 | 79.62% | 1.98 | 31000 | R-410A
214826091 | 3.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P19*+TXV+AEFE5* |  | 46000 | 19 | 12 | 9 | 44000 | 33600 | 76.36% | 2.1 | 34600 | R-454B
216488079 | 3.71 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | A60VGA*+TXV | Z8ES080C16SMPS1 | 44500 | 18 | 12 | 9 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
212603148 | 2.05 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H210P299 | *80VSL0701716A* | 24600 | 17 | 10.5 | 8.5 | 23800 | 20800 | 87.39% | 1.78 | 17600 | R-410A
212603150 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG33936 | *80VSL0701716A* | 23800 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
212603151 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P159 | *80VSL0701716A* | 24000 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
212603167 | 2.03 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG81936 | *80VTL0701716A* | 24400 | 17 | 10.5 | 8.5 | 24000 | 21200 | 88.33% | 1.8 | 17800 | R-410A
214242325 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CNPV*4824AL*+UI | 58TN*B090C21**20 | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
210868914 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF75214LT80X | 34200 | 20 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
215407209 | 1.78 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | CE3005C+TXV |  | 21400 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
215675745 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL1102120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
215389774 | 2.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3617AL* | 926TC48060V17*** | 34800 | 15.2 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.8 | 29600 | R-410A
213607315 | 4.5 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-24WADU | F,PE*UU1960 |  | 54000 | 15.4 | 10 | 9 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
215565329 | 3.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)61A3J+TDR | TL8E100C20UH11 | 42000 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
213753801 | 2.87 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC6A100M21**20 | 34400 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.74 | 29000 | R-410A
216990619 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | C48A***L15*+TXV | 88*TB48090C17*** | 43500 | 20 | 11 | 9 | 46500 | 35400 | 76.13% | 1.86 | 37000 | R-454B
216990628 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | A60VHA*+TXV | 88*TB60070C21*** | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216035142 | 1.87 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3J+TDR |  | 22400 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.7 | 18700 | R-454B
216990521 | 4 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | C60A***L16*+TXV | 88*TB60070C21*** | 48000 | 19 | 10.5 | 10.5 | 51000 | 53500 | 104.9% | 1.92 | 50000 | R-454B
216990546 | 4.13 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | C48A***L18*+TXV | 88*TB60110C21*** | 49500 | 19 | 11.5 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
212624200 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9Y100C16MP11 | 32400 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624216 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8E040A12MP11 | 32000 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624268 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624433 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624498 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624518 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | CPLC100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624532 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | CPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624582 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8V080C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214861588 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3X | MVBDM-24HWFN10-WA3-D |  | 24000 | 18.6 | 12 | 10 | 24000 | 20600 | 85.83% | 2.14 | 19000 | R-454B
216990576 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | V,C36H175P15*+TXV | 88*TB48070C17*** | 32600 | 19 | 11 | 9.5 | 33600 | 26600 | 79.17% | 2 | 30000 | R-454B
216990594 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | C36A***L53*+TXV | 88*TB48090C17*** | 33400 | 20 | 11.5 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
212391592 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31(1,2)30+TXV | *92ESN0801716A* | 23800 | 17 | 10 | 8.5 | 25200 | 23400 | 92.86% | 1.96 | 18400 | R-410A
212391624 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE22(1,2)24+TXV | *92ESN0601714A* | 23000 | 16 | 9.5 | 8.5 | 25200 | 23400 | 92.86% | 1.96 | 18400 | R-410A
213753358 | 2.43 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 59SC2E060M17**14 | 29200 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.77 | 23200 | R-410A
215933610 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU0601716B* | 33600 | 19 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 30800 | R-454B
216618738 | 2.7 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | V,G36H***D129+AEFE3A* |  | 32400 | 17 | 9.5 | 9.05 | 33000 | 25600 | 77.58% | 1.96 | 23000 | R-410A
216618736 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | V,G36H175D149+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.04 | 15000 | R-410A
215413748 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG8J936+AEFE3A* |  | 23400 | 19 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214861602 | 4.5 | No | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-60HFN10-M3 | MVBC-60HWFN10-MD3E-D |  | 54000 | 15.2 | 8.6 | 8.4 | 54000 | 38000 | 70.37% | 1.8 | 33000 | R-454B
212627944 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627958 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8Y100C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214861579 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-48HFN10-M2 | MVBC-48HWFN10-MD2-D |  | 48000 | 17.7 | 10 | 10 | 50000 | 35200 | 70.4% | 1.9 | 40000 | R-454B
215431143 | 2.82 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | A36VDA+TXV+AEFE4B* |  | 33800 | 18 | 10 | 9.4 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
215933050 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU1002120A* | 33200 | 18.5 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30800 | R-454B
215934800 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CSU1002120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 32800 | R-454B
215438163 | 4.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | FE*CC3*60+TXV |  | 53000 | 19 | 11.4 | 8.75 | 52000 | 38000 | 73.08% | 1.96 | 36200 | R-454B
216035492 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AE*S+CM24A3J+TDR |  | 22600 | 19 | 12 | 8.5 | 22800 | 20000 | 87.72% | 2.68 | 17800 | R-454B
215382918 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG84948+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214771859 | 3.5 | Yes | No | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-4860A | HG49960+AEFE5* |  | 42000 | 15.2 | 11.7 | 8.6 | 41000 | 32000 | 78.05% | 1.9 | 36000 | R-410A
215382919 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG86960+TD |  | 41500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215431168 | 3.96 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | V,R60H210P199+AEFE5* |  | 47500 | 17 | 10 | 8.45 | 45000 | 32600 | 72.44% | 1.9 | 30000 | R-410A
215382868 | 1.73 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*E31924 |  | 20800 | 16 | 9.5 | 8.6 | 21200 | 16500 | 77.83% | 1.96 | 15000 | R-410A
215382869 | 1.78 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*E32930 |  | 21400 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
216774363 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | PL48H175P38*+TXV+AEFE4B* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
213753707 | 2.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B155M24**20 | 35000 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213753748 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC2E060M14**12 | 35000 | 15.5 | 9 | 8.1 | 38500 | 32400 | 84.16% | 2.51 | 29600 | R-410A
213753809 | 2.88 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC6A120M24**22 | 34600 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
216488085 | 3.71 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | A60VGA*+TXV | Z8ES100C20SMPS1 | 44500 | 18 | 12 | 9 | 42500 | 33000 | 77.65% | 2 | 31800 | R-454B
215818599 | 4.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | BV**C6*60+TXV |  | 53000 | 18 | 11 | 8.85 | 52000 | 38000 | 73.08% | 1.98 | 36200 | R-454B
213753597 | 2.42 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 59TP6C080V21**20 | 29000 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.8 | 23200 | R-410A
213753617 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)42B34+TDR | 59TP6C100V21**20 | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
212624601 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624633 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8V100C16MP12 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624667 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TMLV100C16MP12 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624669 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TMLV100C16MP12 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624699 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624767 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624783 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624785 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TL8E080C16UH11 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624851 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TL9E080C16UH11 | 30800 | 17.3 | 9.2 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624866 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | CP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624884 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624885 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | CP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624902 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8Y080C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624933 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8Y080C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624966 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8Y100C16MP11 | 29200 | 17.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624986 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8Y100C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625020 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM8Y100C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625067 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM9V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625120 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625135 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TP9C100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625150 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TP9C100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625170 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625236 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TL8E100C20UH11 | 29600 | 16.9 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625251 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TL8E100C20UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625253 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TL8E100C20UH11 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625285 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TL8E100C20UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625337 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625401 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9V100C20MP12 | 32800 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625437 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625452 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625454 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625504 | 2.42 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM8V120C20MP12 | 29000 | 15.8 | 8.5 | 8.4 | 32000 | 27400 | 85.62% | 2.7 | 24800 | R-410A
213752167 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*B070M14**12 | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213752251 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*B090M21**20 | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
212625518 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TMLV120C20MP12 | 28600 | 15.6 | 8.4 | 8.1 | 32000 | 27600 | 86.25% | 2.44 | 25000 | R-410A
212625535 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM9Y120D20MP11 | 31400 | 16.4 | 9.3 | 8.4 | 32200 | 28000 | 86.96% | 2.74 | 25200 | R-410A
212625568 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8V100C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625570 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8V100C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625586 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8V120C20MP12 | 31600 | 16.5 | 8.9 | 8.5 | 32200 | 27600 | 85.71% | 2.7 | 25000 | R-410A
212625637 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CPLC100C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625655 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TPLC100C20MP13 | 28600 | 15.6 | 8.4 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625685 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CPLC120C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
216990538 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | PL60H210P29*+TXV | 88*TB60110C21*** | 48500 | 19 | 11 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216990589 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | V,C36H175P15*+TXV | 88*TB48090C17*** | 33400 | 20 | 11.5 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
216990590 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | PL36H210P74*+TXV | 88*TB48090C17*** | 32800 | 20 | 11 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
216800804 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG37*48+TXV | BGH96M100C5C | 44000 | 16 | 10 | 8.5 | 45000 | 32600 | 72.44% | 1.85 | 33000 | R-454B
216990608 | 3.58 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | PL48H210P75*+TXV | 88*TB48070C17*** | 43000 | 20 | 10.5 | 9 | 46500 | 36800 | 79.14% | 2 | 39000 | R-454B
216990623 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | PL60H210P17*+TXV | 88*TB48090C17*** | 44000 | 20 | 11.5 | 9 | 47000 | 35400 | 75.32% | 1.86 | 37400 | R-454B
212625687 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | CPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625702 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625718 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8V100C20MP12 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625719 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8V100C20MP12 | 32800 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625737 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8V120C20MP12 | 30400 | 16.1 | 8 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625770 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TPLC100C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625786 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625802 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM9Y120D20MP11 | 31800 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
216990640 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | PL60H210P29*+TXV | 88*TB60090C21*** | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 1.92 | 38000 | R-454B
215933560 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0701716B* | 33600 | 19 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30800 | R-454B
216990756 | 1.93 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | C36A***L15*+TXV | 88*TB36045C17*** | 23200 | 17 | 9.5 | 9 | 22000 | 16200 | 73.64% | 1.98 | 19000 | R-454B
214312433 | 2.48 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H***P229+TD |  | 29800 | 15.5 | 11.3 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
216990655 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | V,C60H210P29*+TXV | 88*TB60110C21*** | 44000 | 21 | 11 | 9.5 | 46000 | 36000 | 78.26% | 1.92 | 38000 | R-454B
216990656 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | A60VHA*+TXV | 88*TB60110C21*** | 45000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 2 | 38000 | R-454B
212625835 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625854 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9V120D20MP12 | 29400 | 16.3 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625855 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V120D20MP12 | 32000 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625869 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9V120D20MP12 | 32800 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
216990659 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | V,C48H210P75*+TXV | 88*TB60110C21*** | 44000 | 21 | 11 | 9.5 | 46000 | 36000 | 78.26% | 1.92 | 38000 | R-454B
216992527 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | H,PG48*60+TXV | 88*TB60090C21*** | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216990539 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | V,C60H210P29*+TXV | 88*TB60110C21*** | 48500 | 19 | 11 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216992511 | 4.08 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | H,PG48*60+TXV | 986TD60080C21*** | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
212625870 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9V120D20MP12 | 30600 | 16.6 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625921 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9V040A10MP12 | 30000 | 16.6 | 9.1 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625922 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625955 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9E100C20MP12 | 32400 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626070 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y080B12MP11 | 32200 | 18 | 9.9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626238 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626271 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.2 | 33600 | 28200 | 83.93% | 2.67 | 25800 | R-410A
212626323 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.1 | 33600 | 29000 | 86.31% | 2.69 | 26200 | R-410A
212626337 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626340 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626373 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9Y080C16MP11 | 29600 | 17.8 | 9 | 8.4 | 33600 | 28000 | 83.33% | 2.62 | 25600 | R-410A
212626672 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9E060A10MP12 | 30600 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626771 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8V100C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.62 | 25200 | R-410A
212626839 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E080B12MP12 | 32200 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626855 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8E080B12MP11 | 29200 | 17.2 | 8.9 | 8.5 | 33800 | 27800 | 82.25% | 2.62 | 25600 | R-410A
212626906 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8E100B12MP11 | 29400 | 17.2 | 9.4 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626925 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8E100B12MP11 | 33200 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626938 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TMLE060A12MP11 | 30400 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212380905 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P179 | BGH96M100C5A | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212380860 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG8J936 | BGH96M060B3B | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380871 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P159 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380744 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P459 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213495250 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES040A12SMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
215413745 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214295813 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | F,PE*G32924 |  | 23000 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213352878 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430U-18HFN1-M | MVBL-18HWFN1-MH3 |  | 18000 | 17 | 12.4 | 9.5 | 19000 | 18000 | 94.74% | 2 | 13500 | R-410A
215399938 | 1.87 | Yes | No | LUXAIRE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR |  | 22400 | 15.2 | 11 | 8.5 | 22600 | 21200 | 93.81% | 2.65 | 18600 | R-454B
213495284 | 2.68 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES080C16SMPS1 | 32200 | 18 | 9.9 | 8.5 | 33200 | 27400 | 82.53% | 2.7 | 25200 | R-410A
212381060 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M120D5B | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
213184850 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG48948+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213493896 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES080C16SMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
216797689 | 1.92 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Y243D | SL6*31+TXV |  | 23000 | 18 | 10 | 8.8 | 22400 | 17600 | 78.57% | 1.96 | 16000 | R-454B
215402626 | 1.88 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | L(E,F)W30B4 |  | 22600 | 15.2 | 9 | 8.5 | 24400 | 22000 | 90.16% | 2.8 | 19600 | R-410A
213281364 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H175P389+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213281369 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H175P389+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215678105 | 4.63 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU0802120B* | 55500 | 16.5 | 8.5 | 8.5 | 60000 | 42000 | 70% | 1.9 | 51500 | R-454B
216797257 | 2.92 | Yes | No | LG | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | LUU360HV | H,GG1K936+TD | FG7TC100D-V35C | 35000 | 15.2 | 10.5 | 9 | 40500 | 33800 | 83.46% | 1.8 | 26000 | R-410A
215431120 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | A36VDA+TXV+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
214802107 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG8J936+AEFE4B* |  | 23600 | 20 | 12.7 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215431129 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | V,R36H***P449+AEFE3A* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
215407204 | 1.75 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | CE2903C+TXV |  | 21000 | 16 | 9.5 | 8.7 | 21400 | 16500 | 77.1% | 1.98 | 15000 | R-410A
216618742 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | H,GE48960+AEFE5* |  | 46000 | 17 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
214312422 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG50960+TD |  | 41500 | 15.5 | 11.3 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215382870 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*E34930 |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.04 | 15000 | R-410A
215412970 | 1.78 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG32924+AEFE4B* |  | 21400 | 16 | 9.5 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
215389840 | 4.33 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-4860A | PL60H210P199+TD |  | 52000 | 15.2 | 10.5 | 8.6 | 51000 | 36800 | 72.16% | 1.9 | 41000 | R-410A
216055480 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E026A08MP12 | 21200 | 17 | 10.5 | 8.5 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
213184849 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG48960+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
216679723 | 1.47 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 927TA48060V17*** | 17600 | 16 | 10.5 | 8.5 | 18100 | 18300 | 101.1% | 2.12 | 12200 | R-410A
212626942 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TMLE060A12MP11 | 30400 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626955 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TMLE100B12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626957 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626975 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8E120C16MP11 | 32400 | 18 | 10 | 8.4 | 33800 | 28800 | 85.21% | 2.75 | 26200 | R-410A
212627025 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM8Y100C16MP11 | 31800 | 18.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
212627039 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627058 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9V080C16MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212361596 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M120D5B | 44500 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34000 | R-410A
213281315 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG86960+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
203449873 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | F,PE*BB9948 |  | 44000 | 16 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213281447 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V48H175P159+AEFE4B* |  | 44500 | 18 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213281311 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P299+AEFE5* |  | 45500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213184851 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG88948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
216681636 | 1.47 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CSPH*3012AL* | 927TA60080V21*** | 17600 | 15.5 | 10.5 | 8.5 | 18100 | 18000 | 99.45% | 1.96 | 12200 | R-410A
213613883 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E49960 |  | 50500 | 15.2 | 9.5 | 8.35 | 51000 | 36800 | 72.16% | 1.78 | 34200 | R-410A
205993424 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | BV**C6960 |  | 45000 | 16 | 11.5 | 9.25 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
214861594 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3X | MVBC-48HWFN10-MD3E-D |  | 48000 | 16.5 | 10.5 | 9.5 | 50000 | 46000 | 92% | 1.9 | 37000 | R-454B
213607926 | 4 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-24WADU | F,PE*CC7960 |  | 48000 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
213753615 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)36B34+TDR | 59TP6C100V21**20 | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
212596654 | 3.92 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | F,PC*CC4960+TD |  | 47000 | 15.2 | 10 | 8.4 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
213362051 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG35948 | BGH96M080B3B | 41000 | 16 | 11 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
213281328 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213281353 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213206231 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A045E14**12 | 23800 | 16.5 | 10.4 | 8.1 | 26000 | 20400 | 78.46% | 2.96 | 19100 | R-410A
213206233 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*A045E14**12 | 23800 | 16.4 | 10.3 | 8.1 | 26000 | 20400 | 78.46% | 2.98 | 19100 | R-410A
213206240 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*A045E17**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.98 | 19100 | R-410A
213206242 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A045E17**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.95 | 19100 | R-410A
213206265 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A070E17**12 | 23400 | 17 | 10 | 8.1 | 25600 | 20000 | 78.12% | 2.94 | 18800 | R-410A
213206415 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2D040E17**12 | 23800 | 16 | 10 | 8.1 | 26000 | 20400 | 78.46% | 2.89 | 19100 | R-410A
213206422 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2D060E14**12 | 23400 | 17 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213206467 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC2D080E21**20 | 23800 | 17 | 10.3 | 8.1 | 26000 | 20200 | 77.69% | 2.96 | 19000 | R-410A
213206490 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC5B026E14**10 | 23200 | 16.5 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.94 | 18900 | R-410A
214389572 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | AEW264+TDR |  | 23000 | 16 | 10 | 8.5 | 26000 | 23400 | 90% | 2.77 | 19000 | R-410A
213206244 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*A045E17**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.98 | 19100 | R-410A
214861552 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBC-24HWFN10-MB3E |  | 24000 | 18.2 | 11 | 9.7 | 26000 | 21600 | 83.08% | 1.87 | 20000 | R-454B
213281354 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213146779 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213146784 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213206330 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*A045V14**12 | 23200 | 16.9 | 10.3 | 8.1 | 25600 | 20000 | 78.12% | 2.92 | 18800 | R-410A
213206277 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A070E17**16 | 23800 | 16.5 | 10.4 | 8.1 | 26000 | 20200 | 77.69% | 2.87 | 19000 | R-410A
213206343 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*A070V14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.86 | 19100 | R-410A
213206411 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2D040E17**12 | 23400 | 16 | 10 | 8.1 | 26000 | 20400 | 78.46% | 2.89 | 19100 | R-410A
213206427 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2D060E14**12 | 23400 | 17 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213206443 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC2D060E17**14 | 23800 | 17 | 10 | 8.1 | 26400 | 20400 | 77.27% | 2.86 | 19200 | R-410A
213206462 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2D080E21**20 | 23800 | 17 | 10.4 | 8.1 | 26000 | 20200 | 77.69% | 2.91 | 19000 | R-410A
213206497 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC5B040E14**10 | 23800 | 15.2 | 9.9 | 8.1 | 26200 | 20400 | 77.86% | 2.96 | 19200 | R-410A
213206561 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6B040V14**10 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.63 | 19000 | R-410A
213203962 | 1.44 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)30B34+TDR | *92ESN0601412A* | 17300 | 16.3 | 10.7 | 8.5 | 18500 | 15200 | 82.16% | 2.27 | 15200 | R-410A
213206251 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*A070E14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.99 | 19100 | R-410A
213206436 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC2D060E17**14 | 23800 | 17 | 10 | 8.1 | 26400 | 20400 | 77.27% | 2.85 | 19200 | R-410A
213206520 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC5B060E14**12 | 23800 | 16 | 9.9 | 8.1 | 26000 | 20400 | 78.46% | 2.72 | 19100 | R-410A
213206571 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59TP6B040V14**10 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.63 | 19000 | R-410A
213206587 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6B060V14**12 | 23200 | 16.5 | 10 | 8.1 | 26400 | 20400 | 77.27% | 2.69 | 19300 | R-410A
213613384 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24G4 |  | 23400 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213206341 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*A070V14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.86 | 19100 | R-410A
213206350 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58TP*A070V14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213206357 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*A070V17**16 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213206373 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58TP*A090V17**16 | 23800 | 17 | 10 | 8.1 | 26000 | 20200 | 77.69% | 2.97 | 19000 | R-410A
213206543 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC5B080E17**16 | 23800 | 16 | 9.9 | 8.1 | 26200 | 20200 | 77.1% | 2.71 | 19100 | R-410A
216679375 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**2417AL* | 927TA48060V17*** | 23200 | 16.5 | 10 | 9.5 | 26400 | 25400 | 96.21% | 2.08 | 19200 | R-410A
213206573 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6B040V17**12 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.63 | 19000 | R-410A
216680527 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3617AL* | 927TA48080V17*** | 23400 | 17 | 10 | 9 | 25600 | 23400 | 91.41% | 1.84 | 18800 | R-410A
207728364 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | F,PE*BB9948 |  | 44000 | 16 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213311149 | 2.02 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L159+CBPE4B* |  | 24200 | 18 | 10.5 | 9 | 25000 | 22600 | 90.4% | 1.92 | 18300 | R-410A
214861530 | 2.75 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-33HFN10-M1X | MVBC-36HWFN10-MC1 |  | 33000 | 16.7 | 11.7 | 10 | 35000 | 34000 | 97.14% | 2 | 27400 | R-454B
213146780 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
214861598 | 2 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-24HFN10-M3 | MVBC-24HWFN10-MB3E-D |  | 24000 | 18.1 | 11 | 9.7 | 26000 | 21600 | 83.08% | 1.87 | 20000 | R-454B
213613376 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M244+TDR |  | 23000 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.92 | 19000 | R-410A
213613394 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36F4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213206254 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*A070E14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.97 | 19100 | R-410A
213206385 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58TP*A090V21**20 | 23200 | 17 | 10.3 | 8.1 | 25400 | 19800 | 77.95% | 2.94 | 18600 | R-410A
213206404 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2D040E14**10 | 23600 | 15.5 | 9.9 | 8.1 | 26000 | 20400 | 78.46% | 2.92 | 19100 | R-410A
215431160 | 3.88 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | A60VHA+TXV+AEFE5* |  | 46500 | 17 | 9.5 | 8.35 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
213205912 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*A070V14**12 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.85 | 20400 | R-410A
213205943 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58TP*A090V17**16 | 23600 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.94 | 20000 | R-410A
213205945 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*A090V21**20 | 23800 | 16 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.94 | 20000 | R-410A
213206010 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2D060E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.91 | 20400 | R-410A
212603168 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG80936 | *92ESN0401712A* | 23800 | 16 | 10 | 8.5 | 24400 | 22600 | 92.62% | 1.88 | 18100 | R-410A
213386562 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HE86960+TD |  | 50500 | 15.2 | 9.5 | 8.5 | 51000 | 36800 | 72.16% | 1.8 | 34200 | R-410A
212693030 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HE88960+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
213738343 | 2.45 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | PL36H175P069 | *80MS(N,L)0701712A* | 29400 | 15.2 | 8.5 | 8.1 | 32600 | 27200 | 83.44% | 1.8 | 22400 | R-410A
213738360 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | V,G36H175P159 | *80MSU0401712A* | 29800 | 15.2 | 9 | 8.1 | 32200 | 27200 | 84.47% | 1.8 | 22400 | R-410A
214239986 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EN(A,D)4X48L24**+WALLCON | *80CTL1352422B* | 32400 | 17 | 11.7 | 8.1 | 32600 | 24600 | 75.46% | 1.96 | 31400 | R-410A
213206578 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6B040V17**12 | 23200 | 16 | 10 | 8.1 | 25800 | 20200 | 78.29% | 2.63 | 19000 | R-410A
213206594 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59TP6B060V14**12 | 23200 | 16.5 | 10 | 8.1 | 26400 | 20400 | 77.27% | 2.75 | 19300 | R-410A
213752643 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B070M14**12 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213752691 | 1.88 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B090M21**16 | 22600 | 17.3 | 10.2 | 8.4 | 25200 | 19900 | 78.97% | 2.96 | 18600 | R-410A
213752740 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*B070V14**12 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.88 | 19100 | R-410A
213752776 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*B110V21**22 | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.91 | 19100 | R-410A
213752825 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2E080M21**20 | 23000 | 17.3 | 10.2 | 8.4 | 25600 | 20200 | 78.91% | 2.98 | 18900 | R-410A
213752908 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SP6A040V14**10 | 23000 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.83 | 19000 | R-410A
213206418 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2D040E17**12 | 23800 | 16 | 10 | 8.1 | 26000 | 20400 | 78.46% | 2.89 | 19100 | R-410A
213206455 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC2D080E17**16 | 23800 | 17.5 | 10.4 | 8.1 | 25600 | 20000 | 78.12% | 2.91 | 18800 | R-410A
213206504 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC5B040E17**12 | 23800 | 15.2 | 9.5 | 8.1 | 26400 | 20400 | 77.27% | 2.85 | 19300 | R-410A
213206536 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC5B060E17**14 | 23800 | 16.5 | 10.3 | 8.1 | 26000 | 20200 | 77.69% | 2.71 | 19000 | R-410A
213206636 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6B100V21**20 | 23000 | 17 | 10.3 | 8.1 | 25200 | 19900 | 78.97% | 2.7 | 18600 | R-410A
213752683 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B090M17**14 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213752735 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*B070V14**12 | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.88 | 19100 | R-410A
213752967 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SP6A080V21**20 | 23800 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.92 | 19000 | R-410A
213613385 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24H4 |  | 23800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213752431 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC6A026M14**10 | 23400 | 15.5 | 9 | 8.1 | 25200 | 22600 | 89.68% | 2.86 | 20200 | R-410A
213752516 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SP6A060V14**12 | 22800 | 15.9 | 9.3 | 8.1 | 24400 | 22000 | 90.16% | 2.87 | 19600 | R-410A
216992464 | 4.63 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | H,PG48*60+TXV | 88*TB60090C21*** | 55500 | 19 | 8.5 | 9 | 57500 | 41000 | 71.3% | 2.02 | 50000 | R-454B
213753653 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B070M14**12 | 35200 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.63 | 29400 | R-410A
213753702 | 2.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B135M24**20 | 34800 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213753704 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B135M24**20 | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213753738 | 2.83 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58TP*B110V21**22 | 34000 | 16.4 | 9.8 | 8.5 | 38000 | 31600 | 83.16% | 2.73 | 29000 | R-410A
213281327 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG2K960+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213613378 | 1.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24A4 |  | 22000 | 15.8 | 9.7 | 9 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
213752648 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M14**12 | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213752701 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B090M21**20 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213752715 | 1.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B110M21**20 | 22800 | 17.2 | 10 | 8.4 | 25600 | 20000 | 78.12% | 2.96 | 18800 | R-410A
213752733 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*B070V14**12 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.88 | 19100 | R-410A
213752799 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2E060M14**12 | 23800 | 17 | 10 | 8.5 | 26600 | 20200 | 75.94% | 2.86 | 19200 | R-410A
213752801 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2E060M14**12 | 23800 | 17 | 10 | 8.5 | 26600 | 20200 | 75.94% | 2.86 | 19200 | R-410A
213752882 | 1.9 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC6A060M14**12 | 22800 | 17 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213753036 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6C080V21**20 | 23600 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213613390 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36B4 |  | 23400 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213752681 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B090M17**14 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213752781 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*B110V21**22 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.91 | 19100 | R-410A
213752872 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC6A040M17**12 | 23200 | 16 | 9 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19200 | R-410A
216680647 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3621AL* | 927TA48080V17*** | 23400 | 16.5 | 10 | 9 | 25800 | 23800 | 92.25% | 1.78 | 18900 | R-410A
213752630 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B045M14**12 | 23400 | 17 | 10 | 8.5 | 27000 | 20400 | 75.56% | 2.88 | 19400 | R-410A
213355932 | 4.17 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | A60VHA+TXV+AEFE5* |  | 50000 | 17 | 11.2 | 9.25 | 53000 | 38000 | 71.7% | 1.98 | 42500 | R-410A
213753831 | 2.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SP6A080V17**16 | 34000 | 16 | 9.9 | 8.1 | 38500 | 31400 | 81.56% | 2.71 | 29000 | R-410A
213753867 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59TP6C080V21**20 | 33800 | 16.5 | 9.9 | 8.1 | 37800 | 31400 | 83.07% | 2.72 | 28800 | R-410A
212984707 | 1.53 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *92MSN0801716A* | 18300 | 16.5 | 11 | 8.5 | 18200 | 17700 | 97.25% | 2.14 | 12300 | R-410A
213752638 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B045M14**12 | 23400 | 17 | 10 | 8.5 | 27000 | 20400 | 75.56% | 2.88 | 19400 | R-410A
213752663 | 1.87 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B070M17**16 | 22400 | 17.2 | 10 | 8.4 | 25200 | 20000 | 79.37% | 2.98 | 18700 | R-410A
213752704 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B090M21**20 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213752745 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*B070V17**16 | 22400 | 17.2 | 9 | 8.4 | 25200 | 20000 | 79.37% | 2.98 | 18700 | R-410A
213752761 | 1.87 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*B090V17**16 | 22400 | 17.4 | 9.8 | 8.5 | 25200 | 19900 | 78.97% | 2.97 | 18600 | R-410A
213752763 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*B090V21**20 | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.92 | 19100 | R-410A
213752788 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2E040M17**12 | 23400 | 16 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19300 | R-410A
213752806 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC2E060M17**14 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213752972 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SP6A100V21**20 | 23600 | 17 | 10 | 8.5 | 26000 | 20000 | 76.92% | 2.89 | 18900 | R-410A
213753049 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C100V21**20 | 23600 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213753054 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6C100V21**22 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.94 | 19100 | R-410A
213752655 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M17**12 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.86 | 19000 | R-410A
213752778 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*B110V21**22 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.91 | 19100 | R-410A
213752855 | 1.87 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC6A040M14**10 | 22400 | 16.3 | 9.8 | 8.5 | 25400 | 20200 | 79.53% | 2.94 | 18800 | R-410A
213752937 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SP6A060V17**14 | 23400 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213752980 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6C040V14**10 | 23000 | 16 | 9.5 | 8.5 | 27000 | 20600 | 76.3% | 2.85 | 19500 | R-410A
213753023 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6C080V17**16 | 23400 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213753039 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C080V21**20 | 23800 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213613395 | 2 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36L4 |  | 24000 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
216679494 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*2417AL* | 59TP7A060V17**16 | 23200 | 16.5 | 10 | 9 | 26400 | 24400 | 92.42% | 1.86 | 19300 | R-410A
216680598 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3612AL* | 59TP7A080V17**16 | 23800 | 16 | 10 | 8.5 | 25200 | 22400 | 88.89% | 1.75 | 18700 | R-410A
213206095 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59SC5B060E14**12 | 23800 | 15.2 | 9.4 | 8.1 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213772678 | 1.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *97CMN0801714B* | 23200 | 16 | 10.5 | 8.1 | 22000 | 16800 | 76.36% | 1.88 | 21000 | R-410A
211259644 | 1.53 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96VSN0601412A* | 18400 | 16 | 11 | 8.5 | 18400 | 17600 | 95.65% | 2.12 | 12400 | R-410A
211259862 | 1.55 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *95ESN0261410A* | 18600 | 16 | 11 | 8.5 | 18600 | 17500 | 94.09% | 2.12 | 12500 | R-410A
211259878 | 1.52 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96VTN0601714A* | 18200 | 16 | 10.5 | 8.5 | 18200 | 17700 | 97.25% | 2.14 | 12300 | R-410A
211260311 | 1.45 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *96VSN0801716A* | 17400 | 16 | 10.5 | 8.5 | 18300 | 19200 | 104.9% | 2.3 | 12300 | R-410A
213206328 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A110E21**20 | 23800 | 16.5 | 10.3 | 8.1 | 26200 | 20200 | 77.1% | 2.98 | 19100 | R-410A
213752176 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M14**12 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213752210 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*B070M21**16 | 23600 | 16.5 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213752310 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*B090V17**16 | 23400 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.87 | 20000 | R-410A
213752444 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC6A040M14**10 | 22800 | 15.4 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
214279942 | 2.05 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3721AL* | 59SC6A060M17**16 | 24600 | 17 | 10 | 9 | 25400 | 21200 | 83.46% | 1.78 | 18700 | R-410A
215677095 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *80CSU1002120A* | 56500 | 18 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
212927493 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CE2403C+TXV |  | 22800 | 19 | 12 | 9.2 | 22200 | 17200 | 77.48% | 1.94 | 21400 | R-410A
214242258 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EN(A,D,W)4X48L21**+WALLCON | *95CSU0601716B* | 24000 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
211259736 | 1.58 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *80ESU0401712A* | 19000 | 17 | 11 | 8.5 | 18900 | 17400 | 92.06% | 2.14 | 12600 | R-410A
215850482 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y100C16MP11 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
214295856 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H210P759 | Z8ES080C16SMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 23800 | 74.84% | 2.14 | 24400 | R-410A
213752773 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*B110V21**22 | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.91 | 19100 | R-410A
213752814 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2E080M17**16 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.86 | 19100 | R-410A
212361434 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M080C4B | 41500 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361466 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M080C4B | 41500 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361477 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M100D5A | 44500 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212380854 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG8J936 | BGH96M060B3A | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216800664 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V60H210P19*+TXV | BGH96M100C5C | 51500 | 17 | 11 | 8.5 | 51500 | 37200 | 72.23% | 1.8 | 37000 | R-454B
213752660 | 1.87 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M17**16 | 22400 | 17.3 | 10 | 8.4 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213752758 | 1.9 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*B090V17**16 | 22800 | 17.5 | 9.8 | 8.5 | 25200 | 19900 | 78.97% | 2.97 | 18600 | R-410A
213752827 | 1.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC2E080M21**20 | 22800 | 17.2 | 10 | 8.4 | 25600 | 20200 | 78.91% | 2.96 | 18900 | R-410A
213752857 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC6A040M14**10 | 22400 | 16.3 | 9.8 | 8.4 | 25400 | 20200 | 79.53% | 2.95 | 18800 | R-410A
213753009 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6C060V14**12 | 23400 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
216487999 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | A36VBA*+TXV | TM9Y080B12MP11 | 22400 | 17 | 11.5 | 9.15 | 21200 | 18200 | 85.85% | 1.94 | 17200 | R-454B
213307133 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG2K948+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213253169 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84960+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
215850603 | 2.48 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C16SMPS1 | 29800 | 17.5 | 10.5 | 8.5 | 30400 | 23400 | 76.97% | 2 | 25600 | R-454B
214295843 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H210P759 | TM8V060A12MP12 | 34000 | 17 | 9.5 | 8.1 | 32400 | 23800 | 73.46% | 2.06 | 24600 | R-410A
214295852 | 2.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H***P219 | Z8ES040A12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.06 | 25600 | R-410A
215727894 | 2.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J(1,2)36+TXV | TM9V100C20MP12 | 34200 | 18 | 10 | 8.5 | 31000 | 25600 | 82.58% | 2 | 27600 | R-454B
214295854 | 2.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H175P159 | Z8ES080B12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
214295855 | 2.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H210P759 | Z8ES080B12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
215412951 | 2.82 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,RG9J936+AEFE4B* |  | 33800 | 18 | 10 | 9.45 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
213752895 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC6A080M21**20 | 22400 | 17.3 | 9.7 | 8.4 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213752913 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SP6A040V14**10 | 23200 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.83 | 19000 | R-410A
213752929 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SP6A060V14**12 | 23200 | 16.5 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.86 | 19300 | R-410A
213752988 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6C040V14**10 | 23000 | 16 | 9.5 | 8.5 | 27000 | 20600 | 76.3% | 2.85 | 19500 | R-410A
213753004 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6C060V14**12 | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
208106496 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P199 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
215588311 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 58CU*A100C21**20 | 51500 | 19 | 11.5 | 8.1 | 53000 | 46500 | 87.74% | 1.85 | 48000 | R-454B
215676895 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *95CSU1002122B* | 48500 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
215675925 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CMN1002122B* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
212509297 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | F,PE*SS9948 |  | 44000 | 16 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
212380761 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P199 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380895 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG50960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380911 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P179 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213238536 | 3.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM8E100C16MP11 | 43500 | 16.2 | 11 | 8.4 | 44500 | 31200 | 70.11% | 3.21 | 30600 | R-410A
216992566 | 1.95 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | H,PG7J*36+TXV | 986TD66120C24*** | 23400 | 16 | 9.5 | 8.5 | 22800 | 16200 | 71.05% | 1.98 | 19000 | R-454B
213771355 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4221AL*+UI | 59TN6C100C21**22 | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
211756101 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
213493988 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES120C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.64 | 25600 | R-410A
213495317 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES100B12SMPS1 | 32200 | 18.5 | 9.4 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
213495340 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | Z8ES100C20LMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
215281568 | 1.72 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | SM3925 |  | 20600 | 16 | 10 | 8.7 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
214861543 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBC-30HWFN10-MC3E |  | 30000 | 16.9 | 11.7 | 10 | 34000 | 32600 | 95.88% | 1.96 | 23800 | R-454B
214279890 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3017AL* | 59SC6A060M17**16 | 23400 | 16.5 | 10 | 9 | 25800 | 24400 | 94.57% | 2.02 | 19000 | R-410A
214861545 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3X | MVBDM-36HWFN10-WB3 |  | 36000 | 17.7 | 12 | 10 | 36000 | 32600 | 90.56% | 2.06 | 24600 | R-454B
212614019 | 2.48 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | HG8J936+TD |  | 29800 | 15.2 | 10.5 | 9.5 | 31400 | 26600 | 84.71% | 1.82 | 21600 | R-410A
213752974 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SP6A100V21**20 | 23800 | 17 | 10 | 8.5 | 26000 | 20000 | 76.92% | 2.89 | 18900 | R-410A
213753025 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6C080V17**16 | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
213753663 | 2.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B070M17**16 | 35000 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
215281566 | 1.68 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | SM5931 |  | 20200 | 16 | 9.5 | 8.55 | 21200 | 16500 | 77.83% | 1.96 | 15000 | R-410A
213355437 | 2.92 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M36E6 |  | 35000 | 18 | 9 | 8.1 | 35400 | 26000 | 73.45% | 2.82 | 25000 | R-410A
213608429 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HE86948+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
213366568 | 3.96 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | HE49960+AEFE5* |  | 47500 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
212361485 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M120D5A | 44500 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361490 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M120D5B | 45000 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361590 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M100D5A | 44500 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34000 | R-410A
212361592 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M100D5B | 44500 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34000 | R-410A
214056970 | 1.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | D(A,C,E)24A44+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 14900 | R-410A
216990244 | 2.78 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | V,C36H175P15*+TXV | 88*TB36045C17*** | 33400 | 17 | 9.5 | 9 | 33600 | 25000 | 74.4% | 1.88 | 29600 | R-454B
216011838 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE34936 | CP9C060B12MP13 | 32600 | 17 | 9.5 | 8.1 | 32000 | 23200 | 72.5% | 2.02 | 25400 | R-410A
216011845 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE33936 | CP9C080C16MP13 | 32800 | 17 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 2.04 | 25200 | R-410A
215850713 | 3.33 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL9E080C16UH11 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
215438165 | 3.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | FE*TT4*48+TXV |  | 46000 | 18 | 12 | 9 | 44000 | 33600 | 76.36% | 2.1 | 34600 | R-454B
215912364 | 1.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
213238572 | 3.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D44+TDR | TM9E100C16MP12 | 43500 | 16.2 | 11 | 8.4 | 44500 | 31200 | 70.11% | 3.21 | 30600 | R-410A
216800666 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | A36VDA*+TXV | BGH96M060B3C | 24000 | 18 | 12 | 9 | 22400 | 16800 | 75% | 1.9 | 19000 | R-454B
213495374 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ES120C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.64 | 25600 | R-410A
213493893 | 2.68 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES080C16LMPS1 | 32200 | 18 | 9.9 | 8.5 | 33200 | 27400 | 82.53% | 2.7 | 25200 | R-410A
213493970 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES120C16LMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
216990260 | 2.75 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | C36A***L13*+TXV | 88*TB48070C17*** | 33000 | 17 | 9.5 | 9 | 34400 | 25400 | 73.84% | 1.86 | 30000 | R-454B
216990267 | 2.8 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | PL36H***P44*+TXV | 88*TB48070C17*** | 33600 | 18 | 10 | 9 | 33600 | 24800 | 73.81% | 1.88 | 29400 | R-454B
213307711 | 4 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | F,PE*CC7960 |  | 48000 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
212693034 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HE88960 |  | 50500 | 15.2 | 9.5 | 8.5 | 51000 | 36800 | 72.16% | 1.8 | 34200 | R-410A
216990269 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | C36A***L53*+TXV | 88*TB48070C17*** | 34400 | 18 | 10 | 9 | 33800 | 24800 | 73.37% | 1.9 | 29400 | R-454B
216990678 | 4.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | V,C60H210P29*+TXV | 88*TB60090C21*** | 56000 | 18 | 11.5 | 8.1 | 59000 | 45000 | 76.27% | 2 | 46000 | R-454B
216992557 | 4.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | H,PG48*60+TXV | 987MC60080C21*** | 55500 | 18 | 11 | 8.1 | 58500 | 45500 | 77.78% | 1.95 | 46500 | R-454B
216764767 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S8X1C100M5PTC | 43500 | 17.1 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29400 | R-454B
216764549 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S8X1B060M4PTC | 23000 | 17.1 | 12.5 | 9 | 21600 | 17100 | 79.17% | 2 | 15200 | R-454B
216765894 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3 | S8V2A040M3PDB | 23800 | 17.1 | 12.5 | 8.7 | 22400 | 17500 | 78.12% | 1.98 | 15600 | R-454B
215412952 | 2.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,RG9J936+AEFE3A* |  | 33600 | 17 | 10 | 9.45 | 33400 | 25600 | 76.65% | 2.04 | 23000 | R-410A
213366575 | 3.96 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | HE49948+AEFE5* |  | 47500 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
212596647 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HE49960+TD |  | 47000 | 15.2 | 10 | 8.35 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
203449867 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CE2903C+TXV |  | 22800 | 19 | 12 | 9.2 | 22200 | 17200 | 77.48% | 1.94 | 21400 | R-410A
216011841 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE33936 | CP9C080B12MP13 | 32800 | 17 | 9.5 | 8.3 | 31600 | 23000 | 72.78% | 2 | 24000 | R-410A
216011842 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE34936 | CP9C080B12MP13 | 33200 | 17 | 9.5 | 8.4 | 31800 | 23000 | 72.33% | 2.02 | 24000 | R-410A
213771725 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4824AL*+UI | 59TN6C100C21**22 | 24200 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
215308399 | 2 | Yes | No | AMERISTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | E4HL5036A1000A | F,PE*G34925 |  | 24000 | 15.2 | 11 | 8.5 | 22400 | 17600 | 78.57% | 1.9 | 18100 | R-410A
212381054 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M100D5A | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
213281313 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG2K960+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
215677055 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN0802120B* | 56500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.06 | 56500 | R-454B
215677195 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *96CTN1002122B* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
216011847 | 2.83 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | CP9C080C16MP13 | 34000 | 17 | 10 | 8.1 | 32200 | 23400 | 72.67% | 2.08 | 24400 | R-410A
213307710 | 2.83 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | F,PE*CC4937 |  | 34000 | 15.2 | 10 | 9 | 33400 | 27600 | 82.63% | 1.8 | 23000 | R-410A
213738347 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | PL36H175P159 | *80MS(N,L)0701712A* | 29800 | 15.2 | 9 | 8.1 | 32600 | 27200 | 83.44% | 1.8 | 22400 | R-410A
215940926 | 3 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *97CTN1202422A* | 36000 | 22 | 12.5 | 8.5 | 37600 | 28400 | 75.53% | 2.04 | 32200 | R-454B
215940576 | 2.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X38M17A*+WALLCON | *80CSU0401712B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
213386560 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E86960 |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
213370123 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E50960 |  | 47000 | 15.2 | 10 | 8.4 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
215588387 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6121XMA*+UI | 59MN7C080C21**20 | 52500 | 19.5 | 11.7 | 8.5 | 54000 | 45500 | 84.26% | 2 | 48500 | R-454B
213771637 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *97CMN1002122B* | 24000 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
213163604 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,FG82936+AEFE3A* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
214861600 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBC-36HWFN10-MC3E-D |  | 36000 | 16.1 | 10 | 8.7 | 36000 | 27000 | 75% | 2 | 24800 | R-454B
213187950 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | V,T36H175P149+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
213187957 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | V,T36H175P459+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
213249353 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *G52960 |  | 50500 | 15.2 | 9.5 | 8.5 | 51000 | 36800 | 72.16% | 1.8 | 34200 | R-410A
213249354 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E88960 |  | 50500 | 15.2 | 9.5 | 8.5 | 51000 | 36800 | 72.16% | 1.8 | 34200 | R-410A
214242875 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CNPV*4217AL*+UI | 58TN*B070C17**16 | 24000 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.98 | 20800 | R-410A
214242945 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CNPV*4217AL*+UI | 59TN6C080C17**14 | 24000 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.98 | 20800 | R-410A
214861549 | 4.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M3X | MVBC-60HWFN10-MD3E |  | 54000 | 16 | 10 | 9 | 56000 | 52000 | 92.86% | 1.8 | 45000 | R-454B
213608428 | 1.87 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HE33936+TD |  | 22400 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
213249111 | 1.9 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *E34936+TD |  | 22800 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 14000 | R-410A
213249114 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E88960+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212596660 | 3.92 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | BV**C7960 |  | 47000 | 15.2 | 10 | 8.45 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
216765896 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3 | S9X1B080D4PSB | 23600 | 17 | 12.5 | 8.5 | 22200 | 17300 | 77.93% | 1.96 | 15400 | R-454B
207727235 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | BV**B7925 |  | 23600 | 18 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
207728062 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | F,PE*E34925 |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212693027 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HG52960 |  | 50500 | 15.2 | 9.5 | 8.5 | 51000 | 36800 | 72.16% | 1.8 | 34200 | R-410A
213753771 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC2E100M21**20 | 35000 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
213752718 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B110M21**20 | 23400 | 17.5 | 10.3 | 8.5 | 25600 | 20000 | 78.12% | 3.01 | 18800 | R-410A
213752783 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2E040M17**12 | 23400 | 16 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19300 | R-410A
213752900 | 1.92 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC6A080M21**20 | 23000 | 17.5 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213752934 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SP6A060V14**12 | 23200 | 16.5 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.86 | 19300 | R-410A
213753001 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6C060V14**12 | 23200 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
215431118 | 1.78 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | A24VBA+TXV+AEFE3A* |  | 21400 | 16 | 9.5 | 8.8 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
216800657 | 4.21 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | A60VGA*+TXV | BGH96M100C5C | 50500 | 17 | 11 | 9.5 | 53000 | 47500 | 89.62% | 1.94 | 51000 | R-454B
216766340 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S8V2B060M4PDB | 33200 | 16.5 | 12 | 8.7 | 32600 | 24000 | 73.62% | 2.16 | 21200 | R-454B
215431155 | 2.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z363C | H,RG80936+AEFE4B* |  | 34000 | 18 | 10 | 9.5 | 33400 | 25600 | 76.65% | 2.05 | 23000 | R-410A
215431128 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | PL36H***P449+AEFE3A* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
215431130 | 1.82 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG8J936+AEFE4B* |  | 21800 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
212693015 | 2.63 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HG34936 |  | 31600 | 15.2 | 9 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
213386559 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HE86960 |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
215940676 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *97CTN1002122A* | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
215940726 | 2.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X48M24A*+WALLCON | *96CTN0802120B* | 35000 | 21 | 12 | 8.5 | 38500 | 28400 | 73.77% | 2.04 | 32600 | R-454B
215939806 | 2.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1002122A* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.06 | 29800 | R-454B
215941576 | 3.71 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EVD5X48M21A*+WALLCON | *97CTN1002122A* | 44500 | 20 | 11 | 8.1 | 52000 | 38500 | 74.04% | 2 | 43500 | R-454B
215941646 | 3.79 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN1002122A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.9 | 43500 | R-454B
216981044 | 2.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | V,Y36H175P15*+TXV | TM9V060B12MP12 | 33000 | 17 | 11 | 8.5 | 29400 | 24800 | 84.35% | 2 | 26200 | R-454B
215224773 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | H,PG9J936 | 59MN7C080C21**20 | 33200 | 19 | 12 | 9 | 35200 | 25600 | 72.73% | 2.04 | 30200 | R-410A
216990238 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | PL36H210P29*+TXV | 88*TB36045C17*** | 34000 | 17 | 9.5 | 9 | 34000 | 25000 | 73.53% | 1.86 | 29800 | R-454B
216990690 | 4.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | V,C60H210P17*+TXV | 88*TB60110C21*** | 55500 | 19 | 11 | 8.5 | 58500 | 46000 | 78.63% | 2.02 | 46500 | R-454B
215389770 | 2.58 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-2436A | PL36H175P159+TD |  | 31000 | 15.2 | 10.5 | 8.8 | 32000 | 23200 | 72.5% | 1.9 | 23200 | R-410A
213281361 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H175P789+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214861595 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-48HFN10-M3X-D | MVBC-48HWFN10-MD3E-DD |  | 48000 | 16.3 | 11.7 | 9 | 56000 | 52000 | 92.86% | 1.8 | 45000 | R-454B
216679950 | 2.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4217AL* | 59TP7A080V17**16 | 35600 | 15.2 | 10 | 8.5 | 39000 | 34600 | 88.72% | 1.8 | 29400 | R-410A
214810780 | 2.85 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436AA* | HG82936+AEFE4B* |  | 34200 | 19.5 | 12 | 9.5 | 34400 | 24800 | 72.09% | 2 | 27000 | R-410A
214312430 | 2.45 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H210P759+TD |  | 29400 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
215438167 | 2 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | FE*G32*24+TXV |  | 24000 | 19 | 12 | 9.4 | 22400 | 16600 | 74.11% | 2.08 | 17400 | R-454B
214861601 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX630-48HFN10-M3 | MVBC-48HWFN10-MD3E-D |  | 48000 | 16 | 10 | 8.5 | 48000 | 38000 | 79.17% | 1.85 | 32400 | R-454B
213771217 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *96CTN0601714B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
213771267 | 1.98 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L21A*+WALLCON | *80CTL0901716B* | 23800 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
212603251 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG80936 | *80ES(N,L)0701712A* | 36000 | 15.2 | 10 | 8.5 | 36800 | 34400 | 93.48% | 2.06 | 28000 | R-410A
212603267 | 2.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG80936 | *96VSN0801716A* | 35600 | 16 | 10 | 8.1 | 36800 | 34200 | 92.93% | 2.04 | 28000 | R-410A
213738478 | 2.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG81936 | *80MS(N,L)0701712A* | 35600 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
213738511 | 2.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG80936 | *80VSL0451412B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
213738529 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG80936 | *92MSN0601412A* | 36000 | 15.2 | 10 | 8.5 | 36800 | 34800 | 94.57% | 2 | 28400 | R-410A
213738544 | 3.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | PL36H210P299 | *95MSU0401712A* | 36200 | 15.2 | 10 | 8.5 | 36800 | 34600 | 94.02% | 2.04 | 28200 | R-410A
215932980 | 2.6 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X24M12A*+WALLCON | *96CTN0401410B* | 31200 | 16 | 10 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215933080 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0701716B* | 33200 | 18.5 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 31000 | R-454B
215933130 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL1352422B* | 33400 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215933230 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0401410B* | 31800 | 17 | 10.5 | 9 | 34000 | 26200 | 77.06% | 1.94 | 30000 | R-454B
215933430 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN0802120B* | 33600 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215281572 | 1.73 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | SM7925 |  | 20800 | 16 | 10 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
212596783 | 1.87 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HG33936+TD |  | 22400 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
211599532 | 3.25 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B42T21 | LEM48C4 |  | 39000 | 16 | 12.5 | 8.1 | 40500 | 29000 | 71.6% | 3.33 | 28200 | R-410A
207728056 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | F,PE*G34925 |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213362465 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG35936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216573778 | 2.55 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | CM36B3K+TDR |  | 30600 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.56 | 27000 | R-454B
214861586 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBDM-18HWFN10-WA3-D |  | 18000 | 19 | 12.5 | 10.1 | 18000 | 18600 | 103.3% | 2.12 | 14700 | R-454B
212367400 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG82936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215934040 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU1002122B* | 44000 | 21 | 11 | 9.5 | 48000 | 36200 | 75.42% | 2 | 39000 | R-454B
215438142 | 3.63 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | FE*TT6*60+TXV |  | 43500 | 15.2 | 11.7 | 8.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
213493883 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES080B12SMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.66 | 26200 | R-410A
214777844 | 1.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*E33930 |  | 21600 | 16 | 10 | 8.85 | 21400 | 16500 | 77.1% | 2.02 | 15000 | R-410A
212596784 | 1.85 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HE7J936+TD |  | 22200 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
213370120 | 2.65 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *G35936+TD |  | 31800 | 15.2 | 9 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
213752969 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SP6A100V21**20 | 23600 | 17 | 10 | 8.5 | 26000 | 20000 | 76.92% | 2.89 | 18900 | R-410A
213753017 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C060V17**16 | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.88 | 19400 | R-410A
216679471 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3012AL* | 927TA48060V17*** | 23600 | 16 | 10 | 9 | 25800 | 23200 | 89.92% | 1.8 | 19000 | R-410A
216680539 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3621AL* | 927TA48080V17*** | 23600 | 17 | 10 | 9 | 25600 | 23200 | 90.62% | 1.84 | 18800 | R-410A
215438143 | 3.63 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | FE*CC6*60+TXV |  | 43500 | 15.2 | 11.7 | 8.5 | 44000 | 40000 | 90.91% | 1.8 | 45000 | R-454B
215281569 | 1.73 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | SM7931 |  | 20800 | 16 | 10 | 8.75 | 21400 | 16500 | 77.1% | 2 | 15000 | R-410A
213370129 | 1.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *G35936 |  | 23000 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 14000 | R-410A
215676995 | 4.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0702120B* | 56500 | 18 | 9 | 9 | 64000 | 45000 | 70.31% | 2.06 | 56500 | R-454B
213206513 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC5B040E17**12 | 23800 | 15.2 | 9.5 | 8.1 | 26400 | 20400 | 77.27% | 2.73 | 19300 | R-410A
212627073 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627141 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TL8E080C16UH11 | 29200 | 16.7 | 9.4 | 8.5 | 33800 | 27400 | 81.07% | 2.68 | 25400 | R-410A
212627209 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9Y060B12MP11 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 29400 | 86.47% | 2.43 | 26600 | R-410A
212627240 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627273 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9E060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627274 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9E060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627289 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9E060B12MP12 | 33200 | 17.5 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
216051831 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | F,PE*E34(1,2)25+TXV |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.04 | 15000 | R-410A
213386561 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E86960+TD |  | 50500 | 15.2 | 9.5 | 8.5 | 51000 | 36800 | 72.16% | 1.8 | 34200 | R-410A
214606949 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | F,PE*SS9937 |  | 34000 | 18 | 10.5 | 8.7 | 31600 | 22800 | 72.15% | 2.1 | 23600 | R-410A
213370128 | 1.87 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *E33936 |  | 22400 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
213307709 | 1.97 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | F,PE*E34925 |  | 23600 | 17 | 11.7 | 9 | 22400 | 21600 | 96.43% | 1.8 | 15000 | R-410A
214861533 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-48HFN10-M2 | MVBC-48HWFN10-MD2 |  | 48000 | 17.8 | 10 | 10 | 50000 | 35200 | 70.4% | 1.9 | 40000 | R-454B
212361565 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32(1,2)36+TXV | BGH96M080B3A | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 18400 | R-410A
212361569 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33(1,2)36+TXV | BGH96M080B3B | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.9 | 18400 | R-410A
216992986 | 1.88 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | H,PG7J*36+TXV | 916SA60100M21*** | 22600 | 15.2 | 10.5 | 8.1 | 19400 | 18500 | 95.36% | 1.85 | 16800 | R-454B
216992991 | 1.83 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | H,PG7J*36+TXV | 927TA48060V17*** | 22000 | 16 | 10.5 | 8.5 | 19400 | 18700 | 96.39% | 1.96 | 17000 | R-454B
213249352 | 2.63 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *E34936 |  | 31600 | 15.2 | 9 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
213362466 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG9J936 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215934530 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN1002122B* | 44000 | 20 | 10.5 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
214302677 | 2.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | F,PE*G33936 |  | 33000 | 18 | 11.7 | 9.2 | 32400 | 23600 | 72.84% | 1.86 | 27000 | R-410A
212361443 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33936 | BGH96M060B3A | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.88 | 19000 | R-410A
212361568 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32(1,2)36+TXV | BGH96M080B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 18400 | R-410A
213249350 | 1.85 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *E7J936+TD |  | 22200 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
214569302 | 2.73 | No | No | MOOVAIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DMA36HOS20230E7 | SL5937 |  | 32800 | 15.2 | 9.5 | 9.3 | 36800 | 31600 | 85.87% | 1.88 | 31800 | R-410A
212596659 | 3.92 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | F,PE*CC4960 |  | 47000 | 15.2 | 10 | 8.4 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
213370126 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E51960+TD |  | 50500 | 15.2 | 9.5 | 8.45 | 51000 | 36800 | 72.16% | 1.78 | 34200 | R-410A
216619283 | 1.8 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | H,RG33936+AEFE3A* |  | 21600 | 16 | 10 | 8.85 | 21400 | 16500 | 77.1% | 2.02 | 15000 | R-410A
212596657 | 2.67 | No | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | BV**C1937 |  | 32000 | 15.2 | 9.5 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
215281573 | 1.75 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | SM6931 |  | 21000 | 16 | 10 | 8.85 | 21400 | 16500 | 77.1% | 2.02 | 15000 | R-410A
212693012 | 1.9 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HG34936+TD |  | 22800 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 14000 | R-410A
212689688 | 1.9 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HE34936+TD |  | 22800 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 14000 | R-410A
214861573 | 1.92 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-24HFN10-M1X | MVBC-24HWFN10-MB1-D |  | 23000 | 18.7 | 12 | 10 | 26000 | 23600 | 90.77% | 2.16 | 16900 | R-454B
213156951 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430U-18HFN1-M | MVBE-18HWFN1-MM3E |  | 18000 | 19.3 | 12.1 | 10.8 | 19000 | 18800 | 98.95% | 2.3 | 15800 | R-410A
213493914 | 2.68 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES080C20SMPS1 | 32200 | 18 | 9.9 | 8.5 | 33200 | 28200 | 84.94% | 2.71 | 25600 | R-410A
213493934 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES100C16LMPS1 | 31200 | 17.8 | 9.3 | 8.3 | 33000 | 28200 | 85.45% | 2.66 | 25600 | R-410A
213494015 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ET100C16LMPS1 | 32200 | 18 | 9.4 | 8.5 | 33200 | 27800 | 83.73% | 2.7 | 25400 | R-410A
213495405 | 2.6 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | Z8ET100C20LMPS1 | 31200 | 18.3 | 9.3 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
212693020 | 2.63 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | HE34936 |  | 31600 | 15.2 | 9 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
212627960 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y100C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
215438161 | 2.82 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | FE*SS9*37+TXV |  | 33800 | 19 | 11.7 | 8.5 | 29400 | 24600 | 83.67% | 2 | 26200 | R-454B
213607927 | 4 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-24WADU | HE86948+AEFE4B* |  | 48000 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
213317994 | 4.5 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | F,PE*UU1960 |  | 54000 | 15.4 | 10 | 9 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
212596656 | 2.58 | No | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | F,PE*E32936 |  | 31000 | 15.2 | 9 | 8.25 | 32200 | 23600 | 73.29% | 1.76 | 21000 | R-410A
214295845 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H***P449 | TM8V060A12MP12 | 34000 | 17 | 9.5 | 8.1 | 32400 | 23800 | 73.46% | 2.04 | 24800 | R-410A
214295815 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*G32924 |  | 23000 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213286697 | 1.95 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | CE2301A+TXV |  | 23400 | 17 | 9.5 | 8.75 | 25600 | 25400 | 99.22% | 2.12 | 18500 | R-410A
214074425 | 2.9 | No | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA36HOS20230E7 | HE32936+TD |  | 34800 | 15.2 | 9.5 | 8.2 | 36200 | 31200 | 86.19% | 1.78 | 26400 | R-410A
213370124 | 4.21 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E50960+TD |  | 50500 | 15.2 | 9.5 | 8.4 | 51000 | 36800 | 72.16% | 1.78 | 34200 | R-410A
203449863 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CP2505A+TXV+TD |  | 22800 | 17 | 12 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213355423 | 2.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E6 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
213355885 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG9J936+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214302679 | 2.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*G33936 |  | 33000 | 18 | 11.7 | 9.2 | 32400 | 23600 | 72.84% | 1.86 | 27000 | R-410A
214505266 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*97MC0603BNA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214073859 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | PL60H210P529+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212555856 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TG52960 |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212406525 | 1.9 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | H,TG34930+TD |  | 22800 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 15800 | R-410A
216035144 | 2.6 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)48B3J+TDR |  | 31200 | 15.2 | 10 | 8.5 | 31000 | 31600 | 101.9% | 2.53 | 27000 | R-454B
213366573 | 1.93 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | HE33930+AEFE3A* |  | 23200 | 16 | 11.7 | 8.95 | 22400 | 21600 | 96.43% | 1.8 | 15000 | R-410A
216990328 | 3.71 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | PL60H210P29*+TXV | 88*TB60090C21*** | 44500 | 18 | 9.5 | 9 | 45500 | 33200 | 72.97% | 2.06 | 41000 | R-454B
216990335 | 3.71 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C48A***L16*+TXV | 88*TB60090C21*** | 44500 | 18 | 9.5 | 9 | 46500 | 33600 | 72.26% | 2.06 | 41500 | R-454B
215934550 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU1002120A* | 45000 | 20.5 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
212361560 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33(1,2)36+TXV | BGH96M060B3A | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.88 | 18400 | R-410A
216488028 | 2.82 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | A36VDA*+TXV | TM9V100C16MP12 | 33800 | 18 | 11 | 8.5 | 29800 | 25200 | 84.56% | 2 | 26800 | R-454B
216488030 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | A36VDA*+TXV | TM9V100C20MP12 | 34000 | 18 | 10.5 | 8.95 | 31000 | 25400 | 81.94% | 1.98 | 25400 | R-454B
213738546 | 2.92 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG33936 | *95MSU0401712A* | 35000 | 15.2 | 9.5 | 8.1 | 37400 | 35000 | 93.58% | 1.82 | 28600 | R-410A
215431125 | 1.83 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU17Z243C | PL36H175P159+AEFE4B* |  | 22000 | 16 | 10 | 9 | 21400 | 16500 | 77.1% | 2.05 | 15000 | R-410A
213249112 | 1.9 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *G34936+TD |  | 22800 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 14000 | R-410A
213753811 | 2.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC6A120M24**22 | 35000 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
214271625 | 2.8 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | PL36H210P299 | 58TN*B045C17**12 | 33600 | 19 | 11.7 | 9 | 35200 | 27400 | 77.84% | 2.02 | 31800 | R-410A
214271684 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | PL36H175P149 | 58TN*B090C17**16 | 32600 | 20 | 12 | 9 | 35000 | 27200 | 77.71% | 2.04 | 31600 | R-410A
213366572 | 1.95 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | HE33936+AEFE4B* |  | 23400 | 17 | 11.7 | 8.95 | 22400 | 21600 | 96.43% | 1.8 | 15000 | R-410A
213738465 | 2.92 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | V,G36H***P449 | *80MS(N,L)0701412A* | 35000 | 16 | 9.5 | 8.1 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
215933940 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1002122B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
212361442 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32936 | BGH96M060B3A | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
212361451 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32936 | BGH96M080B3B | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
216764510 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*DD10AS3 | S8X1C100M5PSC | 51000 | 16 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.1 | 34000 | R-454B
216764933 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8X2B080M4PTC | 31800 | 17.1 | 11.7 | 8.5 | 32000 | 23800 | 74.38% | 2 | 21000 | R-454B
216764953 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S8X2B060M4PSC | 33000 | 17.1 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2 | 21400 | R-454B
216764960 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S8X2B060M4PTC | 33000 | 17.1 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2 | 21400 | R-454B
212627291 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9E060B12MP12 | 33600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627309 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.4 | 34000 | 29400 | 86.47% | 2.71 | 26600 | R-410A
212627324 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627340 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9V060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627342 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627440 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9Y080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627458 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9Y080B12MP11 | 32600 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212617029 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HD19960+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212624527 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624574 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8V080C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624576 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
215588113 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6121AM*+UI | 58TN*B045C17**12 | 48500 | 18 | 11 | 10 | 52500 | 52000 | 99.05% | 2 | 51000 | R-454B
215588165 | 4.17 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 58TN*B110C21**20 | 50000 | 18.5 | 11.5 | 10.5 | 52500 | 53000 | 101% | 1.94 | 50500 | R-454B
212624609 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213370125 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E51960 |  | 47000 | 15.2 | 10 | 8.45 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
212627540 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627576 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLE040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212693023 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | HG52960+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
213249113 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *G52960+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
215413742 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212627593 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.77 | 26200 | R-410A
212396764 | 4.42 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TG52960+TD |  | 53000 | 15.2 | 9.5 | 8.5 | 51000 | 37200 | 72.94% | 1.8 | 35200 | R-410A
215934190 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0902120B* | 45500 | 21.5 | 11.5 | 9.5 | 48500 | 36600 | 75.46% | 2 | 39500 | R-454B
215934240 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0602120B* | 44500 | 20.5 | 10 | 9.4 | 49000 | 37400 | 76.33% | 2 | 40500 | R-454B
212624624 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
215588181 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 59MN7C100C21**22 | 49500 | 18.5 | 11 | 10.5 | 52500 | 53500 | 101.9% | 1.92 | 50500 | R-454B
215588215 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA4921XMA*+UI | 59CU5B080C21**20 | 52000 | 19 | 11.5 | 8.1 | 53500 | 45500 | 85.05% | 1.9 | 48500 | R-454B
212624674 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TMLV100C16MP12 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624676 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TMLV100C16MP12 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
215588231 | 4.25 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6021XMA*+UI | 59MN7C060C21**20 | 51000 | 18.5 | 10.5 | 8.1 | 54000 | 46500 | 86.11% | 1.86 | 49500 | R-454B
212624691 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
214521904 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES040A12LMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
214521936 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ES100C16SMPS1 | 31800 | 17.9 | 9.4 | 8.4 | 33200 | 28200 | 84.94% | 2.68 | 25600 | R-410A
214074426 | 2.95 | No | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA36HOS20230E7 | HG33(1,2)36+TXV+TD |  | 35400 | 15.2 | 9.5 | 8.35 | 36200 | 31200 | 86.19% | 1.8 | 26400 | R-410A
213368026 | 2.82 | No | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-36-O | HE32936+TD |  | 33800 | 15.2 | 9.5 | 8.2 | 36000 | 31200 | 86.67% | 1.78 | 26400 | R-410A
213369637 | 2.82 | No | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-36-O | *E32936+TD |  | 33800 | 15.2 | 9.5 | 8.2 | 36000 | 31200 | 86.67% | 1.78 | 26400 | R-410A
213369639 | 2.88 | No | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-36-O | *G8J936+TD |  | 34600 | 15.2 | 9.5 | 8.45 | 36400 | 31200 | 85.71% | 1.82 | 26400 | R-410A
216619375 | 2.45 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | PL36H***P449+TD |  | 29400 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
213286704 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | CE2505C+TXV |  | 23600 | 17 | 10 | 9 | 25600 | 25200 | 98.44% | 2.14 | 18600 | R-410A
216991841 | 1.85 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | PL36H175P15*+TXV | 88*TB36045C17*** | 22200 | 16 | 10.5 | 8.5 | 19200 | 18100 | 94.27% | 1.96 | 16600 | R-454B
216991880 | 1.88 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | PL36H175P15*+TXV | 912SE36060M14*** | 22600 | 15.2 | 11 | 8.5 | 19400 | 18400 | 94.85% | 1.98 | 16700 | R-454B
216992448 | 3.58 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | H,PG35*48+TXV | 986TD66120C24*** | 43000 | 18 | 9 | 8.95 | 45500 | 33200 | 72.97% | 2.04 | 41000 | R-454B
216992959 | 1.85 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | H,PG7J*36+TXV | 8(0,1)*SB36070M17*** | 22200 | 16 | 10.5 | 8.5 | 19400 | 18800 | 96.91% | 1.96 | 17000 | R-454B
216992961 | 1.83 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | H,PG7J*36+TXV | 8(0,1)*SB42090M17*** | 22000 | 16 | 10.5 | 8.5 | 19400 | 18700 | 96.39% | 1.98 | 17000 | R-454B
213286700 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | CE2903C+TXV |  | 23800 | 17 | 10 | 8.85 | 25600 | 25400 | 99.22% | 2.14 | 18500 | R-410A
214826085 | 2 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YG9J*36+TXV+AEFE4B* |  | 24000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
213369685 | 2.48 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | *G8J936+TD |  | 29800 | 15.2 | 10.5 | 9.5 | 31400 | 26600 | 84.71% | 1.82 | 21600 | R-410A
213771735 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4824AL*+UI | 59TN6C120C24**22 | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
215348774 | 4.21 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | HE49960+TD |  | 50500 | 15.2 | 9.5 | 8.35 | 51000 | 36800 | 72.16% | 1.78 | 34200 | R-410A
212406526 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TG52948+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
215387297 | 3.92 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | F,PE*TT4948 |  | 47000 | 16 | 9.5 | 8.4 | 45000 | 32600 | 72.44% | 1.88 | 30000 | R-410A
212498648 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | CE3005C+TXV |  | 23000 | 16 | 11.5 | 8.8 | 22400 | 21600 | 96.43% | 1.78 | 15000 | R-410A
212396550 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*G33930 |  | 23400 | 17 | 11.5 | 8.95 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
212603198 | 2.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG33936 | *95ESU0601716A* | 24200 | 17 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212603202 | 2.03 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG35936 | *95ESU0601716A* | 24400 | 17 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212396547 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*E32925 |  | 23000 | 16 | 11.5 | 8.85 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
215932160 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X37M17A*+WALLCON | *96CTN0601714B* | 33200 | 19 | 10.5 | 9.5 | 34400 | 26400 | 76.74% | 2.06 | 30400 | R-454B
215932560 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1102120B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.04 | 29800 | R-454B
215932610 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 34000 | 20 | 11.7 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 29800 | R-454B
215932710 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0702120B* | 34400 | 20.5 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.96 | 30000 | R-454B
213368027 | 2.87 | No | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-36-O | HG33936+TD |  | 34400 | 15.2 | 9.5 | 8.3 | 36200 | 31200 | 86.19% | 1.8 | 26400 | R-410A
213356021 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG32924+AEFE4B* |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213362471 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG35936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213362472 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG9J936 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212627642 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TL8E080C16UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27800 | 81.76% | 2.66 | 25600 | R-410A
212627644 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9Y080C16MP11 | 29200 | 17.7 | 8.9 | 8.5 | 34000 | 27800 | 81.76% | 2.66 | 25600 | R-410A
212627657 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627674 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212627693 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627710 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CPLC080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627725 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627759 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8V080C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
216055863 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
213369682 | 2.42 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | *E32936+TD |  | 29000 | 15.2 | 10 | 9.2 | 31200 | 26600 | 85.26% | 1.78 | 21600 | R-410A
213258337 | 1.88 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32936 | *96VTN0401410A* | 22600 | 16 | 9.5 | 8.5 | 24200 | 23800 | 98.35% | 2.02 | 18000 | R-410A
213258338 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG33936 | *96VTN0401410A* | 23000 | 16 | 9.5 | 8.5 | 24000 | 23400 | 97.5% | 1.96 | 17900 | R-410A
213258339 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE33936 | *96VTN0401410A* | 23000 | 16 | 9.5 | 8.5 | 24000 | 23400 | 97.5% | 1.96 | 17900 | R-410A
213258352 | 1.9 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG31930 | *96VTN0601412A* | 22800 | 16 | 9.5 | 8.5 | 24800 | 25200 | 101.6% | 2.14 | 18300 | R-410A
216990759 | 1.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | V,C36H***P03*+TXV | 88*TB36070C14*** | 22000 | 16 | 9.5 | 9 | 22400 | 16500 | 73.66% | 1.94 | 19400 | R-454B
216990321 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C48A***L16*+TXV | 88*TB60070C21*** | 44000 | 17 | 9.5 | 9 | 45500 | 33200 | 72.97% | 2.08 | 41000 | R-454B
216990323 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | PL60H210P17*+TXV | 88*TB60070C21*** | 45000 | 18 | 10 | 9 | 45500 | 33200 | 72.97% | 2.08 | 41000 | R-454B
216990338 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | V,C60H210P17*+TXV | 88*TB60090C21*** | 45000 | 18 | 10 | 9 | 45500 | 33000 | 72.53% | 2.08 | 40500 | R-454B
215934120 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1352422B* | 45000 | 21.5 | 11.5 | 9.5 | 48000 | 36200 | 75.42% | 2 | 39000 | R-454B
215934570 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0901716B* | 44000 | 20.5 | 11.5 | 9 | 49000 | 35800 | 73.06% | 1.86 | 38500 | R-454B
215933720 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712A* | 34200 | 20 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.94 | 30200 | R-454B
215934940 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *96CTN0801714B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 28800 | 74.81% | 2.02 | 33000 | R-454B
213366571 | 1.95 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | HE33930+AEFE4B* |  | 23400 | 17 | 11.7 | 8.95 | 22400 | 21600 | 96.43% | 1.8 | 15000 | R-410A
213370122 | 2.65 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *E35936+TD |  | 31800 | 15.2 | 9 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
213249351 | 2.63 | No | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *G34936 |  | 31600 | 15.2 | 9 | 8.5 | 32400 | 23600 | 72.84% | 1.8 | 21000 | R-410A
212361558 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31(1,2)30+TXV | BGH96M060B3A | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 18400 | R-410A
214295842 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H175P159 | TM8V060A12MP12 | 34000 | 17 | 9.5 | 8.1 | 32400 | 23800 | 73.46% | 2.04 | 24800 | R-410A
215934090 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CSU1002120A* | 44500 | 21 | 11 | 9.5 | 48500 | 36400 | 75.05% | 2 | 39500 | R-454B
215934490 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0802120B* | 44000 | 20 | 10.5 | 9 | 48500 | 36600 | 75.46% | 1.8 | 39500 | R-454B
212627760 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627775 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627777 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212596658 | 1.82 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | SK3925 |  | 21800 | 15.2 | 11 | 8.2 | 22400 | 21200 | 94.64% | 1.76 | 14000 | R-410A
212627792 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TMLV100C16MP12 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627827 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213355886 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG9J936+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212498647 | 1.87 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | CP3005C+TXV+TD |  | 22400 | 15.2 | 10.5 | 8.25 | 22400 | 21200 | 94.64% | 1.76 | 15800 | R-410A
213368028 | 2.88 | No | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-36-O | HG8J936+TD |  | 34600 | 15.2 | 9.5 | 8.45 | 36400 | 31200 | 85.71% | 1.82 | 26400 | R-410A
215934880 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *95CSU0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215935130 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0801714B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 28800 | 74.81% | 2.02 | 33000 | R-454B
215438169 | 2 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | FE*E33*30+TXV |  | 24000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
213206515 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC5B060E14**12 | 23200 | 15.9 | 9.8 | 8.1 | 26000 | 20400 | 78.46% | 2.72 | 19100 | R-410A
213206592 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6B060V14**12 | 23200 | 16.5 | 10 | 8.1 | 26400 | 20400 | 77.27% | 2.69 | 19300 | R-410A
213206601 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6B060V17**14 | 23800 | 16.5 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.78 | 19100 | R-410A
213613379 | 1.9 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24B4 |  | 22800 | 16 | 9.9 | 8.8 | 26400 | 20400 | 77.27% | 2.84 | 19200 | R-410A
213366566 | 1.93 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU36-24WADU | HE33936+AEFE3A* |  | 23200 | 16 | 11.7 | 8.95 | 22400 | 21600 | 96.43% | 1.8 | 15000 | R-410A
213249110 | 1.87 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *G33936+TD |  | 22400 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
215935090 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0602120B* | 35400 | 21 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33400 | R-454B
213355887 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG9J936+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212627842 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627910 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627977 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627995 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214295851 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H210P759 | Z8ES040A12SMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 23800 | 74.84% | 2.1 | 24600 | R-410A
213369681 | 2.38 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | *E31930+TD |  | 28600 | 15.2 | 10 | 9.05 | 31000 | 26600 | 85.81% | 1.76 | 21400 | R-410A
213369613 | 1.87 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | *G33936 |  | 22400 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
212396765 | 4.42 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE86960+TD |  | 53000 | 15.2 | 9.5 | 8.5 | 51000 | 37200 | 72.94% | 1.8 | 35200 | R-410A
212555858 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE86960 |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
214312420 | 2.45 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | V,R36H***P449+TD |  | 29400 | 15.2 | 11 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
212624694 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
215588279 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 59MN7C060C21**20 | 51500 | 18.5 | 11 | 8.1 | 54500 | 46500 | 85.32% | 1.86 | 49000 | R-454B
215588265 | 4.42 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 58CU*A080C21**20 | 53000 | 20 | 12.5 | 8.5 | 53000 | 46000 | 86.79% | 2 | 47500 | R-454B
215588281 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 59MN7C080C21**20 | 52500 | 19.5 | 12 | 8.5 | 53500 | 45500 | 85.05% | 2 | 48000 | R-454B
212624709 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624711 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212361452 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33936 | BGH96M080B3B | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212361559 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32(1,2)36+TXV | BGH96M060B3A | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 18400 | R-410A
214796642 | 2.8 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV+TD |  | 33600 | 15.2 | 10 | 8.5 | 30600 | 23000 | 75.16% | 2 | 27000 | R-454B
214505171 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA2422*4B* | D*80SC0604BUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
216764985 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S8X1C080M5PTC | 33800 | 17.1 | 12 | 8.7 | 33400 | 24400 | 73.05% | 2.1 | 21600 | R-454B
214295846 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | TM8V060A12MP12 | 34000 | 17 | 9.5 | 8.1 | 32400 | 23800 | 73.46% | 2.06 | 24600 | R-410A
212628045 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TL8E100C20UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
214074424 | 2.9 | No | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA36HOS20230E7 | HE32(1,2)36+TXV+TD |  | 34800 | 15.2 | 9.5 | 8.2 | 36200 | 31200 | 86.19% | 1.78 | 26400 | R-410A
216765019 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC007AS3 | S8X1C080M5PTC | 33800 | 17.5 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.1 | 21400 | R-454B
216765042 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D008AS3 | S8X2C100M5PTC | 43500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 2.1 | 30200 | R-454B
216765051 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | S8X1C080M5PTC | 43500 | 17 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29200 | R-454B
216765058 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*DD10AS3 | S8X2D120M5PTC | 43500 | 17.1 | 11.7 | 9 | 44500 | 32600 | 73.26% | 2.1 | 29800 | R-454B
216765083 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | S8X1C100M5PTC | 51000 | 16.5 | 10 | 8.7 | 52000 | 39000 | 75% | 2.1 | 34400 | R-454B
216765085 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | S8X2D120M5PSC | 51500 | 16.5 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
214295850 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H175P159 | Z8ES040A12SMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 23800 | 74.84% | 2.1 | 24600 | R-410A
212627923 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CP9C100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212396546 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*E32930 |  | 23000 | 16 | 11.5 | 8.85 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
212627937 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y080C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627939 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8Y080C16MP11 | 33000 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
215588329 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 59MN7C120C24**22 | 51500 | 19 | 11.5 | 8.1 | 53000 | 46500 | 87.74% | 1.85 | 48000 | R-454B
215588399 | 4.42 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6124XMA*+UI | 58TN*B135C24**22 | 53000 | 20 | 12.5 | 8.5 | 53000 | 46000 | 86.79% | 1.95 | 47500 | R-454B
215588415 | 4.42 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6124XMA*+UI | 59TN6C120C24**22 | 53000 | 19.5 | 12 | 8.5 | 53500 | 46500 | 86.92% | 1.95 | 48000 | R-454B
215588431 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6024AM*+UI | 59TN7A100C21**22 | 49000 | 19 | 11 | 10.5 | 52500 | 53500 | 101.9% | 1.96 | 50500 | R-454B
212624743 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TPLC100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624758 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TL9E080C16UH11 | 30000 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.65 | 25600 | R-410A
212624760 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TL9E080C16UH11 | 30000 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.65 | 25600 | R-410A
213258332 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE33936 | *96VSN1002120A* | 23800 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 17900 | R-410A
213258334 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG31930 | *96VTN0401410A* | 23000 | 15.2 | 9.5 | 8.5 | 25000 | 23600 | 94.4% | 1.96 | 18500 | R-410A
213258357 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE33936 | *96VTN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 24200 | 97.58% | 2.04 | 18300 | R-410A
213258309 | 1.9 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31930 | *96VSN0601412A* | 22800 | 16 | 9.5 | 8.5 | 24800 | 25200 | 101.6% | 2.14 | 18300 | R-410A
213258323 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *96VSN0601714A* | 23800 | 16 | 10 | 8.5 | 25200 | 23600 | 93.65% | 1.98 | 18500 | R-410A
213881422 | 2.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H175P149 | 58TP*B070V17**16 | 34600 | 16 | 9.5 | 8.5 | 36200 | 34400 | 95.03% | 2.02 | 28000 | R-410A
213881424 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H175P159 | 58TP*B070V17**16 | 35200 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
214861544 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBDM-30HWFN10-WB3 |  | 30000 | 17.2 | 12.1 | 10.8 | 33000 | 33200 | 100.6% | 1.97 | 24000 | R-454B
212624775 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TL8E080C16UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624843 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624874 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | CP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624892 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | CP9C100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624893 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | CP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
215348775 | 4.21 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE49960 |  | 50500 | 15.2 | 9.5 | 8.35 | 51000 | 36800 | 72.16% | 1.78 | 34200 | R-410A
212624341 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM8V080C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
216765094 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D010AS3 | S8X2D120M5PSC | 52500 | 16.5 | 11 | 9 | 51000 | 38500 | 75.49% | 2.2 | 34000 | R-454B
216765119 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TXCD010AS3 | S8X1D120M5PTC | 52000 | 16.5 | 11.2 | 8.7 | 51000 | 38500 | 75.49% | 2.2 | 33800 | R-454B
216764783 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D008AS3 | S8X2D120M5PSC | 43500 | 17.1 | 12 | 9 | 44500 | 32800 | 73.71% | 2.2 | 29800 | R-454B
213366574 | 3.96 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-24WADU | HE49948+AEFE5* |  | 47500 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
216764910 | 1.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S8X1B040M2PTC | 22800 | 17.5 | 12.5 | 8.7 | 21600 | 17100 | 79.17% | 1.9 | 15200 | R-454B
216764917 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S8X2A040M3PSC | 23000 | 17.5 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2 | 15300 | R-454B
215934000 | 3.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0702120B* | 43500 | 20.5 | 10.5 | 9.5 | 48000 | 36600 | 76.25% | 2 | 39500 | R-454B
215934050 | 3.58 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0602120B* | 43000 | 20 | 10 | 9.5 | 48500 | 37200 | 76.7% | 1.88 | 40000 | R-454B
215934250 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0801714B* | 44500 | 20.5 | 11 | 9.5 | 49000 | 36600 | 74.69% | 2 | 39500 | R-454B
212627948 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8Y080C16MP11 | 33200 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627971 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8Y100C16MP11 | 33200 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628087 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628098 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9V100C20MP12 | 29600 | 16.9 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628107 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628114 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9V100C20MP12 | 30800 | 17.3 | 9.2 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
213738490 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG81936 | *80MS(N,L)0901714A* | 36000 | 16 | 10.5 | 8.1 | 36800 | 34600 | 94.02% | 2 | 28200 | R-410A
216774744 | 1.85 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | H,TE7J(1,2)36+TXV+TD |  | 22200 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
212544102 | 1.9 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | H,TG34936 |  | 22800 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 15800 | R-410A
216488042 | 2.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | A36VDA*+TXV | Z8ES080B12SMPS1 | 33200 | 18 | 11.7 | 8.5 | 28800 | 24400 | 84.72% | 2 | 25800 | R-454B
213739926 | 1.87 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H***P039 | *96MSN0401410A* | 22400 | 15.2 | 9.5 | 8.5 | 25400 | 24800 | 97.64% | 2.1 | 18500 | R-410A
213739953 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG80936 | *96MSN0601412A* | 23600 | 16 | 10 | 8.5 | 24600 | 23400 | 95.12% | 1.98 | 18100 | R-410A
216681818 | 2.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4824AL* | 927TA60100V21*** | 35800 | 16.5 | 10 | 9 | 38000 | 34200 | 90% | 1.96 | 29000 | R-410A
212628060 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TL8E100C20UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
214295847 | 2.82 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H175P159 | TM8V080B12MP12 | 33800 | 17 | 9.5 | 8.1 | 32400 | 23800 | 73.46% | 2.04 | 24600 | R-410A
214802902 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60C34+TDR | R801V0755A21UH | 45000 | 15.6 | 10.1 | 8.1 | 45500 | 34000 | 74.73% | 3 | 36600 | R-410A
214802918 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D44+TDR | R801V1005A21DZ | 45500 | 15.5 | 10.2 | 8.4 | 46000 | 33800 | 73.48% | 3.1 | 36000 | R-410A
216774742 | 1.87 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | H,TG33(1,2)36+TXV+TD |  | 22400 | 15.2 | 10.5 | 8.4 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
212624408 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM9Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624443 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212624460 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B34+TDR | TM8Y100C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212624475 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | CPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624476 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | CPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
215850950 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
213369684 | 2.45 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | *G7J936+TD |  | 29400 | 15.2 | 10 | 9.35 | 31200 | 26600 | 85.26% | 1.8 | 21600 | R-410A
212396551 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*G33925 |  | 23400 | 17 | 11.5 | 8.95 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
215588499 | 4.42 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 58CU*B100C21**20 | 53000 | 19 | 12 | 8.1 | 53000 | 46000 | 86.79% | 1.85 | 48000 | R-454B
215935200 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0702120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 33200 | R-454B
215935330 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M24A*+WALLCON | *80CSU1002120A* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 33000 | R-454B
215675435 | 3.88 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *97CMN0602120B* | 46500 | 18 | 9.5 | 9 | 50000 | 37000 | 74% | 1.98 | 46000 | R-454B
214312435 | 2.47 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RG1K936+TD |  | 29600 | 15.5 | 11.2 | 9.4 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
213739962 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG80936 | *96VSN0401410B* | 23600 | 16 | 10 | 8.5 | 24600 | 23600 | 95.93% | 1.98 | 18200 | R-410A
213739996 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | V,G36H175P159 | *96VTN0401712B* | 23400 | 16 | 10 | 8.5 | 24600 | 23800 | 96.75% | 2 | 18100 | R-410A
213740001 | 1.87 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H***P039 | *96VTN0601412B* | 22400 | 16 | 9.5 | 8.5 | 25200 | 25000 | 99.21% | 2.12 | 18500 | R-410A
213740003 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG32936 | *96VTN0601412B* | 23200 | 16 | 10 | 8.5 | 25200 | 26400 | 104.8% | 2.28 | 18400 | R-410A
213738540 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG80936 | *92MSN0601714A* | 35600 | 16 | 10 | 8.5 | 36200 | 34400 | 95.03% | 2.02 | 28000 | R-410A
214295848 | 2.82 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H210P759 | TM8V080B12MP12 | 33800 | 17 | 9.5 | 8.1 | 32400 | 23800 | 73.46% | 2.04 | 24600 | R-410A
212614022 | 1.43 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HE20924+TD |  | 17100 | 16 | 11 | 8.65 | 17000 | 14500 | 85.29% | 2.02 | 13500 | R-410A
212361446 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33936 | BGH96M060B3B | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.88 | 19000 | R-410A
214505238 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*80VC0803B*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214505256 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*96SC0603BUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
215932730 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0902120B* | 34400 | 20.5 | 12 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 29800 | R-454B
215932530 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CSU1002120A* | 34000 | 20 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 30000 | R-454B
215934180 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0901716B* | 44500 | 21 | 11.5 | 9.5 | 48500 | 36000 | 74.23% | 2 | 38500 | R-454B
216991844 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | C36A***L15*+TXV | 88*TB36045C17*** | 22200 | 16 | 10.5 | 8.1 | 19200 | 18300 | 95.31% | 1.85 | 16600 | R-454B
216991878 | 1.87 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | C36A***L13*+TXV | 912SE36060M14*** | 22400 | 15.2 | 11 | 8.5 | 19400 | 18400 | 94.85% | 1.98 | 16700 | R-454B
210868917 | 3.71 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF100215LT80X | 44500 | 19 | 11.7 | 8.5 | 43000 | 45000 | 104.7% | 2 | 44500 | R-410A
212396553 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*G34930 |  | 23600 | 17 | 11.5 | 9 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
213752880 | 1.93 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC6A060M14**12 | 23200 | 17 | 9.9 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
216992982 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | H,PG7J*36+TXV | 916SA36060M14*** | 22000 | 15.2 | 10.5 | 8.5 | 19400 | 18800 | 96.91% | 1.98 | 17000 | R-454B
213753033 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6C080V21**20 | 23600 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
214505177 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA2422*4B* | D*80VC0804C*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
215934510 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN1202422B* | 44000 | 20 | 10.5 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
215934610 | 3.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0801714B* | 43500 | 19.5 | 11.5 | 9 | 49000 | 35600 | 72.65% | 1.92 | 37200 | R-454B
212596653 | 3.92 | Yes | No | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | BC**C4960+TD |  | 47000 | 15.2 | 10 | 8.4 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
215588083 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**4821AM*+UI | 59MN7C080C21**20 | 48000 | 18.5 | 10.5 | 12 | 52500 | 52000 | 99.05% | 2.02 | 50500 | R-454B
215588119 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6121AM*+UI | 59MN7C060C21**20 | 49000 | 18.5 | 10 | 10.5 | 54000 | 53500 | 99.07% | 1.88 | 52000 | R-454B
213079423 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4221AL* | 59SC2E060M17**14 | 35200 | 16 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.88 | 29400 | R-410A
213079471 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4217AL* | 59SC2E060M17**14 | 35400 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.94 | 29400 | R-410A
213079741 | 3.05 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3721AL* | 59SC2E100M21**20 | 36600 | 16.5 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.06 | 29000 | R-410A
213079873 | 3.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4321AL* | 59SC2E100M21**22 | 36200 | 16.5 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.04 | 29000 | R-410A
213080375 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3621AL* | 59SC6A100M21**22 | 35000 | 16 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.82 | 29400 | R-410A
212624492 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | CPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624993 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM8Y100C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213187954 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | V,T36H175P139+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
215588217 | 4.25 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA4921XMA*+UI | 59MN7C060C21**20 | 51000 | 18.5 | 10.5 | 8.1 | 54000 | 46500 | 86.11% | 1.86 | 49500 | R-454B
215588283 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 59MN7C100C21**22 | 52500 | 19.5 | 12 | 8.5 | 53500 | 46500 | 86.92% | 1.95 | 48000 | R-454B
215588285 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6124XMA*+UI | 59MN7C120C24**22 | 52500 | 19.5 | 12 | 8.5 | 53500 | 46500 | 86.92% | 1.95 | 48000 | R-454B
215588317 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 58TN*B110C21**20 | 52000 | 19.5 | 12 | 8.5 | 52500 | 46500 | 88.57% | 1.95 | 48000 | R-454B
215588353 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6024XMA*+UI | 58TN*B070C21**20 | 51500 | 19 | 11.5 | 8.1 | 53000 | 47000 | 88.68% | 1.82 | 48500 | R-454B
215588403 | 4.42 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6124XMA*+UI | 59CU5B100C21**22 | 53000 | 19.5 | 12 | 8.1 | 53000 | 46000 | 86.79% | 1.85 | 48000 | R-454B
215588151 | 4.17 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 58CU*A080C21**20 | 50000 | 18.5 | 11.5 | 9.5 | 52000 | 53000 | 101.9% | 1.9 | 50500 | R-454B
210717749 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG48960 | 59TN6B120C24**22 | 44500 | 21 | 12 | 9.5 | 44000 | 35800 | 81.36% | 2.36 | 42000 | R-410A
213369683 | 2.45 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | *G33936+TD |  | 29400 | 15.2 | 10 | 9.35 | 31200 | 26600 | 85.26% | 1.8 | 21600 | R-410A
215588363 | 4.25 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6024XMA*+UI | 59MN7C060C21**20 | 51000 | 18.5 | 10.5 | 8.1 | 53500 | 46500 | 86.92% | 1.86 | 49000 | R-454B
215588381 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6121XMA*+UI | 59CU5B080C21**20 | 52500 | 19 | 11.7 | 8.1 | 53500 | 45500 | 85.05% | 1.9 | 48500 | R-454B
212625026 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8Y100C16MP11 | 33400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625076 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9V100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625092 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625211 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8Y120C20MP11 | 32600 | 18 | 9 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625228 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TL8E100C20UH11 | 29200 | 16.7 | 9.4 | 8.5 | 34000 | 27000 | 79.41% | 2.68 | 25200 | R-410A
215588483 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA6024XMA*+UI | 59TN6C080C21**20 | 51500 | 19 | 11.5 | 8.1 | 53000 | 47000 | 88.68% | 1.85 | 48000 | R-454B
216992996 | 1.8 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | H,PG7J*36+TXV | 986TD60080C21*** | 21600 | 15.2 | 10 | 8.5 | 19200 | 18100 | 94.27% | 1.98 | 16600 | R-454B
212624156 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TP9C080B12MP13 | 31400 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212623992 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM9Y080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624005 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9Y080B12MP11 | 33600 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624091 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8V060A12MP12 | 32400 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624226 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TMLE040A12MP11 | 32000 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624259 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLE080C16MP11 | 31800 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212625243 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TL8E100C20UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625361 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | CP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625411 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM9V100C20MP12 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625428 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625578 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8V100C20MP12 | 29600 | 15.9 | 8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
216766879 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9V2B060U4VSB | 23800 | 17.5 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2.06 | 15500 | R-454B
216737585 | 1.88 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *96MSN1002120A* | 22600 | 15.2 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17800 | R-454B
216737844 | 1.88 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *96VTN0801716B* | 22600 | 16 | 10.5 | 8.1 | 21200 | 18900 | 89.15% | 1.85 | 17800 | R-454B
216738226 | 1.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *80MSU0802120A* | 22600 | 16 | 11 | 8.1 | 20600 | 18400 | 89.32% | 1.85 | 17500 | R-454B
216738471 | 1.88 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *92MSN0801716A* | 22600 | 16 | 10.5 | 8.1 | 20800 | 18400 | 88.46% | 1.85 | 17500 | R-454B
212361561 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31(1,2)30+TXV | BGH96M060B3B | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 18400 | R-410A
214295849 | 2.7 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | TM8V080B12MP12 | 32400 | 17 | 9.5 | 8.1 | 32400 | 23400 | 72.22% | 2 | 25600 | R-410A
212624423 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8E120C16MP11 | 32000 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624441 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE120C16MP11 | 32800 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212624458 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM8Y080C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212614028 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | HG21930+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
212624491 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | CPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624507 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624541 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | CPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624543 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CPLC100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
216734373 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0451714A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
214861554 | 3 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-36HFN10-M3 | MVBC-36HWFN10-MC3E |  | 36000 | 16.2 | 10 | 8.7 | 36000 | 27000 | 75% | 2 | 24800 | R-454B
215588515 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 58CU*B080C21**20 | 52500 | 19.5 | 12 | 8.1 | 52000 | 45500 | 87.5% | 1.9 | 47500 | R-454B
215588549 | 4.38 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6124XMA*+UI | 59TN6C080C21**20 | 52500 | 19.5 | 12 | 8.5 | 53500 | 46500 | 86.92% | 1.95 | 48000 | R-454B
212625596 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625661 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TPLC120C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
213258296 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *96VSN0401410A* | 23200 | 16 | 10 | 8.5 | 24200 | 23800 | 98.35% | 2.02 | 18000 | R-410A
212624557 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TL8E080C16UH11 | 29200 | 16.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213369633 | 2.38 | Yes | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-30-O | *E31930+TD |  | 28600 | 15.2 | 10 | 9.05 | 31000 | 26600 | 85.81% | 1.76 | 21400 | R-410A
213369634 | 2.42 | Yes | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-30-O | *E32936+TD |  | 29000 | 15.2 | 10 | 9.2 | 31200 | 26600 | 85.26% | 1.78 | 21600 | R-410A
212624559 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624577 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM8V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624591 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM8V080C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212406528 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE88948+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212624593 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624625 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8V100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624693 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624708 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TPLC080C16MP13 | 33400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213753620 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30B34+TDR | 59TP6C100V21**22 | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
213258297 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE34936 | *96VSN0401410A* | 23200 | 16 | 10 | 8.5 | 24200 | 23800 | 98.35% | 2.02 | 18000 | R-410A
214861589 | 2.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30-30HFN10-M3X | MVBC-30HWFN10-MC3E-D |  | 30000 | 16.8 | 11.7 | 10 | 34000 | 32600 | 95.88% | 1.96 | 23800 | R-454B
213258228 | 1.49 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG33936 | *96VSN0601412A* | 17900 | 16 | 10.5 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
213258310 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32936 | *96VSN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 25200 | 101.6% | 2.14 | 18300 | R-410A
213258311 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32936 | *96VSN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 25200 | 101.6% | 2.14 | 18300 | R-410A
213258313 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE33936 | *96VSN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 24200 | 97.58% | 2.04 | 18300 | R-410A
212624710 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TPLC100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213258329 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32936 | *96VSN0801716A* | 23800 | 16 | 10 | 8.5 | 25200 | 23000 | 91.27% | 1.92 | 18500 | R-410A
212625663 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625677 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | CPLC100C20MP13 | 32000 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625694 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | CPLC120C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625697 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | CPLC120C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
213258379 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG33936 | *96VTN1002120A* | 23800 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
213258380 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE33936 | *96VTN1002120A* | 23800 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
213258946 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VSN0601714A* | 23800 | 16 | 10 | 8.5 | 25200 | 23600 | 93.65% | 1.98 | 18500 | R-410A
212624794 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TL8E080C16UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624809 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TL8E080C16UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624827 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TL9E080C16UH11 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624943 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8Y080C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624960 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8Y080C16MP11 | 33400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625008 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM8Y100C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213258947 | 2.02 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VSN0801716A* | 24200 | 16 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212625713 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8V100C20MP12 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625728 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8V120C20MP12 | 32200 | 16.5 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625730 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8V120C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625760 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625763 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625028 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625094 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TP9C100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625108 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625145 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625293 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | CP9C100C20MP13 | 29200 | 16.7 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212625312 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TP9C100C20MP13 | 29200 | 16.7 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212625328 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | CP9C100C20MP13 | 29600 | 16.9 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625343 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625779 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625780 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TPLC120C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625796 | 2.4 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9Y120D20MP11 | 28800 | 15.6 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.76 | 25200 | R-410A
212625797 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9Y120D20MP11 | 31600 | 16.5 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625828 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9V120D20MP12 | 29800 | 16.4 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.79 | 25200 | R-410A
212625829 | 2.4 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TP9C120D20MP13 | 28800 | 16.1 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.52 | 25200 | R-410A
212625844 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CP9C120D20MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625845 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | CP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
215821497 | 2.82 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | A36VDA*+TXV+AEFE4B* |  | 33800 | 19 | 11.7 | 8.5 | 29400 | 24600 | 83.67% | 2 | 26200 | R-454B
213362468 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG9J936 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213356018 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG32924+AEFE4B* |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
214295844 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H***P219 | TM8V060A12MP12 | 32800 | 17 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 2.02 | 25000 | R-410A
214295853 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H***P449 | Z8ES040A12SMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 23800 | 74.84% | 2.1 | 24600 | R-410A
216055223 | 3.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | LP9C120D20MP13 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33400 | 75.06% | 2 | 32800 | R-454B
212614016 | 2.38 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | HE31930+TD |  | 28600 | 15.2 | 10 | 9.05 | 31000 | 26600 | 85.81% | 1.76 | 21400 | R-410A
212396763 | 2.78 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | H,TG34936+TD |  | 33400 | 15.2 | 9 | 8.5 | 32400 | 24000 | 74.07% | 1.8 | 22000 | R-410A
212396554 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*G34925 |  | 23600 | 17 | 11.5 | 9 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
214074423 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | HE21924+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
213369674 | 1.43 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | *E20924+TD |  | 17100 | 16 | 11 | 8.65 | 17000 | 14500 | 85.29% | 2.02 | 13500 | R-410A
211260393 | 1.47 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *80VTL0451412A* | 17600 | 16.5 | 10.5 | 8.5 | 18500 | 19100 | 103.2% | 2.3 | 12400 | R-410A
211261330 | 1.49 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L14A* | *95ESN0401410A* | 17900 | 15.5 | 10.5 | 8.5 | 18500 | 18500 | 100% | 2.22 | 12400 | R-410A
214301900 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE9J(1,2)36+TXV | Z8ES120C16LMPS1 | 34000 | 18 | 9.5 | 8.5 | 31800 | 24000 | 75.47% | 2.12 | 24600 | R-410A
213258934 | 1.47 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE7J936 | *96VSN0401712A* | 17600 | 15.2 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.28 | 11500 | R-410A
213258216 | 1.43 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE31930 | *96VSN0401712A* | 17200 | 15.2 | 10 | 8.5 | 17100 | 18700 | 109.4% | 2.28 | 11500 | R-410A
213258223 | 1.41 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE30924 | *96VSN0401712A* | 16900 | 15.2 | 10 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
216766846 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCA001AS3 | S8V2A040M3PCB | 21600 | 15.2 | 11.2 | 10 | 21200 | 16100 | 75.94% | 1.89 | 22000 | R-454B
216734894 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80CSU0601716A* | 23600 | 17 | 11 | 8.5 | 21200 | 18800 | 88.68% | 1.94 | 17900 | R-454B
212361440 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M120D5B | 45000 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361458 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M080B3B | 41500 | 16 | 11.5 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
216735419 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80CSU0401712A* | 23800 | 17.5 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.96 | 17700 | R-454B
207728379 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | F,PE*CC6948 |  | 45500 | 17 | 11.7 | 9.25 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
212361475 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M100C5B | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
215223124 | 1.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PG9J930 | 987MB42060C17*** | 23600 | 16 | 10.5 | 8.1 | 19400 | 16300 | 84.02% | 2 | 19600 | R-410A
215223135 | 1.95 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE7J936 | 987MB66120C24*** | 23400 | 16 | 10.5 | 8.1 | 19800 | 16300 | 82.32% | 1.96 | 19800 | R-410A
212625861 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9V120D20MP12 | 32400 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625877 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625911 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9V040A10MP12 | 31400 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625912 | 2.42 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9V040A10MP12 | 29000 | 16.3 | 9 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625930 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9V040A10MP12 | 30400 | 16.7 | 9 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
213258230 | 1.49 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG34936 | *96VSN0601412A* | 17900 | 16 | 10.5 | 8.5 | 16900 | 18100 | 107.1% | 2.22 | 11400 | R-410A
216734403 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0701716A* | 22400 | 16 | 11 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
211656177 | 2.93 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AFM474+TDR |  | 35200 | 18 | 9 | 8.1 | 36000 | 26000 | 72.22% | 2.81 | 25200 | R-410A
213355440 | 2.93 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48D6 |  | 35200 | 18 | 9 | 8.2 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
212614018 | 2.45 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | HG7J936+TD |  | 29400 | 15.2 | 10 | 9.35 | 31200 | 26600 | 85.26% | 1.8 | 21600 | R-410A
212361594 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M120D5A | 44500 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34000 | R-410A
213258219 | 1.48 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG33936 | *96VSN0401712A* | 17700 | 15.2 | 10.5 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
213258222 | 1.48 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE34936 | *96VSN0401712A* | 17700 | 15.2 | 10.5 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
215941023 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1002122A* | 44500 | 21 | 11 | 9.5 | 48000 | 36400 | 75.83% | 2 | 39000 | R-454B
216734414 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0901714A* | 22400 | 16 | 11 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
216734545 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *95CSU0601716B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734563 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *97CMN0801714B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18600 | 89.42% | 1.85 | 17500 | R-454B
213369679 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | *G21924+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
213249109 | 3.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | *E49960+TD |  | 47000 | 15.2 | 10 | 8.35 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
216678750 | 2.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CSPH*3612AL* | 59TP7A060V17**16 | 35600 | 15.2 | 9.5 | 8.5 | 38500 | 34600 | 89.87% | 1.8 | 29400 | R-410A
216734334 | 1.88 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | OMV112K14A | 22600 | 15.5 | 10.5 | 8.5 | 21400 | 19100 | 89.25% | 1.96 | 18000 | R-454B
216734625 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96MSN0261410A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
212361582 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M080C4A | 41000 | 16 | 11 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 33400 | R-410A
213872343 | 2.73 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 31800 | 23000 | 72.33% | 2.04 | 25000 | R-410A
215487371 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*96VC0804CNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
213753020 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6C060V17**16 | 23200 | 16.5 | 10 | 8.5 | 26800 | 20400 | 76.12% | 2.88 | 19400 | R-410A
212361492 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M120D5B | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361583 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 33400 | R-410A
212361585 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 33400 | R-410A
216681338 | 2.55 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CAP**4321AL* | 59TP7A080V21**20 | 30600 | 15.2 | 9 | 9 | 33000 | 26000 | 78.79% | 1.78 | 23200 | R-410A
212625446 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625459 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625463 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625511 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | CPLC120C20MP13 | 28600 | 15.6 | 8.4 | 8.1 | 32000 | 27600 | 86.25% | 2.44 | 25000 | R-410A
212625644 | 2.42 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8V100C20MP12 | 29000 | 15.8 | 8.5 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625646 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8V100C20MP12 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625679 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CPLC100C20MP13 | 32600 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625710 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V100C20MP12 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
215487365 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*80VC0804C*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487376 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3626*3A* | D*80VC0804C*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
214575728 | 1.78 | Yes | No | MOOVAIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DMA24HOS20230E7 | SK1925 |  | 21400 | 16 | 10 | 8.35 | 22800 | 19600 | 85.96% | 1.76 | 19800 | R-410A
214074421 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | HG21(1,2)24+TXV+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
213369678 | 1.87 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | *E20924+TD |  | 22400 | 16 | 10 | 8.6 | 23000 | 19600 | 85.22% | 1.8 | 19800 | R-410A
212361441 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31930 | BGH96M060B3A | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 19000 | R-410A
213370121 | 1.92 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU36-24WADU | *E35936 |  | 23000 | 15.2 | 11 | 8.5 | 22400 | 21200 | 94.64% | 1.8 | 14000 | R-410A
215727926 | 3.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36(1,2)60+TXV | TM8V080C16MP12 | 43000 | 17 | 11.5 | 8.4 | 42000 | 32800 | 78.1% | 1.98 | 31200 | R-454B
212625711 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8V100C20MP12 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625744 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLV120C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625777 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625778 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625794 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TPLC120C20MP13 | 30400 | 16.1 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625878 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
216735105 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *97CMN0801714B* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
212626031 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8Y060A12MP11 | 32400 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626044 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8Y060A12MP11 | 33200 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212361432 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M080B3B | 41500 | 16 | 11.5 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
215727933 | 3.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48(1,2)60+TXV | TM8V120C20MP12 | 44000 | 18 | 11.7 | 8.5 | 42500 | 33200 | 78.12% | 2 | 32000 | R-454B
215727944 | 4.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36(1,2)60+TXV | TM9E080C20MP12 | 52000 | 18 | 10.5 | 8.3 | 53000 | 39500 | 74.53% | 1.96 | 37000 | R-454B
215727967 | 3.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48(1,2)60+TXV | TM9Y120D20MP11 | 44000 | 18 | 11.7 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31400 | R-454B
212498649 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | CE2505C+TXV |  | 23000 | 16 | 11.5 | 8.8 | 22400 | 21600 | 96.43% | 1.78 | 15000 | R-410A
212396548 | 1.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | F,PE*E32924 |  | 22800 | 16 | 11.5 | 8.85 | 22400 | 21200 | 94.64% | 1.8 | 15000 | R-410A
215383023 | 3.38 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG72948+TD |  | 40500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
215931700 | 4.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0902120B* | 57000 | 19 | 11.5 | 8.5 | 60500 | 46500 | 76.86% | 2.04 | 47500 | R-454B
215932000 | 2.57 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X30M14A*+WALLCON | *96CTN0401410B* | 30800 | 17 | 10 | 9 | 34400 | 26600 | 77.33% | 1.9 | 30400 | R-454B
211261414 | 1.51 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L14A* | *95ESN0261410A* | 18100 | 15.5 | 10.5 | 8.5 | 18800 | 18500 | 98.4% | 2.22 | 12500 | R-410A
211262100 | 1.49 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *92ESN0601714A* | 17900 | 16.5 | 10.5 | 8.5 | 18300 | 18500 | 101.1% | 2.22 | 12300 | R-410A
212361431 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M080B3A | 41500 | 16 | 11.5 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
212361464 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212361479 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M100D5A | 45000 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212361481 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M100D5B | 44500 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212361578 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M080B3A | 41000 | 16 | 11 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 33400 | R-410A
212625914 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9V040A10MP12 | 29600 | 16.4 | 9 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625963 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9E100C20MP12 | 33200 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626029 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626045 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626062 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8Y120C20MP11 | 31200 | 17.9 | 9.3 | 8.1 | 33400 | 29800 | 89.22% | 2.75 | 26600 | R-410A
212626079 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8Y080B12MP11 | 33000 | 18 | 10 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626063 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9E100C16MP12 | 30400 | 17.5 | 9 | 8.4 | 33400 | 27400 | 82.04% | 2.62 | 25200 | R-410A
212626163 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9V080B12MP12 | 31400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.61 | 26400 | R-410A
212626213 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.62 | 25800 | R-410A
212626263 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626265 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626314 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM8E100B12MP11 | 32000 | 17.9 | 9.9 | 8.3 | 33600 | 27600 | 82.14% | 2.61 | 25400 | R-410A
212626331 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8E100B12MP11 | 30400 | 17.5 | 9 | 8.4 | 33600 | 27600 | 82.14% | 2.61 | 25400 | R-410A
214074422 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | HE21(1,2)24+TXV+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
215932150 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X37M17A*+WALLCON | *96CTN0401410B* | 32200 | 17.5 | 10.5 | 9 | 34000 | 26200 | 77.06% | 1.96 | 30000 | R-454B
215932370 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CMN0601714B* | 33800 | 19.5 | 11 | 9.5 | 34200 | 26200 | 76.61% | 2.06 | 30000 | R-454B
215932050 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0601716A* | 32200 | 19.5 | 11 | 9.5 | 35000 | 27000 | 77.14% | 2 | 30800 | R-454B
215933170 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN0601714B* | 33000 | 18.5 | 10.5 | 9 | 34400 | 26200 | 76.16% | 1.92 | 30200 | R-454B
212626380 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9E100C16MP12 | 32200 | 18 | 9.9 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626415 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8Y100C20MP11 | 31200 | 17.9 | 9.3 | 8.4 | 33600 | 30000 | 89.29% | 2.83 | 26800 | R-410A
212626648 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.3 | 33800 | 29600 | 87.57% | 2.7 | 26600 | R-410A
212626764 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9V080B12MP12 | 31800 | 17 | 9 | 8.4 | 33800 | 29600 | 87.57% | 2.72 | 26600 | R-410A
212626765 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9V080B12MP12 | 31800 | 17 | 9 | 8.4 | 33800 | 29600 | 87.57% | 2.72 | 26600 | R-410A
212626781 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9E080B12MP12 | 31600 | 17.5 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212626798 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8E080C16MP11 | 32200 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.73 | 26000 | R-410A
212626832 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9E080B12MP12 | 32200 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
214074419 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HG21(1,2)18+TXV+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
214575727 | 1.35 | Yes | Yes | MOOVAIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DMA18HOS20230E7 | SK1925 |  | 16200 | 16 | 11 | 8.4 | 16900 | 14500 | 85.8% | 1.98 | 13500 | R-410A
213258217 | 1.46 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *96VSN0401712A* | 17500 | 15.2 | 10 | 8.5 | 17100 | 18700 | 109.4% | 2.28 | 11500 | R-410A
213258226 | 1.48 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *96VSN0601412A* | 17700 | 16 | 10 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
215588351 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6024XMA*+UI | 58CU*A100C21**20 | 51500 | 19 | 11.5 | 8.1 | 53000 | 46500 | 87.74% | 1.85 | 48000 | R-454B
215588435 | 4.17 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6121AM*+UI | 58CU*B040C17**12 | 50000 | 19 | 12 | 10 | 52000 | 51500 | 99.04% | 1.96 | 50000 | R-454B
213203988 | 1.43 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | D(A,C,E)24B44+TDR | *95ESN0601412A* | 17200 | 16.4 | 10.8 | 8.5 | 18300 | 14000 | 76.5% | 2.3 | 14300 | R-410A
212614021 | 1.43 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HE20918+TD |  | 17100 | 16 | 11 | 8.65 | 17000 | 14500 | 85.29% | 2.02 | 13500 | R-410A
212614023 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HG21918+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
215487372 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*96VC1005CNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487387 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CHPEA3026*3A* | D*80VC0804C*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487419 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CA*EA6030*3A* | D*96VC0804CNA* | 40500 | 16.5 | 10 | 8.8 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215487403 | 2.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA6030*3A* | D*80VC1005C*A* | 35000 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216766877 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S8V2B060M4PCB | 23600 | 17.1 | 12.7 | 8.7 | 21800 | 17300 | 79.36% | 2.03 | 15400 | R-454B
212406527 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE86948+TD |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212396766 | 4.42 | No | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE88960+TD |  | 53000 | 15.2 | 9.5 | 8.5 | 51000 | 37200 | 72.94% | 1.8 | 35200 | R-410A
213281444 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V48H175P159+AEFE4B* |  | 44500 | 18 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
216488063 | 2.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | A36VDA*+TXV | Z9ES080C20SMPS1 | 34200 | 18 | 11 | 8.5 | 30600 | 26000 | 84.97% | 2 | 27600 | R-454B
216735446 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80CSU1002120A* | 23800 | 16.5 | 11 | 8.5 | 21400 | 18900 | 88.32% | 1.96 | 18000 | R-454B
216734451 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80VSL0901716B* | 22200 | 16.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734594 | 1.88 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *92MSN0601412A* | 22600 | 15.5 | 11 | 8.5 | 21000 | 18800 | 89.52% | 1.98 | 17700 | R-454B
216734603 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *92MSN0601714A* | 22400 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
216734667 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96MSN0601716A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734735 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *95MSU0401712A* | 22400 | 16 | 10.5 | 8.5 | 21000 | 18800 | 89.52% | 1.96 | 17700 | R-454B
216735003 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80MSU0401712A* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
212361467 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M080C4B | 42000 | 17 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213771665 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4821AL*+UI | 59TN6C100C21**22 | 24000 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
212361435 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M100C5A | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
215933950 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1202422B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
215935170 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU1002120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 32800 | R-454B
216800683 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG84*60+TXV | BGH96M100C5C | 44500 | 16 | 10.5 | 8.5 | 45000 | 32600 | 72.44% | 1.85 | 33000 | R-454B
212614025 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HG21930+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
214074420 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HG21(1,2)24+TXV+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
216766857 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8V2B080M4PDB | 23200 | 17 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2 | 15300 | R-454B
213368020 | 1.48 | Yes | Yes | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-18-O | HG21924+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
212626179 | 2.63 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9Y100C16MP11 | 31600 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.63 | 25800 | R-410A
212626211 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.62 | 25800 | R-410A
212626212 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.62 | 25800 | R-410A
212626345 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM9V080C16MP12 | 31800 | 17.5 | 9.9 | 8.3 | 33600 | 27600 | 82.14% | 2.63 | 25400 | R-410A
212626915 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8E100B12MP11 | 30400 | 17.5 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626917 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626947 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TMLE060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626964 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TMLE100B12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212627641 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TL8E080C16UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27800 | 81.76% | 2.66 | 25600 | R-410A
212627643 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TL8E080C16UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27800 | 81.76% | 2.66 | 25600 | R-410A
212627694 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CPLC080C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
204802864 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | F,PE*TT1948 |  | 46500 | 17 | 11.7 | 9.45 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
212361595 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M120D5A | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34000 | R-410A
212614020 | 2.88 | No | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA36HOS20230E7 | HG8J936+TD |  | 34600 | 15.2 | 9.5 | 9.8 | 37400 | 31600 | 84.49% | 1.96 | 32000 | R-410A
215487363 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*80VC0603B*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487379 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3626*3A* | D*96VC0403BNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
213369675 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | *G21918+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
213369677 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | *G21930+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
212626966 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TMLE100B12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626981 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.2 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212627016 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.3 | 33800 | 29200 | 86.39% | 2.78 | 26400 | R-410A
212627032 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627081 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TP9C080C16MP13 | 30800 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627082 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627098 | 2.8 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TP9C080C16MP13 | 33600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212626365 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9E100C16MP12 | 32400 | 18 | 9.9 | 8.4 | 33600 | 27200 | 80.95% | 2.64 | 25200 | R-410A
212626850 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E080B12MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626865 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.2 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626881 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9Y100C20MP11 | 32200 | 15.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.38 | 25400 | R-410A
216735295 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96CTN0601714B* | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216735145 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *92MSN0601714A* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
213752462 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC6A060M14**12 | 23200 | 16 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.9 | 19700 | R-410A
213369676 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | *G21924+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
212614024 | 1.48 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | HG21924+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
208106494 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P199 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
216680862 | 1.45 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 59TP7A080V17**16 | 17400 | 16 | 10.5 | 8.5 | 17900 | 18300 | 102.2% | 2.14 | 12200 | R-410A
216990644 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | PL48H210P75*+TXV | 88*TB60090C21*** | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 1.92 | 38000 | R-454B
215224765 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG49960 | 59MN7C080C21**20 | 44500 | 21 | 12 | 9 | 44500 | 36000 | 80.9% | 2.26 | 42500 | R-410A
212626381 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9E100C16MP12 | 29400 | 17.2 | 9.4 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626396 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9E100C16MP12 | 30800 | 17.7 | 9 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626563 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.66 | 25800 | R-410A
212626599 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.68 | 25800 | R-410A
212626681 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM8E080B12MP11 | 31800 | 17.9 | 9.4 | 8.3 | 33800 | 28200 | 83.43% | 2.59 | 25800 | R-410A
212626863 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.2 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626882 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
215934660 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X30M17A*+WALLCON | *96CTN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
215934910 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CMN0801714B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33200 | R-454B
215588437 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6121AM*+UI | 58CU*B060C17**16 | 49500 | 19 | 12 | 10 | 52000 | 51500 | 99.04% | 2 | 50000 | R-454B
215588451 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*6012AM*+UI | 58CU*B060C17**16 | 49500 | 18.5 | 11.5 | 10 | 51500 | 50500 | 98.06% | 2 | 50000 | R-454B
215588519 | 4.29 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA4924XMA*+UI | 59TN7A080C21**20 | 51500 | 19 | 11.5 | 8.1 | 53000 | 46500 | 87.74% | 1.85 | 48000 | R-454B
215588553 | 4.42 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAVA6124XMA*+UI | 58CU*B100C21**20 | 53000 | 19.5 | 12 | 8.1 | 53000 | 46000 | 86.79% | 1.85 | 48000 | R-454B
214779006 | 4.42 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-4860AA* | HG88960+AEFE5* |  | 53000 | 18 | 11.5 | 9.5 | 53000 | 38000 | 71.7% | 1.9 | 42500 | R-410A
212626897 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8E060A12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626899 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8E060A12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
216734805 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VTN0601412B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216498593 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H175P149 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212627758 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8V080C16MP12 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627791 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627808 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TMLV100C16MP12 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627809 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLV100C16MP12 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627841 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627843 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
215675345 | 3.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | FCMA5B60L0D*+WALLCON |  | 46500 | 19.5 | 10.5 | 9.5 | 47000 | 33000 | 70.21% | 2.2 | 41000 | R-454B
216011839 | 2.82 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | CP9C060B12MP13 | 33800 | 17 | 9.5 | 8.5 | 31800 | 23400 | 73.58% | 2.04 | 24400 | R-410A
213752601 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6C080V21**20 | 23800 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
216735237 | 1.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VSN0601412B* | 22600 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216735335 | 1.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VTN0601412B* | 22600 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216736682 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *96VSN0601412B* | 22400 | 15.2 | 10.5 | 8.1 | 21200 | 19100 | 90.09% | 1.9 | 17900 | R-454B
215224768 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG48960 | 59MN7C120C24**22 | 44500 | 21 | 12 | 9.5 | 44000 | 35800 | 81.36% | 2.34 | 42000 | R-410A
212624056 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | CPLC060A12MP13 | 31600 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
213258308 | 1.9 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG31930 | *96VSN0601412A* | 22800 | 16 | 9.5 | 8.5 | 24800 | 25200 | 101.6% | 2.14 | 18300 | R-410A
213258340 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *96VTN0401410A* | 23200 | 16 | 10 | 8.5 | 24200 | 23800 | 98.35% | 2.02 | 18000 | R-410A
213258367 | 2 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *96VTN0601714A* | 24000 | 16 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.88 | 18100 | R-410A
213258381 | 2 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *96VTN1002120A* | 24000 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
213258951 | 1.97 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VTN0601714A* | 23600 | 16 | 10 | 8.5 | 25200 | 24000 | 95.24% | 2.02 | 18400 | R-410A
212624108 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLV060A12MP12 | 31600 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624109 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TMLV060A12MP12 | 31600 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624123 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624159 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TP9C080B12MP13 | 32200 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624190 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9Y100C20MP11 | 30800 | 15.2 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624191 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9Y100C20MP11 | 33400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624224 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLE040A12MP11 | 32000 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624241 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
216498594 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H175P159 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215668981 | 2.87 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL0701716B* | 34400 | 18 | 10 | 8.1 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215668997 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL0901716B* | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
213369680 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | *G21930+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
213369673 | 1.43 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA18HOS20230E7 | *E20918+TD |  | 17100 | 16 | 11 | 8.65 | 17000 | 14500 | 85.29% | 2.02 | 13500 | R-410A
216738562 | 1.9 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *96MSN0801716A* | 22800 | 15.2 | 10.5 | 8.1 | 20800 | 18600 | 89.42% | 1.9 | 17600 | R-454B
216739030 | 1.92 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | FHMA5*24L*B* |  | 23000 | 15.5 | 11 | 8.5 | 21400 | 19200 | 89.72% | 1.98 | 18000 | R-454B
216737276 | 1.88 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80CTL0701716B* | 22600 | 16 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
215487383 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3626*3A* | D*96VC1005CNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487426 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA4830*3A* | D*80VC1005C*A* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215487433 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA6030*3A* | D*80VC0805D*A* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215487435 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA6030*3A* | D*96VC0804CNA* | 40500 | 16.5 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
212498646 | 1.87 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2036A10NU** | CP2505C+TXV+TD |  | 22400 | 15.2 | 10.5 | 8.25 | 22400 | 21200 | 94.64% | 1.76 | 15800 | R-410A
215935340 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M24A*+WALLCON | *80CTL0702120B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 33000 | R-454B
214855374 | 3.38 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z483C | H,RG48960+TD |  | 40500 | 15.2 | 11 | 8.55 | 40000 | 34200 | 85.5% | 1.94 | 30200 | R-410A
214861567 | 4.5 | Yes | No | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-60HFN10-M2X | MVBC-60HWFN10-MD2 |  | 54000 | 15.4 | 10 | 9.2 | 59000 | 53000 | 89.83% | 2 | 41000 | R-454B
216764851 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S8X2D120M5PTC | 51500 | 16.5 | 11 | 9 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
216764883 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8X2C100M5PSC | 51000 | 16 | 11 | 9 | 51000 | 38500 | 75.49% | 2.1 | 34000 | R-454B
216764885 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8X2D120M5PSC | 51000 | 16.5 | 11 | 8.7 | 51000 | 38500 | 75.49% | 2.1 | 33800 | R-454B
213753806 | 2.83 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC6A100M21**22 | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.71 | 29000 | R-410A
213352690 | 1.43 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L139 | 59TP6C040V14**10 | 17100 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
216736759 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *95MSU0802120A* | 22400 | 15.2 | 10.5 | 8.1 | 21200 | 19100 | 90.09% | 1.85 | 17800 | R-454B
216736907 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *97VTN0601716A* | 22400 | 15.2 | 10.5 | 8.1 | 21200 | 19100 | 90.09% | 1.85 | 17900 | R-454B
216736939 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *97VTN1002120A* | 22400 | 15.5 | 10.5 | 8.1 | 21200 | 19100 | 90.09% | 1.85 | 17800 | R-454B
212614027 | 1.92 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | HG21924+TD |  | 23000 | 16 | 10 | 8.8 | 23000 | 19600 | 85.22% | 1.84 | 19800 | R-410A
216011844 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE32936 | CP9C080C16MP13 | 32800 | 17 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 2.04 | 25200 | R-410A
212498518 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CE2903A+TXV |  | 29400 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
215487381 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3626*3A* | D*96VC0803BNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487394 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CHPEA3026*3A* | D*96VC1005CNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
212627941 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627959 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8Y100C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628026 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212628028 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212628044 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TL8E100C20UH11 | 29200 | 16.7 | 9.4 | 8.5 | 34000 | 27000 | 79.41% | 2.68 | 25200 | R-410A
212628058 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TL8E100C20UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
215669265 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0601714B* | 33600 | 17.5 | 9.5 | 9 | 35200 | 25400 | 72.16% | 1.88 | 30600 | R-454B
215935070 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *95CSU0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
216011846 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE34936 | CP9C080C16MP13 | 32800 | 17 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 2.04 | 25200 | R-410A
215487367 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*80VC1005C*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487417 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CA*EA6030*3A* | D*80VC0805D*A* | 40500 | 17 | 10 | 8.8 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
212626401 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9E100C16MP12 | 31200 | 17.8 | 9.7 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626619 | 2.63 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9Y100C16MP11 | 31600 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.69 | 26000 | R-410A
212626667 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9E060A10MP12 | 32600 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626678 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9E060A10MP12 | 33200 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626835 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9E080B12MP12 | 30000 | 16.9 | 9.5 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626842 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9E080B12MP12 | 30400 | 17 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626867 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212624291 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212596648 | 3.79 | Yes | No | TOSOT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | TU60-48WADU | M60E499+TD |  | 45500 | 15.2 | 10 | 8.35 | 46000 | 33200 | 72.17% | 1.78 | 30200 | R-410A
212624306 | 2.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8E100C16MP11 | 32200 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.76 | 26000 | R-410A
213411112 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG35936 | Z8ET100C20LMPS1 | 34000 | 18 | 9.5 | 8.5 | 31800 | 23800 | 74.84% | 2.14 | 24400 | R-410A
212624326 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212396759 | 3.88 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2060A10NU** | BV**C9(1,2)60+TXV |  | 46500 | 15.2 | 9.5 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
212627755 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627771 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8V100C16MP12 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627814 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TPLC080C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627821 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TPLC080C16MP13 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627848 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627862 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627896 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TL9E080C16UH11 | 32800 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627907 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.4 | 34000 | 30200 | 88.82% | 2.83 | 27000 | R-410A
215669185 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0601716B* | 33600 | 17.5 | 9.5 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
215669535 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0601714B* | 34400 | 18 | 10 | 9 | 34600 | 25200 | 72.83% | 1.9 | 30200 | R-454B
212626878 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9Y100C20MP11 | 32200 | 15.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.38 | 25400 | R-410A
212626894 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626903 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8E060A12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626919 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8E100B12MP11 | 30400 | 17.5 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626928 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TMLE060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626962 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TMLE100B12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212627037 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | CP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627053 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
216991427 | 1.98 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MURAQ24AA3 | C36A***L13*+TXV | 912SE36060M14*** | 23800 | 15.2 | 10 | 8.5 | 22400 | 19000 | 84.82% | 1.92 | 17900 | R-454B
213369631 | 1.48 | Yes | Yes | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-18-O | *G21924+TD |  | 17700 | 16 | 11.5 | 8.85 | 17100 | 14600 | 85.38% | 2.06 | 13600 | R-410A
216011837 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE33936 | CP9C060B12MP13 | 32600 | 17 | 9.5 | 8.1 | 32000 | 23200 | 72.5% | 2.02 | 25400 | R-410A
215223131 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE9J936 | 987MB60060C21*** | 23600 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.96 | 19800 | R-410A
212394497 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE32936 | TM9E080C16MP12 | 33000 | 18 | 10 | 8.5 | 32400 | 22800 | 70.37% | 2.04 | 25200 | R-410A
212394524 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | TM9V100C16MP12 | 34000 | 17 | 10 | 8.5 | 32400 | 23600 | 72.84% | 2.1 | 24400 | R-410A
212394540 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE34936 | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.5 | 32400 | 23000 | 70.99% | 2.04 | 25000 | R-410A
216737783 | 1.9 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *96CTN1002122B* | 22800 | 15.2 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.9 | 17800 | R-454B
212555859 | 3.92 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | H,TE88960 |  | 47000 | 15.2 | 10 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
216974476 | 4.58 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | V,C60H210P17*+TXV | 83*CA60080C21*** | 55000 | 18 | 9 | 8.5 | 57000 | 41000 | 71.93% | 2.02 | 49500 | R-454B
213366557 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | A36VCA+TXV | Z8ET080B12LMPS1 | 33200 | 18 | 9.5 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
213366560 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG34936 | Z8ET080B12LMPS1 | 33200 | 18 | 9.5 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
216488095 | 3.79 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | A60VGA*+TXV | Z9ES100C16SMPS1 | 45500 | 18 | 11.7 | 9 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
213771487 | 2.03 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X43L21A*+WALLCON | *95CSU0601716B* | 24400 | 16.5 | 10.5 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213770517 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X24L17A*+WALLCON | *80CTL0901716B* | 23400 | 16.5 | 10.5 | 8.1 | 21800 | 16800 | 77.06% | 1.9 | 21000 | R-410A
212628109 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9V100C20MP12 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628126 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628127 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628128 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
216734815 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VTN0601716B* | 22400 | 16 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
216735367 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *97VTN0601716A* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
212624007 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627921 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627932 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8Y080C16MP11 | 29200 | 17.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627946 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8Y080C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627957 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8Y100C16MP11 | 29800 | 17.8 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627980 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9V100C16MP12 | 29800 | 16.9 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628005 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628071 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9V100C20MP12 | 30000 | 17 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.69 | 25800 | R-410A
212628073 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TP9C100C20MP13 | 29200 | 16.7 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
216679722 | 1.47 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 59TP7A060V17**16 | 17600 | 16 | 10.5 | 8.5 | 18100 | 18300 | 101.1% | 2.12 | 12200 | R-410A
215223197 | 2.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | H,PE9J936 | 987MB66100C21*** | 32000 | 17 | 11.5 | 8.5 | 31000 | 24600 | 79.35% | 1.98 | 30400 | R-410A
215223198 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | H,PG35936 | 987MB66120C24*** | 31800 | 17 | 11.5 | 8.5 | 31000 | 24600 | 79.35% | 1.98 | 30400 | R-410A
215487406 | 2.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA6030*3A* | D*80VC0804C*A* | 35000 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
212441665 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE8J936 | TM9Y080B12MP11 | 32800 | 17 | 9.5 | 8.5 | 32400 | 23400 | 72.22% | 2.02 | 25800 | R-410A
215487405 | 2.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA6030*3A* | D*80VC0805C*A* | 35000 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216986083 | 1.95 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MURAQ24AA3 | C36A***L15*+TXV | 926SB36040V17*** | 23400 | 15.2 | 9.5 | 8.5 | 22000 | 18900 | 85.91% | 1.96 | 17800 | R-454B
216011849 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE33936 | CP9C100C16MP13 | 33200 | 17 | 10 | 8.5 | 31400 | 22800 | 72.61% | 2.06 | 25400 | R-410A
215487478 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80VC0803B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215487461 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA6030*3A* | D*96VC1005DNA* | 45500 | 16.5 | 10 | 8.5 | 46500 | 33600 | 72.26% | 2 | 29000 | R-32
212520374 | 2.53 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | H,PG34936 | 58SU*A040E17**12 | 30400 | 15.2 | 9 | 8.1 | 32600 | 26600 | 81.6% | 1.8 | 22400 | R-410A
213770617 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X25L17A*+WALLCON | *80CTL0901716B* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
213770717 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X30L17A*+WALLCON | *80CTL0701412B* | 23600 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213782030 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X42AAL+WALLCON | *96CTN1002122B* | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
213782350 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X60AAL+WALLCON | *96CTN1002122B* | 33000 | 16.5 | 11.5 | 8.1 | 32200 | 24800 | 77.02% | 2 | 31200 | R-410A
212628116 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
213771705 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CAP**4824AL*+UI | 59MN7C100C21**22 | 24200 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
212626876 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.2 | 33800 | 30000 | 88.76% | 2.77 | 26800 | R-410A
212626910 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8E100B12MP11 | 30800 | 17.7 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626935 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLE060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626937 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626944 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TMLE060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626946 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLE060A12MP11 | 32800 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626953 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626971 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLE100B12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626994 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TL8E080C16UH11 | 31800 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212627712 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627721 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
215438162 | 3.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | FE*BB9*48+TXV |  | 45000 | 18 | 11.7 | 8.8 | 44000 | 33600 | 76.36% | 2.06 | 34600 | R-454B
215224760 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG7J936 | 59MN7C100C21**22 | 23000 | 20 | 13 | 10.5 | 25000 | 19400 | 77.6% | 2.46 | 23800 | R-410A
214505271 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*97MC1005CNA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
213258220 | 1.48 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE33936 | *96VSN0401712A* | 17700 | 15.2 | 10.5 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
213258236 | 1.46 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE32936 | *96VSN0601714A* | 17500 | 16 | 10 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11400 | R-410A
215487401 | 2.9 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA4830*3A* | D*80VC0805C*A* | 34800 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
215669365 | 2.85 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0602120B* | 34200 | 18 | 10 | 9 | 34400 | 25000 | 72.67% | 1.9 | 30000 | R-454B
215669751 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU0601716A* | 33600 | 16.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 30800 | R-454B
215668965 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CSU1002120A* | 34400 | 17.5 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215669515 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0802120B* | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215487467 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96VC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215487483 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80VC0604B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
214442621 | 2.42 | Yes | No | FRIEDRICH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WFPU18Z363C | H,RE8J936+TD |  | 29000 | 15.2 | 11 | 9.35 | 28400 | 23800 | 83.8% | 2.08 | 22000 | R-410A
213772096 | 2 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CSPH*3612AL*+UI | 88*TB36070C14*** | 24000 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.98 | 20600 | R-410A
216766502 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3+P0V0C000M50SD |  | 43500 | 17.1 | 12.5 | 8.7 | 43500 | 31800 | 73.1% | 2.24 | 28800 | R-454B
216766518 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S9X1C100U5PSB | 43500 | 15.2 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29200 | R-454B
212627160 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TL8E100C20UH11 | 29200 | 16.7 | 9.4 | 8.5 | 33800 | 27200 | 80.47% | 2.69 | 25200 | R-410A
212627230 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TPLC080B12MP13 | 31600 | 17 | 9 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
216679734 | 1.45 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CSPH*2412AL* | 59TP7A060V17**16 | 17400 | 15.5 | 10 | 8.1 | 18100 | 18400 | 101.7% | 2.05 | 12200 | R-410A
212627253 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TL9E060B12UH11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627319 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | CP9C060B12MP13 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627337 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627339 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
215940426 | 2.93 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *97CTN0601716A* | 35200 | 21 | 11.7 | 8.5 | 38500 | 29400 | 76.36% | 2.02 | 33800 | R-454B
215940256 | 2.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *96CTN0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
212627877 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TL8E080C16UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627892 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627909 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CP9C100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627925 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CP9C100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212626923 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8E100B12MP11 | 32800 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626940 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626941 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626958 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212627041 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627057 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V080C16MP12 | 32600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627075 | 2.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9V080C16MP12 | 33600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627089 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627092 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TP9C080C16MP13 | 30800 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627107 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30200 | 89.35% | 2.82 | 27000 | R-410A
212627125 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TL9E100C20UH11 | 32400 | 17 | 10 | 8.4 | 33800 | 28800 | 85.21% | 2.79 | 26200 | R-410A
212627172 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9V100C20MP12 | 32200 | 17.5 | 9.4 | 8.5 | 33800 | 28200 | 83.43% | 2.7 | 25800 | R-410A
212627737 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | CPLC100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
216679902 | 2.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CSPH*4212AL* | 59TP7A080V17**16 | 35600 | 15.2 | 9.8 | 8.5 | 38500 | 34600 | 89.87% | 1.8 | 29200 | R-410A
212627739 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TL8E080C16UH11 | 29200 | 16.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627753 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8V080C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212626996 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM8V080C16MP12 | 31800 | 17.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212627044 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | CP9C080C16MP13 | 30400 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627105 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30200 | 89.35% | 2.82 | 27000 | R-410A
212627207 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9Y060B12MP11 | 31800 | 17.5 | 9 | 8.1 | 34000 | 29400 | 86.47% | 2.43 | 26600 | R-410A
212627225 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212627239 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TL9E060B12UH11 | 29200 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627276 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627290 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9E060B12MP12 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627308 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.4 | 34000 | 29400 | 86.47% | 2.71 | 26600 | R-410A
212627326 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | CP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627357 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9V060B12MP12 | 33600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627358 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627374 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627476 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TMLE080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627524 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212627525 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212627526 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212627542 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9Y100C20MP11 | 33000 | 15.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627559 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9Y100C16MP11 | 32000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212627112 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.4 | 33800 | 27200 | 80.47% | 2.65 | 25200 | R-410A
212627135 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | CPLC100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27200 | 80.47% | 2.48 | 25200 | R-410A
212627169 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | CP9C100C20MP13 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
212627244 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627269 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9E060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627278 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9E060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627330 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | CP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627335 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9V060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627344 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9V060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627364 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627437 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8E080B12MP11 | 33200 | 18 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627446 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9Y080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627480 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE080B12MP11 | 33200 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627496 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
216498595 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H175P459 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216735588 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MSU1002120A* | 23200 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
212627378 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TP9C060B12MP13 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627380 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TP9C060B12MP13 | 33600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627396 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.72 | 26000 | R-410A
212627469 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627487 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CPLC060A12MP13 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212627528 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212627587 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212627621 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8V080C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627562 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212627637 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8V100C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.68 | 25400 | R-410A
212627773 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627778 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8V100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627803 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TMLV100C16MP12 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627828 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627898 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TL9E080C16UH11 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216011854 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | CP9C100C20MP13 | 34000 | 17 | 9.5 | 8.1 | 32400 | 24400 | 75.31% | 2.12 | 25000 | R-410A
214810781 | 2.85 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436AA* | HG82936+AEFE3A* |  | 34200 | 19 | 12 | 9.5 | 34400 | 24800 | 72.09% | 2 | 27000 | R-410A
215487408 | 2.92 | Yes | No | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CHPEA4830*3A* | D*96VC1005DNA* | 35000 | 18.5 | 10.5 | 8.1 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216011853 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE34936 | CP9C100C20MP13 | 33400 | 17 | 9.5 | 8.1 | 32000 | 23200 | 72.5% | 2.06 | 26000 | R-410A
213872350 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | Z8ES040A12SMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 23800 | 74.84% | 2.1 | 24600 | R-410A
212596704 | 2.72 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | F,PE*G32936 |  | 32600 | 17 | 10 | 8.35 | 31400 | 22800 | 72.61% | 1.94 | 23600 | R-410A
215438166 | 2 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | FE*G32*25+TXV |  | 24000 | 19 | 12 | 9.4 | 22400 | 16600 | 74.11% | 2.08 | 17400 | R-454B
215438164 | 4.5 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | FE*TT9*60+TXV |  | 54000 | 19 | 11.7 | 9 | 52000 | 38000 | 73.08% | 2 | 36200 | R-454B
213214820 | 2.5 | No | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOD30U-36HFN1-MR0 | MVC-30HWFN1-M |  | 30000 | 17.3 | 11 | 8.5 | 30000 | 21000 | 70% | 1.86 | 17000 | R-410A
213411108 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG35936 | Z8ES080C16SMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 23800 | 74.84% | 2.14 | 24400 | R-410A
216681063 | 3.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4821AL* | 59TP7A080V21**20 | 36200 | 16 | 10 | 9 | 38000 | 34400 | 90.53% | 1.96 | 29000 | R-410A
213872347 | 2.65 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG7J936 | Z8ES040A12LMPS1 | 31800 | 17 | 10 | 8.1 | 30600 | 22200 | 72.55% | 2 | 24000 | R-410A
213872356 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | Z8ES080C20LMPS1 | 34000 | 18 | 10 | 8.5 | 31800 | 24000 | 75.47% | 2.12 | 24800 | R-410A
212627071 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627094 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
216990245 | 2.73 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | PL36H210P74*+TXV | 88*TB36045C17*** | 32800 | 17 | 9 | 9 | 33600 | 25000 | 74.4% | 1.88 | 29600 | R-454B
215487456 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA6030*3A* | D*80VC0805C*A* | 45500 | 16.5 | 10 | 8.5 | 46500 | 33600 | 72.26% | 2 | 29000 | R-32
216440240 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | 5PX*C007AS3 | S9V2C100U5VSB+LRP | 44000 | 20 | 12 | 9.7 | 46500 | 33400 | 71.83% | 2.1 | 42000 | R-454B
216974753 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | A36VCA*+TXV | 83*CA48060C17*** | 32600 | 20 | 11 | 9.5 | 33200 | 26400 | 79.52% | 2 | 29600 | R-454B
216974767 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | C36A***L13*+TXV | 83*CB36040C17*** | 32800 | 20 | 11.5 | 9.5 | 33200 | 26200 | 78.92% | 2.02 | 29600 | R-454B
214271784 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | V,C60H210P179 | 58TN*B110C21**20 | 45000 | 21 | 12 | 9.5 | 43500 | 35600 | 81.84% | 2.36 | 42000 | R-410A
216974808 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | PL48H175P78*+TXV | 83*CB48060C17*** | 43500 | 21 | 11 | 9.5 | 46000 | 36200 | 78.7% | 1.9 | 38500 | R-454B
212627623 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627673 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212627680 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8Y080C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627698 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627705 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212626360 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM8V080C16MP12 | 29800 | 16.9 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.64 | 25200 | R-410A
212626378 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9V100C16MP12 | 29800 | 16.9 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.63 | 25200 | R-410A
212626392 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9E100C16MP12 | 32600 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212391590 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31(1,2)30+TXV | *92ESN0601714A* | 23800 | 16 | 10 | 8.5 | 25200 | 23400 | 92.86% | 1.96 | 18400 | R-410A
212986245 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L14** | *96MSN0401410A* | 23400 | 16 | 10 | 8.1 | 26400 | 24600 | 93.18% | 2.02 | 19200 | R-410A
215934929 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CMN1002122B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215935049 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *80CTL1102120B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.02 | 32600 | R-454B
215935129 | 2.95 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0801714B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 28800 | 74.81% | 2.02 | 33000 | R-454B
216440376 | 3.71 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | 5TXCD008AS3 | L8V1C100U5VSB+LRP | 44500 | 20 | 12 | 9.7 | 47500 | 34000 | 71.58% | 2.1 | 43000 | R-454B
216440474 | 4.42 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X60A1 | 5PX*D010AS3 | S9V2D120U5VSB+LRP | 53000 | 18.8 | 10.5 | 9.4 | 53500 | 38000 | 71.03% | 2 | 47500 | R-454B
216440506 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X60A1 | 5TXCC007AS3 | S9V2C080U5VSB+LRP | 52000 | 18.4 | 10 | 9 | 54500 | 38500 | 70.64% | 2 | 48000 | R-454B
216440390 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | 5TXCD008AS3 | S9V2D120U5PSC+LRP | 44000 | 20 | 12 | 9.7 | 46500 | 33200 | 71.4% | 2.1 | 42000 | R-454B
216440406 | 3.71 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | 5TXCD010AS3 | S9V2C100U5PSC+LRP | 44500 | 20 | 12 | 9.7 | 46000 | 33200 | 72.17% | 2.1 | 42000 | R-454B
212624039 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TMLE080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
213872344 | 2.83 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | TP9C080C16MP13 | 34000 | 17 | 10 | 8.1 | 32200 | 23400 | 72.67% | 2.08 | 24400 | R-410A
215487443 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*96VC1005CNA* | 45500 | 16.2 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
215487450 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA4830*3A* | D*96VC0804CNA* | 45500 | 16.2 | 10 | 8.5 | 46000 | 33600 | 73.04% | 2 | 28400 | R-32
215487452 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA4830*3A* | D*80VC0805D*A* | 45500 | 17 | 10 | 8.5 | 46000 | 33600 | 73.04% | 2 | 28400 | R-32
212626560 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.66 | 25800 | R-410A
212626735 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8E100C16MP11 | 31800 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626737 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.2 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
213258267 | 1.48 | Yes | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE34936 | *96VTN0401712A* | 17700 | 15.2 | 10.5 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
213258935 | 1.48 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE7J936 | *96VSN0601412A* | 17800 | 16 | 10.5 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
212626742 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9Y100C16MP11 | 32000 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626778 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8E100B12MP11 | 29400 | 17.2 | 9.4 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212626801 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.2 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
214862297 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,CD16936 | 987MC42060C17*** | 23800 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.98 | 19800 | R-410A
214862302 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE9J936 | 987MC42060C17*** | 23600 | 16 | 11 | 8.1 | 20000 | 16300 | 81.5% | 1.94 | 19800 | R-410A
212626837 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9E080B12MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626851 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9E080B12MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212624002 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9Y080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624011 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TMLE080B12MP11 | 29800 | 17.4 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624045 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TMLE080B12MP11 | 32600 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624111 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TMLV060A12MP12 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624145 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9V080B12MP12 | 31800 | 17 | 9 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624163 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
216440206 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5TXCC007AS3 | S9V2C080U5VSB+LRP | 34200 | 19.4 | 12.5 | 9.4 | 32600 | 24200 | 74.23% | 2.1 | 30800 | R-454B
212624170 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624193 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM8E100C16MP11 | 31400 | 18 | 9.9 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624197 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9Y100C16MP11 | 31600 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624213 | 2.63 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8E040A12MP11 | 31600 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624277 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.77 | 26200 | R-410A
212624406 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624422 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9Y080C16MP11 | 33400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624472 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624520 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | CPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624572 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8V080C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624654 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TMLV100C16MP12 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624672 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLV100C16MP12 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624690 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624722 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624770 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TL8E080C16UH11 | 29600 | 16.9 | 9.5 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624829 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TL9E080C16UH11 | 30800 | 17.3 | 9.2 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216488019 | 1.92 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | A36VBA*+TXV | Z9ES080B12SMPS1 | 23000 | 18 | 12 | 9.5 | 21400 | 18700 | 87.38% | 2 | 16900 | R-454B
216974735 | 4.13 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | V,C60H210P17*+TXV | 83*CB60100C21*** | 49500 | 19 | 11.5 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216974433 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | V,C48H175P15*+TXV | 83*CB48060C17*** | 44000 | 17 | 9.5 | 9 | 46500 | 33800 | 72.69% | 2.04 | 41500 | R-454B
216974451 | 3.71 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C60A***L16*+TXV | 83*CB60080C21*** | 44500 | 17 | 9.5 | 9 | 46500 | 33400 | 71.83% | 2.06 | 41500 | R-454B
216990270 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | V,C36H175P45*+TXV | 88*TB48070C17*** | 34400 | 18 | 10 | 9 | 33800 | 24800 | 73.37% | 1.9 | 29400 | R-454B
216679482 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3612AL* | 59TP7A060V17**16 | 24000 | 16 | 10 | 8.5 | 25400 | 22200 | 87.4% | 1.75 | 18800 | R-410A
213258233 | 1.43 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG31930 | *96VSN0601714A* | 17200 | 16 | 10 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11400 | R-410A
213258276 | 1.49 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE34936 | *96VTN0601412A* | 17900 | 16 | 10.5 | 8.5 | 17000 | 18100 | 106.5% | 2.22 | 11500 | R-410A
216679518 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3617AL* | 59TP7A060V17**16 | 23600 | 16.5 | 10 | 9 | 25800 | 23600 | 91.47% | 1.76 | 18900 | R-410A
212441617 | 2.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE8J936 | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 32400 | 22800 | 70.37% | 2.04 | 25000 | R-410A
212441650 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE8J936 | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 32400 | 23200 | 71.6% | 2.02 | 25600 | R-410A
215821495 | 2 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | A24VBA*+TXV+AEFE3A* |  | 24000 | 19 | 12 | 9.45 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
215940920 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN0801716A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.04 | 32800 | R-454B
215934620 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | FCMA5B48L0C*+WALLCON |  | 45500 | 22 | 12 | 9.5 | 48500 | 36000 | 74.23% | 1.96 | 39000 | R-454B
215935299 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN1002122B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215935149 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0401712A* | 35600 | 22 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 33200 | R-454B
216679498 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *97VTN0601716A* | 23200 | 16.5 | 10 | 9 | 26400 | 24400 | 92.42% | 1.86 | 19300 | R-410A
216734379 | 1.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0701412A* | 22400 | 16.5 | 11 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
214862327 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE7J936 | 987MC60080C21*** | 23400 | 16 | 11 | 8.1 | 20000 | 16300 | 81.5% | 1.92 | 19800 | R-410A
214862336 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE7J936 | 987MC66100C21*** | 23600 | 16 | 11 | 8.1 | 19800 | 16200 | 81.82% | 1.94 | 19600 | R-410A
216987085 | 1.83 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | PL36H***P44*+TXV | 926SB36040V17*** | 22000 | 15.2 | 10.5 | 8.5 | 19200 | 18200 | 94.79% | 1.98 | 16700 | R-454B
216972008 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P17*+TXV | 58CU*B100C21**20 | 49500 | 19 | 11.5 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216972107 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L16*+TXV | 58TN*B110C21**20 | 48500 | 19 | 11 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216972140 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L18*+TXV | 59CU5B080C21**20 | 49000 | 19 | 10.5 | 10.5 | 51000 | 52000 | 102% | 1.94 | 50000 | R-454B
216972157 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L16*+TXV | 59CU5B100C21**22 | 48500 | 19 | 11 | 10.5 | 50000 | 52500 | 105% | 1.98 | 49500 | R-454B
216972256 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C48A***L16*+TXV | 59MN7C100C21**22 | 48000 | 19 | 10.5 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216972274 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P29*+TXV | 59TN6C080C17**14 | 48000 | 18 | 12 | 9 | 48500 | 49500 | 102.1% | 1.96 | 48000 | R-454B
215940970 | 3.58 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0801716A* | 43000 | 20 | 10.5 | 9.5 | 48500 | 37400 | 77.11% | 2 | 40000 | R-454B
215940990 | 3.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN1002122A* | 43500 | 21 | 10.5 | 9.5 | 48000 | 36400 | 75.83% | 2 | 39500 | R-454B
215941240 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0802120A* | 45000 | 20 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
215224775 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | H,PG9J936 | 59MN7C120C24**22 | 32800 | 20 | 11.7 | 9 | 34800 | 27200 | 78.16% | 2.04 | 31600 | R-410A
216972774 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | A60VHA*+TXV | 58TN*B090C21**20 | 45000 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972776 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL48H210P75*+TXV | 58TN*B090C21**20 | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 1.92 | 38000 | R-454B
216972790 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H210P75*+TXV | 58TN*B110C21**20 | 44000 | 21 | 11 | 9.5 | 46000 | 36000 | 78.26% | 1.92 | 38000 | R-454B
216972810 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C48A***L53*+TXV | 59CU5B060C17**16 | 44000 | 20 | 10.5 | 9.5 | 47000 | 36200 | 77.02% | 2 | 38500 | R-454B
216972825 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C60H210P29*+TXV | 59CU5B100C21**22 | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 2 | 38000 | R-454B
216972826 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | A60VHA*+TXV | 59CU5B100C21**22 | 45000 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972858 | 3.58 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H175P38*+TXV | 59MN7C080C17**14 | 43000 | 20 | 10.5 | 9.5 | 47000 | 36200 | 77.02% | 2 | 38500 | R-454B
216766616 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S8V2C100M5PCB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32000 | 72.73% | 2.22 | 29200 | R-454B
216734147 | 1.83 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *96VSN0401410B* | 22000 | 15.5 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
216766802 | 2 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S8V2B060M4PDB | 24000 | 17.5 | 12.7 | 9 | 22000 | 17500 | 79.55% | 2.06 | 15500 | R-454B
216766836 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S8V2B080M4PDB | 23800 | 17.1 | 12.7 | 8.5 | 22200 | 17400 | 78.38% | 1.96 | 15500 | R-454B
216766868 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S8V2B080M4PDB | 23800 | 17.5 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2.06 | 15500 | R-454B
216766416 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCD008AS3 | S8V2D120M5PDB | 34200 | 17.1 | 12.5 | 9 | 32600 | 24200 | 74.23% | 2.22 | 21400 | R-454B
216766620 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S9X2D120U5PSB | 44000 | 16 | 12 | 9 | 44000 | 32400 | 73.64% | 2.24 | 29400 | R-454B
216972976 | 4.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | V,C60H210P29*+TXV | 58TN*B090C21**20 | 56000 | 18 | 11.5 | 8.1 | 59000 | 45000 | 76.27% | 2 | 46000 | R-454B
216972288 | 3.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL48H210P75*+TXV | 59TN6C080C17**14 | 46500 | 18 | 11.5 | 10 | 48000 | 49500 | 103.1% | 2.06 | 47500 | R-454B
216972339 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P17*+TXV | 59TN6C100C21**22 | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216972926 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L19*+TXV | 59TN6C100C21**22 | 45000 | 21 | 10.5 | 9.5 | 46500 | 36400 | 78.28% | 2 | 39000 | R-454B
216972943 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C48A***L15*+TXV | 59TN7A080C21**20 | 43500 | 20 | 10.5 | 9.5 | 46000 | 36200 | 78.7% | 1.92 | 38500 | R-454B
212480213 | 2.53 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | A36VCA+TXV | 58SU*A040E17**12 | 30400 | 15.2 | 9 | 8.1 | 32600 | 26600 | 81.6% | 1.8 | 22400 | R-410A
215487388 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CHPEA3026*3A* | D*80VC0805C*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
214385389 | 2.93 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,YE35936 | *80MSU0401712A* | 35200 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
214385662 | 2.83 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,YA10936 | *95MSU0401712A* | 34000 | 15.2 | 9 | 8.1 | 37400 | 35000 | 93.58% | 1.82 | 28600 | R-410A
214385721 | 2.58 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | H,YA10936 | *80CSU0401712A* | 31000 | 17 | 10.5 | 8.1 | 31600 | 23800 | 75.32% | 1.86 | 30200 | R-410A
216797063 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | *UHMB060CCV3+LRP | 29600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.67 | 38000 | R-454B
216797074 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | L8V1B080U4VSB+LRP | 30200 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.72 | 38000 | R-454B
215438168 | 2 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | FE*E32*25+TXV |  | 24000 | 19 | 12 | 9.4 | 22400 | 16600 | 74.11% | 2.08 | 17400 | R-454B
214570608 | 2.03 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CAP**4321AL*+UI | 58TN*B070C21**20 | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
214571128 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CNPV*3621AL*+UI | 59MN7C080C21**20 | 23400 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
214571178 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CNPV*4221AL*+UI | 59MN7C060C21**20 | 23600 | 16 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.94 | 20800 | R-410A
215731281 | 2 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | FE*G33*25+TXV |  | 24000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
209880030 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF96TV304017M4S*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
216770096 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCC009AS3 | *UHMC100CCV4 | 23800 | 17.5 | 13 | 9 | 21400 | 16900 | 78.97% | 2.08 | 15100 | R-454B
216734295 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *97VTN0601716A* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216732523 | 1.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M14A* | *80VSL0451412B* | 21800 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.98 | 17900 | R-454B
216733442 | 1.92 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *96MSN0601412A* | 23000 | 15.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
216680538 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3621AL* | 59TP7A080V17**16 | 23600 | 17 | 10 | 9 | 25600 | 23200 | 90.62% | 1.84 | 18800 | R-410A
216990284 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | PL36H210P29*+TXV | 88*TB60070C21*** | 34400 | 18 | 10 | 9 | 33800 | 24800 | 73.37% | 1.88 | 29400 | R-454B
215821498 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | A48VGA*+TXV+AEFE5* |  | 46000 | 19 | 12 | 9 | 44000 | 33600 | 76.36% | 2.1 | 34600 | R-454B
215726297 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y48H175P38*+TXV+AEFE4B* |  | 46000 | 19 | 12 | 9 | 44000 | 33600 | 76.36% | 2.1 | 34600 | R-454B
212627153 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM8Y100C16MP11 | 29200 | 17.7 | 9.4 | 8.5 | 33800 | 27200 | 80.47% | 2.67 | 25200 | R-410A
212614345 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | F,PE*E34936 |  | 33600 | 18 | 9.5 | 8.4 | 32200 | 23400 | 72.67% | 2.1 | 24400 | R-410A
215667740 | 1.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *80CTL0451712B* | 23600 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214491652 | 1.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA1810A* | CA*EA2422*4B* | D*96VC0603BNA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
216440524 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X60A1 | 5TXCD008AS3+P0V0C000M50SD+LRP |  | 52000 | 18.8 | 10.5 | 9 | 54000 | 38000 | 70.37% | 2 | 47500 | R-454B
212624831 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TL9E080C16UH11 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624870 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | CP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624963 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8Y100C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624988 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8Y100C16MP11 | 31000 | 18.2 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625006 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y100C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625031 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625054 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625147 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TP9C100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
216735728 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *97CMN0801714B* | 22800 | 16 | 11 | 8.5 | 20400 | 18300 | 89.71% | 1.98 | 17400 | R-454B
212396760 | 3.88 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TXD2060A10NU** | BV**C9960 |  | 46500 | 15.2 | 9.5 | 8.5 | 46000 | 33200 | 72.17% | 1.8 | 30200 | R-410A
213258235 | 1.46 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *96VSN0601714A* | 17500 | 16 | 10 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11400 | R-410A
212480039 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 59SC2D080E17**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22400 | 91.06% | 1.88 | 18100 | R-410A
212627560 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
216735701 | 1.98 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *95CSU1002122B* | 23800 | 15.5 | 11 | 8.5 | 21000 | 18700 | 89.05% | 1.98 | 17800 | R-454B
216737105 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MS(N,L)0902420A* | 22200 | 15.5 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.9 | 17600 | R-454B
216797079 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2B060M4PCB | 29800 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.63 | 37600 | R-454B
216797090 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2C080M5PDB | 30200 | 18 | 9.8 | 8.5 | 32600 | 32600 | 100% | 2.88 | 37400 | R-454B
216797113 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B080U4PSC+LRP | 29600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.68 | 37800 | R-454B
216797115 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B080U4VSB+LRP | 29600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.68 | 37800 | R-454B
214771858 | 1.93 | Yes | Yes | ECOER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EODA19H-2436A | HG7J924+AEFE4B* |  | 23200 | 20 | 12.5 | 9.25 | 22400 | 19200 | 85.71% | 2.06 | 21400 | R-410A
216972423 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P45*+TXV | 58CU*B040C17**12 | 33800 | 20 | 11.7 | 9.5 | 32600 | 25600 | 78.53% | 2.06 | 29000 | R-454B
216972441 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 58CU*B060C17**16 | 32800 | 20 | 11.5 | 9.5 | 33200 | 26200 | 78.92% | 2 | 29600 | R-454B
216972490 | 2.78 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H***P44*+TXV | 58TN*B070C14**12 | 33400 | 19 | 11 | 9 | 33600 | 26600 | 79.17% | 1.92 | 30000 | R-454B
212624420 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9Y080C16MP11 | 33200 | 18.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624452 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TPLC080C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27200 | 80.47% | 2.48 | 25200 | R-410A
212624470 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624506 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624513 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624581 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624611 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM8V100C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624622 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
216981025 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV-BLEED | Y82E120C20LMPS1 | 54000 | 19 | 12 | 9 | 52000 | 38000 | 73.08% | 2 | 35800 | R-454B
215487369 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*96VC0603BNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
216011843 | 2.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | CP9C080B12MP13 | 33600 | 17 | 10 | 8.5 | 31800 | 23000 | 72.33% | 2.04 | 24000 | R-410A
212480345 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | C36A***L159 | 59TP6B080V21**20 | 29600 | 15.2 | 9 | 8.1 | 32000 | 27000 | 84.38% | 1.78 | 22200 | R-410A
215832583 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | V,Y36H175P15*+TXV+AEFE4B* |  | 34000 | 19 | 11.7 | 9 | 30800 | 24800 | 80.52% | 2.1 | 25600 | R-454B
215487470 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96VC0603BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215487471 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*96VC0403BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215487473 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96VC0403BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
213772670 | 1.92 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X24L17A*+WALLCON | *97CMN0601714B* | 23000 | 16 | 10 | 8.1 | 22000 | 16900 | 76.82% | 1.88 | 21000 | R-410A
213772720 | 2.02 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0451712B* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
213772940 | 1.95 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0451712B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.92 | 20800 | R-410A
215487469 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96VC0603BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
209880028 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF96TV306017M4S*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25600 | R-410A
212441667 | 2.77 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE8J936 | TM9Y080C16MP11 | 33200 | 18 | 9.5 | 8.5 | 32400 | 23200 | 71.6% | 2.04 | 25800 | R-410A
214301845 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE7J(1,2)36+TXV | TM9E040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 1.98 | 24800 | R-410A
215674276 | 3.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1002122B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 41500 | R-454B
215674376 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL1102120B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215674056 | 3.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0902120B* | 44500 | 18 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.06 | 42500 | R-454B
213753745 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58TP*B135V24**22 | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
213753778 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC2E120M24**20 | 35200 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
213753794 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC6A080M21**20 | 35200 | 16 | 9.5 | 8.1 | 39000 | 32200 | 82.56% | 2.52 | 29600 | R-410A
213753847 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SP6A120V24**22 | 35400 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
216981022 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P19*+TXV-BLEED | Y82E100C20LMPS1 | 54000 | 19 | 12 | 9 | 52000 | 37600 | 72.31% | 2 | 35600 | R-454B
213753612 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 59TP6C100V21**20 | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
216972523 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 58TN*B070C21**20 | 32800 | 20 | 11 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
216972590 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L15*+TXV | 59CU5B060C17**16 | 33000 | 19 | 11 | 9.5 | 33400 | 26400 | 79.04% | 2.02 | 29600 | R-454B
216972608 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P29*+TXV | 59CU5B100C21**22 | 33800 | 20 | 12 | 9.5 | 32400 | 25400 | 78.4% | 2.04 | 28600 | R-454B
216972624 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H175P14*+TXV | 59MN7C060C17**14 | 32400 | 19 | 10.5 | 9.5 | 32400 | 25600 | 79.01% | 2.04 | 28800 | R-454B
216972626 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P14*+TXV | 59MN7C060C17**14 | 32400 | 19 | 10.5 | 9.5 | 32400 | 25600 | 79.01% | 2.04 | 28800 | R-454B
216972673 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L13*+TXV | 59TN6C080C17**14 | 32200 | 20 | 10.5 | 9.5 | 33200 | 26200 | 78.92% | 2.02 | 29600 | R-454B
216972691 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P29*+TXV | 59TN7A060C17**16 | 33000 | 19 | 11 | 9 | 33800 | 26600 | 78.7% | 1.9 | 30000 | R-454B
216972692 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | A36VCA*+TXV | 59TN7A060C17**16 | 32400 | 19 | 10.5 | 9 | 33800 | 26600 | 78.7% | 1.9 | 30000 | R-454B
216972693 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L13*+TXV | 59TN7A060C17**16 | 32400 | 19 | 10.5 | 9 | 34000 | 27000 | 79.41% | 1.88 | 30400 | R-454B
216735633 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80CTL0902120B* | 23400 | 16 | 11 | 8.5 | 20800 | 18600 | 89.42% | 1.98 | 17700 | R-454B
216735765 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *92MSN0601714A* | 23000 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
214521983 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z9ES080C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33000 | 27600 | 83.64% | 2.65 | 25200 | R-410A
212623999 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM9Y080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
213753051 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6C100V21**20 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
212479863 | 2.05 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 58S(B,C)*A070E17**16 | 24600 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212479880 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 58S(B,C)*A070E17**16 | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212479945 | 2.07 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 58SU*A060E17**16 | 24800 | 17 | 10.5 | 8.5 | 25000 | 21400 | 85.6% | 1.82 | 18300 | R-410A
212479964 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 58TP*A045V14**12 | 24000 | 16 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212479978 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149 | 58TP*A070V17**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212480046 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 59SC5B026E14**10 | 22800 | 16 | 9.5 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17900 | R-410A
212480079 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 59SC5B080E17**16 | 24800 | 15.2 | 10 | 8.5 | 25200 | 21600 | 85.71% | 1.8 | 18400 | R-410A
212625213 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8Y120C20MP11 | 32600 | 18 | 9 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625231 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TL8E100C20UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625263 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TL8E100C20UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625406 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625433 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
214233330 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | H,PG9J936 | 59TN6C080C17**14 | 32600 | 19 | 11.7 | 9 | 35200 | 27400 | 77.84% | 2.04 | 31800 | R-410A
213312363 | 2.82 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | PL36H***P449+AEFE3A* |  | 33800 | 18 | 9.5 | 8.45 | 32200 | 23400 | 72.67% | 2.1 | 24400 | R-410A
216974478 | 4.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | C60A***L19*+TXV | 83*CA60080C21*** | 56000 | 18 | 9 | 9 | 57500 | 41000 | 71.3% | 2.02 | 50000 | R-454B
213770867 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L17A*+WALLCON | *97CMN0801714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.94 | 20800 | R-410A
216974698 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | V,C48H210P16*+TXV | 83*CA60080C21*** | 48500 | 19 | 11 | 10.5 | 50000 | 52500 | 105% | 1.98 | 49500 | R-454B
216974713 | 4.08 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | V,C60H210P17*+TXV | 83*CA60100C21*** | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216974714 | 4.08 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | C48A***L18*+TXV | 83*CA60100C21*** | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216974730 | 4.13 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | A60VHA*+TXV | 83*CB60100C21*** | 49500 | 19 | 11.5 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216974732 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | C48A***L16*+TXV | 83*CB60100C21*** | 48500 | 19 | 11 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216974344 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | PL36H175P15*+TXV | 83*CA36040C17*** | 33800 | 18 | 9.5 | 9 | 33400 | 24600 | 73.65% | 1.88 | 29200 | R-454B
216974380 | 2.77 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | C36A***L13*+TXV | 83*CB48060C17*** | 33200 | 17 | 9.5 | 8.5 | 34200 | 25200 | 73.68% | 1.84 | 30000 | R-454B
215389837 | 4.29 | Yes | No | ECOER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EODA19H-4860A | HG84960+TD |  | 51500 | 15.2 | 10.5 | 8.6 | 51000 | 36800 | 72.16% | 1.9 | 41000 | R-410A
212624636 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8Y080C16MP11 | 31600 | 18.4 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624647 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TMLV100C16MP12 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624665 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TMLV100C16MP12 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624670 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TMLV100C16MP12 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
216990293 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | PL48H175P78*+TXV | 88*TB48070C17*** | 44000 | 17 | 9.5 | 9 | 47000 | 34000 | 72.34% | 2.04 | 42000 | R-454B
216990295 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C48A***L15*+TXV | 88*TB48070C17*** | 44000 | 17 | 9.5 | 9 | 47000 | 34000 | 72.34% | 2.04 | 42000 | R-454B
212624681 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624706 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TPLC080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
216987092 | 1.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | PL36H175P15*+TXV | 926SB36060V14*** | 22600 | 16 | 11 | 8.1 | 19200 | 18100 | 94.27% | 1.85 | 16600 | R-454B
216986117 | 1.93 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MURAQ24AA3 | C36A***L13*+TXV | 926TC36060V14*** | 23200 | 15.2 | 9.5 | 8.5 | 22400 | 19000 | 84.82% | 1.9 | 17900 | R-454B
215940326 | 2.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 33000 | R-454B
209880026 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF97MV307017DHS*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
209880033 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF96TV507021M4S*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
209880035 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF96TV508521M4S*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
215487440 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*80VC0805C*A* | 45500 | 16.5 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
215669115 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU1002120A* | 33800 | 17.5 | 9.5 | 9 | 35000 | 25200 | 72% | 1.88 | 30400 | R-454B
216011848 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE32936 | CP9C100C16MP13 | 33200 | 17 | 10 | 8.5 | 31400 | 22800 | 72.61% | 2.06 | 25400 | R-410A
216011850 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE34936 | CP9C100C16MP13 | 33200 | 17 | 10 | 8.5 | 31400 | 22800 | 72.61% | 2.06 | 25400 | R-410A
216011851 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | CP9C100C16MP13 | 34000 | 17 | 10 | 8.5 | 32400 | 23600 | 72.84% | 2.1 | 24400 | R-410A
216766918 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8V2B080M4PDB | 32600 | 16 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.98 | 21600 | R-454B
215674206 | 3.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1352422B* | 45000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
216734663 | 1.85 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96MSN0601716A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734479 | 1.85 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80CTL0451712B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
215669605 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN1002122B* | 34800 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
214572648 | 2.65 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4224AL*+UI | 58TN*B070C21**20 | 31800 | 18 | 11 | 8.5 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
214572748 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4321AL*+UI | 59MN7C080C21**20 | 32800 | 17.5 | 11.5 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
214572798 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4821AL*+UI | 59MN7C060C21**20 | 32200 | 17 | 11 | 8.5 | 32600 | 25200 | 77.3% | 1.96 | 31600 | R-410A
214572898 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**6024AL*+UI | 59CU5B080C21**20 | 32800 | 17.5 | 11.5 | 8.5 | 31600 | 24800 | 78.48% | 1.98 | 31000 | R-410A
216675565 | 2.08 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | ESH5X36M12A* | *80CSU1002120A* | 25000 | 15.2 | 10 | 8.5 | 24200 | 19500 | 80.58% | 1.92 | 19000 | R-454B
212625540 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | CPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625590 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TMLV120C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
213258356 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG33936 | *96VTN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 24200 | 97.58% | 2.04 | 18300 | R-410A
214595722 | 1.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96VTN0601716B* | 23600 | 16.5 | 10 | 9 | 26000 | 24000 | 92.31% | 2 | 19000 | R-410A
212625624 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TP9C120D20MP13 | 31200 | 16.8 | 9.3 | 8.1 | 32200 | 28000 | 86.96% | 2.51 | 25200 | R-410A
212625647 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8V120C20MP12 | 28600 | 15.6 | 8.4 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
212625649 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8V120C20MP12 | 29600 | 15.9 | 8 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
215668599 | 2.82 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0801714B* | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215668703 | 2.85 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *95CSU0601716B* | 34200 | 17.5 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30600 | R-454B
215668735 | 2.85 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0602120B* | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215668751 | 2.87 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0802120B* | 34400 | 18 | 10 | 8.1 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
212624064 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624133 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CP9C080B12MP13 | 31800 | 17 | 9 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624134 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CP9C080B12MP13 | 31800 | 17 | 9 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624148 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624151 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624198 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9Y100C16MP11 | 32000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624199 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9Y100C16MP11 | 32000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624250 | 2.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8E080C16MP11 | 32200 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212624282 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9E080C16MP12 | 31800 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212624315 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TMLE100C16MP11 | 32200 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624318 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624348 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM8V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212624483 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624484 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624501 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | CPLC080C16MP13 | 33400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624534 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
214301846 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE9J(1,2)36+TXV | TM9E040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 1.98 | 24800 | R-410A
214301848 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE9J(1,2)36+TXV | TM9E060A10MP12 | 33600 | 17 | 9.5 | 8.1 | 32200 | 23400 | 72.67% | 2.02 | 24400 | R-410A
214301865 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE9J(1,2)36+TXV | TM9V100C16MP12 | 34000 | 17 | 10 | 8.5 | 32400 | 23600 | 72.84% | 2.1 | 24400 | R-410A
214301898 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE9J(1,2)36+TXV | Z8ES100C20SMPS1 | 34000 | 17 | 9.5 | 8.5 | 31800 | 23800 | 74.84% | 2.14 | 24400 | R-410A
214301912 | 2.83 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE9J(1,2)36+TXV | Z8ET100C16LMPS1 | 34000 | 18 | 9.5 | 8.5 | 31800 | 23800 | 74.84% | 2.12 | 24600 | R-410A
212624720 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624781 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TL8E080C16UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624815 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TL8E080C16UH11 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624822 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TL9E080C16UH11 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624863 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM8Y100C16MP11 | 29800 | 17.8 | 9.5 | 8.5 | 34000 | 27000 | 79.41% | 2.66 | 25200 | R-410A
212624888 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
216990309 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C48A***L16*+TXV | 88*TB48090C17*** | 44000 | 17 | 9.5 | 9 | 46500 | 33800 | 72.69% | 2.06 | 41500 | R-454B
212624899 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | CP9C100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624940 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8Y080C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625013 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8Y100C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625015 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM8Y100C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625065 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625122 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625172 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625199 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625206 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8Y100C20MP11 | 33000 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625281 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TL8E100C20UH11 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625340 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625381 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9V100C20MP12 | 30000 | 17 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625465 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625467 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625472 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TP9C100C20MP13 | 33400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625533 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM9Y120D20MP11 | 31400 | 16.4 | 9.3 | 8.4 | 32200 | 28000 | 86.96% | 2.74 | 25200 | R-410A
212625547 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | CPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212624552 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | CPLC100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624585 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8V080C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624619 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624666 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TMLV100C16MP12 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212480055 | 2.05 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59SC5B060E17**14 | 24600 | 16 | 10.5 | 8.1 | 25000 | 22000 | 88% | 1.84 | 18400 | R-410A
212480088 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59SP6A060V17**14 | 23800 | 16 | 10 | 8.5 | 25200 | 23600 | 93.65% | 1.98 | 18500 | R-410A
212480156 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 59TP6B080V17**16 | 24000 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212479869 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149 | 58S(B,C)*A070E17**16 | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212625692 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625706 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625751 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TMLV120C20MP12 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625781 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625799 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9Y120D20MP11 | 29400 | 15.8 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625801 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9Y120D20MP11 | 31800 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625815 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9Y120D20MP11 | 30200 | 16 | 9.1 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625851 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CP9C120D20MP13 | 33000 | 17 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
216734497 | 1.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80CTL0701716B* | 22400 | 16.5 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
216734781 | 1.85 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VTN0401410B* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17700 | R-454B
216734932 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80MS(N,L)0701712A* | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
216734981 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80VSL0701716B* | 23200 | 16.5 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.96 | 17700 | R-454B
212625867 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V120D20MP12 | 32200 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625874 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TP9C120D20MP13 | 29400 | 16.3 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625876 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625890 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TP9C120D20MP13 | 30600 | 16.6 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625924 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9V040A10MP12 | 32000 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
215832569 | 2 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | A36VDA*+TXV+AEFE4B* |  | 24000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
212625933 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9V040A10MP12 | 33000 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212479802 | 1.5 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A36VCA+TXV | 58S(B,C)*A070E17**12 | 18000 | 16 | 11 | 8.5 | 17300 | 18300 | 105.8% | 2.26 | 11600 | R-410A
216735919 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *95MSU0601716A* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17400 | R-454B
216736033 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96VTN1002120B* | 22800 | 16.5 | 11 | 8.5 | 20400 | 18300 | 89.71% | 1.98 | 17400 | R-454B
213607928 | 4 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-48WADU | HE86948+AEFE4B* |  | 48000 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
212625558 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | CPLC120C20MP13 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625631 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9V120D20MP12 | 31800 | 17 | 9.4 | 8.5 | 32200 | 28200 | 87.58% | 2.8 | 25400 | R-410A
212625633 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TP9C120D20MP13 | 31800 | 17 | 9.4 | 8.1 | 32200 | 28200 | 87.58% | 2.5 | 25400 | R-410A
212625640 | 2.42 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | CPLC120C20MP13 | 29000 | 15.8 | 8.5 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625674 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CPLC100C20MP13 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625690 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CPLC120C20MP13 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625733 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8V120C20MP12 | 32600 | 16.5 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625817 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9Y120D20MP11 | 31800 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625951 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9E100C20MP12 | 33000 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626026 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9E100C16MP12 | 30000 | 17.4 | 9.5 | 8.3 | 33400 | 27400 | 82.04% | 2.6 | 25200 | R-410A
212626074 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8Y080B12MP11 | 30600 | 17.6 | 9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626210 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.62 | 25800 | R-410A
212626285 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.1 | 33600 | 28600 | 85.12% | 2.67 | 26000 | R-410A
215487375 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3626*3A* | D*80VC0803B*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
216682780 | 2.48 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X36L21A* | *97VTN1002122A* | 29800 | 15.2 | 9 | 8.5 | 34000 | 27600 | 81.18% | 1.75 | 23400 | R-410A
212603085 | 1.52 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG80936 | *80ES(N,L)0701712A* | 18200 | 16 | 11 | 8.5 | 17100 | 17900 | 104.7% | 2.22 | 11500 | R-410A
212520221 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG32936 | 58S(B,C)*A070E21**16 | 23600 | 17 | 10 | 8.1 | 24600 | 22400 | 91.06% | 1.9 | 18100 | R-410A
212520239 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG9J936 | 58SP*A045V14**12 | 24200 | 16 | 10 | 8.5 | 24800 | 22600 | 91.13% | 1.9 | 18200 | R-410A
215487416 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CA*EA6030*3A* | D*80VC0805C*A* | 40500 | 17 | 10 | 8.8 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215487427 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA4830*3A* | D*96VC0804CNA* | 40500 | 16.5 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215487434 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA6030*3A* | D*80VC1005C*A* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215487457 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA6030*3A* | D*80VC1005C*A* | 45500 | 16.5 | 10 | 8.5 | 46500 | 33600 | 72.26% | 2 | 29000 | R-32
212520240 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG24936 | 58SP*A045V17**16 | 22800 | 17 | 9.5 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212520254 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG34936 | 58SP*A090V21**20 | 24200 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.88 | 18000 | R-410A
212520273 | 2 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG32936 | 58TP*A070V14**12 | 24000 | 17 | 9.5 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212625849 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CP9C120D20MP13 | 32800 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625858 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V120D20MP12 | 31600 | 17 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625865 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9V120D20MP12 | 30200 | 16.5 | 9.1 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
216011836 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE32936 | CP9C060B12MP13 | 32600 | 17 | 9.5 | 8.1 | 32000 | 23200 | 72.5% | 2.02 | 25400 | R-410A
215726295 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG81*36+TXV+AEFE4B* |  | 34000 | 19 | 11.7 | 9 | 30800 | 24800 | 80.52% | 2.1 | 25600 | R-454B
212625883 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625885 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
216681129 | 2.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4221AL* | 59TP7A080V21**20 | 35600 | 15.5 | 10 | 8.5 | 39000 | 34800 | 89.23% | 1.75 | 29400 | R-410A
213753859 | 2.78 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59TP6C080V17**16 | 33400 | 15.9 | 9.8 | 8.1 | 37800 | 31800 | 84.13% | 2.7 | 29000 | R-410A
212625960 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9E100C20MP12 | 33200 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626040 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8Y060A12MP11 | 32400 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626060 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM9E100C16MP12 | 32000 | 17.9 | 9.9 | 8.3 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
212626067 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8Y080B12MP11 | 30000 | 17.4 | 9.5 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626217 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8E080C16MP11 | 31800 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.65 | 25800 | R-410A
212626351 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9V080C16MP12 | 30400 | 17 | 9 | 8.4 | 33600 | 27600 | 82.14% | 2.62 | 25400 | R-410A
212626383 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9E100C16MP12 | 30000 | 17.4 | 9.5 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626399 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9E100C16MP12 | 30800 | 17.7 | 9 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
213752982 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6C040V14**10 | 23000 | 16 | 9.5 | 8.5 | 27000 | 20600 | 76.3% | 2.85 | 19500 | R-410A
213752996 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C040V17**12 | 23400 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
215727891 | 2.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J(1,2)36+TXV | TM9V080B12MP12 | 33000 | 17 | 11 | 8.5 | 29200 | 24800 | 84.93% | 2 | 26000 | R-454B
215726298 | 4.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P17*+TXV+AEFE5* |  | 54000 | 19 | 11.7 | 9 | 52000 | 38000 | 73.08% | 2.1 | 36200 | R-454B
215731276 | 4.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | FE*TT4*60+TXV |  | 53500 | 19 | 12 | 9 | 51000 | 37400 | 73.33% | 2 | 35200 | R-454B
213187956 | 2 | Yes | No | AMERISTAR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | E4HL5030A1000A | PL36H175P459+TD |  | 24000 | 15.2 | 10 | 8.1 | 22400 | 19100 | 85.27% | 1.75 | 18100 | R-410A
215933270 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN1202422B* | 33400 | 19 | 11 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215676025 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *95CSU1002122B* | 48500 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
215487384 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CHPEA3026*3A* | D*80VC0603B*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
212361591 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M100D5A | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34000 | R-410A
212361468 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
215727908 | 2.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J(1,2)36+TXV | Z8ET080B12LMPS1 | 32800 | 18 | 11.7 | 8.5 | 28400 | 24400 | 85.92% | 2 | 25400 | R-454B
215931750 | 4.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0802120B* | 56500 | 18.5 | 11 | 8.5 | 60500 | 46500 | 76.86% | 2.02 | 48000 | R-454B
215940163 | 2.82 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1002122A* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.92 | 30400 | R-454B
215940193 | 2.85 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
215940263 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *96CTN0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215940413 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0401712B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
216736780 | 1.88 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *95MSU1002122A* | 22600 | 16 | 10.5 | 8.1 | 21200 | 19100 | 90.09% | 1.85 | 17900 | R-454B
216736109 | 1.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | OMV098J12* | 23200 | 15.2 | 11 | 8.5 | 20600 | 18500 | 89.81% | 1.98 | 17500 | R-454B
214861540 | 1.5 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOX430-18HFN10-M3X | MVBDM-18HWFN10-WA3 |  | 18000 | 19 | 12.5 | 10.2 | 18000 | 18600 | 103.3% | 2.12 | 14700 | R-454B
215931900 | 4.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V60*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN1202422B* | 56000 | 17.5 | 11 | 8.1 | 61000 | 46000 | 75.41% | 1.95 | 47500 | R-454B
215933320 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0701716B* | 33400 | 19 | 11 | 9 | 35200 | 26800 | 76.14% | 1.9 | 30800 | R-454B
215932870 | 2.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0902120B* | 34600 | 20.5 | 12 | 9.5 | 34200 | 25800 | 75.44% | 2.06 | 29800 | R-454B
212480095 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 59SP6A080V17**16 | 23800 | 16 | 10 | 8.5 | 25200 | 23000 | 91.27% | 1.92 | 18500 | R-410A
212480128 | 2.03 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149 | 59SU5A060E17**16 | 24400 | 17 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212480130 | 2.03 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 59SU5A060E17**16 | 24400 | 17 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
212480147 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59TP6B060V17**14 | 24000 | 16 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.88 | 18100 | R-410A
212479830 | 1.44 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A24VBA+TXV | 59SP6A040V14**10 | 17300 | 16 | 10.5 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
212520291 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG9J936 | 58TP*A110V21**22 | 23800 | 17 | 10.5 | 8.1 | 24400 | 23200 | 95.08% | 1.96 | 18000 | R-410A
212394496 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | TM9E080B12MP12 | 34000 | 17 | 10 | 8.5 | 32200 | 23600 | 73.29% | 2.06 | 24400 | R-410A
215940513 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *96CTN0802120B* | 34400 | 20.5 | 11.7 | 8.5 | 38500 | 28200 | 73.25% | 2.04 | 32200 | R-454B
215932920 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0802120B* | 34400 | 20.5 | 12 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
212614026 | 1.87 | Yes | Yes | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA24HOS20230E7 | HE20924+TD |  | 22400 | 16 | 10 | 8.6 | 23000 | 19600 | 85.22% | 1.8 | 19800 | R-410A
215487466 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96VC0803BNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216680838 | 1.43 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 59TP7A080V17**16 | 17200 | 16 | 10.5 | 8.5 | 18100 | 19200 | 106.1% | 2.2 | 12200 | R-410A
216733866 | 1.85 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *80MS(N,L)0701716A* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216989073 | 1.97 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MURAQ24AA3 | PL36H210P29*+TXV | 8(0,1)*SB36070M17*** | 23600 | 15.2 | 9.5 | 9 | 23200 | 19200 | 82.76% | 2 | 18200 | R-454B
216987101 | 1.85 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | PL36H175P15*+TXV | 926TC30040V14*** | 22200 | 15.2 | 10.5 | 8.1 | 19200 | 18400 | 95.83% | 1.85 | 16700 | R-454B
212394512 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE35936 | TM9V060B12MP12 | 34000 | 17 | 9.5 | 8.5 | 32400 | 23800 | 73.46% | 2.06 | 24600 | R-410A
215487407 | 2.92 | Yes | No | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CHPEA4830*3A* | D*96VC1205DNA* | 35000 | 18.5 | 10.5 | 8.1 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
215669465 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0701716B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215669565 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0802120B* | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215669665 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *95CSU0802120B* | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
216680886 | 1.46 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CSPH*3012AL* | 59TP7A080V17**16 | 17500 | 15.5 | 10.5 | 8.1 | 18000 | 18100 | 100.6% | 2 | 12200 | R-410A
215933070 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0701412B* | 33000 | 18.5 | 10.5 | 9 | 35400 | 27200 | 76.84% | 1.9 | 31000 | R-454B
215933740 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU1002120A* | 34200 | 19.5 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.96 | 30000 | R-454B
215487441 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*80VC1005C*A* | 45500 | 16.5 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
216987133 | 1.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | C36A***L15*+TXV | 935SB36040M17*** | 22600 | 16 | 11 | 8.1 | 19200 | 18200 | 94.79% | 1.85 | 16700 | R-454B
216989682 | 1.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | PL36H175P15*+TXV | 82*SB36070V14*** | 22600 | 16 | 11 | 8.5 | 19200 | 18300 | 95.31% | 1.96 | 16600 | R-454B
216989684 | 1.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | V,C36H***P21*+TXV | 82*SB36070V14*** | 22600 | 16 | 11 | 8.5 | 19200 | 18300 | 95.31% | 1.96 | 16600 | R-454B
216678816 | 2.95 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *97VTN0601716A* | 35400 | 15.5 | 10 | 8.5 | 38500 | 34600 | 89.87% | 1.78 | 29400 | R-410A
213781090 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L24A*+WALLCON | *80CTL0902120B* | 31800 | 17 | 11 | 8.1 | 32800 | 24200 | 73.78% | 1.88 | 31000 | R-410A
216974397 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | PL48H210P75*+TXV | 83*CA48060C17*** | 44000 | 17 | 9.5 | 9 | 46500 | 33800 | 72.69% | 2.04 | 41500 | R-454B
216974412 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | PL60H210P17*+TXV | 83*CA60080C21*** | 45000 | 18 | 10 | 9 | 45000 | 33000 | 73.33% | 2.08 | 40500 | R-454B
216974444 | 3.75 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | V,C60H210P29*+TXV | 83*CB60080C21*** | 45000 | 18 | 9 | 9 | 45000 | 33000 | 73.33% | 2.06 | 40500 | R-454B
215487448 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA4830*3A* | D*80VC0805C*A* | 45500 | 16.5 | 10 | 8.5 | 46000 | 33600 | 73.04% | 2 | 28400 | R-32
215727974 | 4.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36(1,2)60+TXV | Z8ES100C20SMPS1 | 51500 | 18 | 11 | 8.3 | 51500 | 38000 | 73.79% | 1.96 | 35600 | R-454B
210868919 | 4.42 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA | FCCA6021SZEA | FF100215LT80X | 53000 | 19 | 10 | 8.1 | 52500 | 50000 | 95.24% | 1.9 | 50500 | R-410A
215487484 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80VC0603B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
212596705 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | F,PE*G34936 |  | 33600 | 18 | 9.5 | 8.4 | 32200 | 23400 | 72.67% | 2.1 | 24400 | R-410A
213614477 | 1.98 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YZT48B21 | D(A,C,E)60D44+TDR | TM9Y080C16MP11 | 23800 | 16 | 12.6 | 8.5 | 47500 | 34600 | 72.84% | 3.1 | 33400 | R-410A
216766670 | 4.38 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S9X1C100U5PSB | 52500 | 15.2 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.21 | 34400 | R-454B
216766686 | 4.33 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S9X2D120U5PSB | 52000 | 15.2 | 11.2 | 9 | 50500 | 38500 | 76.24% | 2.23 | 33600 | R-454B
216766736 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S9X2D120U5PSB | 51000 | 15.2 | 11.2 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34000 | R-454B
216766750 | 4.38 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S9X1C100U5PSB | 52500 | 15.2 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.21 | 34400 | R-454B
216770078 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S9V2D120U5VSB | 51500 | 15.2 | 11.2 | 9 | 51500 | 39000 | 75.73% | 2.2 | 34200 | R-454B
214505205 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA2422*4B* | D*96VC1005CNA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214505254 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA3026*4B* | D*96VC0603BNA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
215669871 | 2.78 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN0801714B* | 33400 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215669903 | 2.68 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0401410B* | 32200 | 15.2 | 9 | 8.5 | 36200 | 25800 | 71.27% | 1.76 | 31200 | R-454B
214573668 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3721AL*+UI | 58TN*B070C21**20 | 32800 | 17.5 | 11 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
214573918 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4821AL*+UI | 59CU5B080C21**20 | 32200 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
212480007 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 58TP*A090V17**16 | 23800 | 17 | 10.5 | 8.1 | 24400 | 23000 | 94.26% | 1.94 | 18000 | R-410A
212480050 | 2.02 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59SC5B040E17**12 | 24200 | 15.2 | 9.5 | 8.5 | 24800 | 22200 | 89.52% | 1.84 | 18300 | R-410A
212988803 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *95MSU0401712A* | 17700 | 16.5 | 10.5 | 8.1 | 17700 | 17800 | 100.6% | 2.14 | 12000 | R-410A
215669735 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN1202422B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
216972958 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H210P75*+TXV | 59TN7A100C21**22 | 43500 | 21 | 10.5 | 9.5 | 46000 | 36000 | 78.26% | 2 | 38500 | R-454B
215934810 | 2.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CTL0451712B* | 35200 | 21 | 11.7 | 8.5 | 39000 | 29400 | 75.38% | 2 | 33600 | R-454B
215935110 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 33000 | R-454B
215933790 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0901716B* | 34200 | 19.5 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.94 | 30000 | R-454B
212361450 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE31930 | BGH96M080B3B | 22800 | 18 | 11.5 | 8.65 | 22200 | 17000 | 76.58% | 1.84 | 19000 | R-410A
216766935 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S8V2A040M3PCB | 32600 | 16 | 11.7 | 8.5 | 33200 | 24400 | 73.49% | 2.04 | 21400 | R-454B
216766951 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S8V2C100M5PDB | 32600 | 16 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.12 | 21200 | R-454B
216766986 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD05AS3 | S8V2C080M5PCB | 32600 | 16 | 11.7 | 8.1 | 33400 | 24400 | 73.05% | 1.98 | 21600 | R-454B
216767002 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S9X2C100D5PSB | 34400 | 16 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.15 | 21400 | R-454B
216767004 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8V2C080M5PDB | 34200 | 17 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
216770109 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TAMXD05AV41 |  | 33800 | 16.5 | 12 | 8.7 | 32800 | 24000 | 73.17% | 2.17 | 21200 | R-454B
212348380 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | LEW30D4 |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
215938036 | 3.79 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL1352422B* | 45500 | 21 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.95 | 43000 | R-454B
216734143 | 1.83 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *96VSN0401410B* | 22000 | 15.5 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
216732637 | 1.82 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M14A* | *96VTN0601412B* | 21800 | 15.5 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 17900 | R-454B
216732537 | 1.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M14A* | *80CTL0701412B* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 17900 | R-454B
216732803 | 1.82 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *80CTL0901716B* | 21800 | 15.5 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.98 | 17900 | R-454B
215487458 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA6030*3A* | D*96VC0804CNA* | 45500 | 16.2 | 10 | 8.5 | 46500 | 33600 | 72.26% | 2 | 29000 | R-32
215669983 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0702120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
216974446 | 3.71 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C48A***L15*+TXV | 83*CB60080C21*** | 44500 | 17 | 9.5 | 9 | 46500 | 33400 | 71.83% | 2.06 | 41500 | R-454B
216974463 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | V,C48H210P16*+TXV | 83*CB60100C21*** | 44000 | 17 | 9.5 | 9 | 46500 | 33600 | 72.26% | 2.04 | 41500 | R-454B
215674565 | 3.79 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0602120B* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34200 | 71.25% | 2.06 | 42500 | R-454B
212624700 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624716 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TPLC100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624736 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624750 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TPLC100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
216735948 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *95MSU1002122A* | 23600 | 17 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.96 | 17700 | R-454B
213258324 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE34936 | *96VSN0601714A* | 23800 | 16 | 10 | 8.5 | 25200 | 23600 | 93.65% | 1.98 | 18500 | R-410A
213305981 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | CE3005A+TXV |  | 23600 | 17 | 10 | 9 | 25600 | 25200 | 98.44% | 2.14 | 18600 | R-410A
213312931 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936+AEFE4B* |  | 34000 | 18 | 10.5 | 8.7 | 31600 | 22800 | 72.15% | 2.1 | 23600 | R-410A
213258237 | 1.48 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG33936 | *96VSN0601714A* | 17700 | 16 | 10.5 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11400 | R-410A
213258270 | 1.46 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE31930 | *96VTN0601412A* | 17500 | 16 | 10 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
213352712 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 59TP6C100V21**20 | 23200 | 17 | 10 | 8.5 | 24600 | 24200 | 98.37% | 2.04 | 18100 | R-410A
215941590 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X48M24A*+WALLCON | *96CTN0802120B* | 44500 | 20 | 11 | 8.1 | 52000 | 38000 | 73.08% | 1.9 | 43500 | R-454B
213258321 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG33936 | *96VSN0601714A* | 23800 | 16 | 10 | 8.5 | 25200 | 23600 | 93.65% | 1.98 | 18500 | R-410A
213258354 | 1.93 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32936 | *96VTN0601412A* | 23200 | 16 | 10 | 8.5 | 24800 | 25200 | 101.6% | 2.14 | 18300 | R-410A
215935240 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *95CSU0601716B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33200 | R-454B
215669053 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CMN0801714B* | 34200 | 18 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215669085 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *96CTN1002122B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215669235 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0801714B* | 33600 | 17.5 | 9.5 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
212498516 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CE3005C+TXV |  | 23600 | 17 | 10 | 9 | 25600 | 25200 | 98.44% | 2.14 | 18600 | R-410A
212498509 | 1.48 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CE2403C+TXV |  | 17700 | 17 | 11 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
215669165 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0902120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215942576 | 3 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *95CSU0802120B* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215669783 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0701716B* | 33600 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.78 | 31000 | R-454B
215669815 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL1102120B* | 33800 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
213781290 | 2.68 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L21A*+WALLCON | *80CTL0701716B* | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.96 | 31400 | R-410A
213781640 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X61L21A*+WALLCON | *96CTN0801714B* | 33000 | 17 | 11 | 8.1 | 32000 | 25000 | 78.12% | 1.96 | 31400 | R-410A
215937110 | 3.58 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVM5X48M21A*+WALLCON | *96CTN0801714B* | 43000 | 19 | 11 | 8.1 | 53000 | 37600 | 70.94% | 2 | 42500 | R-454B
215937330 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0901716B* | 44500 | 20.5 | 11.5 | 8.1 | 53500 | 37600 | 70.28% | 1.95 | 43000 | R-454B
215936910 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN0801714B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.04 | 33000 | R-454B
216675453 | 2.12 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X37M21A* | *80CSU0401712A* | 25400 | 16.5 | 10 | 9 | 23400 | 19200 | 82.05% | 2.06 | 18600 | R-454B
215674477 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0702120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215487475 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80VC0805C*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215670119 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN1202422B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215933180 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN0602120B* | 33000 | 18.5 | 11 | 9 | 35400 | 27200 | 76.84% | 1.92 | 31000 | R-454B
215932830 | 2.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0801714B* | 34200 | 20 | 11.5 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30200 | R-454B
215670169 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0701412B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
216732839 | 1.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *95CSU0601716B* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 18000 | R-454B
216732939 | 1.85 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *96MSN0801716A* | 22200 | 15.5 | 10.5 | 8.5 | 21200 | 19200 | 90.57% | 1.96 | 18000 | R-454B
216733575 | 1.9 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *96VTN0601412B* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216733607 | 1.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *97VTN0601716A* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17500 | R-454B
215487402 | 2.9 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA4830*3A* | D*80VC0804C*A* | 34800 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
213204349 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0802120A* | 23400 | 16 | 9.5 | 8.1 | 24800 | 26200 | 105.6% | 2.75 | 25200 | R-410A
215487453 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA4830*3A* | D*96VC1005DNA* | 45500 | 16.5 | 10 | 8.5 | 46000 | 33600 | 73.04% | 2 | 28400 | R-32
215487455 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA6030*3A* | D*80VC0804C*A* | 45500 | 16.5 | 10 | 8.5 | 46500 | 33600 | 72.26% | 2 | 29000 | R-32
215487464 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*96VC0804CNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215940220 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0801716A* | 34000 | 19 | 11 | 9 | 34800 | 26400 | 75.86% | 1.92 | 30400 | R-454B
215669967 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0701412B* | 33800 | 16.5 | 9 | 8.5 | 35800 | 25400 | 70.95% | 1.78 | 30800 | R-454B
215674560 | 3.79 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0602120B* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34200 | 71.25% | 2.06 | 42500 | R-454B
216971965 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C48A***L16*+TXV | 58CU*B040C17**12 | 48500 | 18 | 11.5 | 11.5 | 49500 | 50500 | 102% | 1.98 | 48500 | R-454B
216971998 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | A60VHA*+TXV | 58CU*B100C21**20 | 49500 | 19 | 11.5 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216972098 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | V,C60H210P29*+TXV | 58TN*B110C21**20 | 48500 | 19 | 11 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
214573248 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CSPH*6012AL*+UI | 58TN*B070C21**20 | 33000 | 17 | 11 | 8.5 | 32200 | 25000 | 77.64% | 2 | 31400 | R-410A
214573568 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CNPV*6024AL*+UI | 59CU5B100C21**22 | 32800 | 19 | 12 | 8.5 | 32200 | 24600 | 76.4% | 1.98 | 31200 | R-410A
215431165 | 3.83 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | V,R60H210P179+AEFE5* |  | 46000 | 17 | 9.5 | 8.3 | 45000 | 32600 | 72.44% | 1.86 | 30000 | R-410A
215670039 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *95CSU1002122B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
216971962 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL48H210P75*+TXV | 58CU*B040C17**12 | 48500 | 18 | 11.5 | 11.5 | 49500 | 50500 | 102% | 1.98 | 48500 | R-454B
216972135 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P17*+TXV | 59CU5B080C21**20 | 49000 | 19 | 10.5 | 10.5 | 51000 | 52500 | 102.9% | 1.92 | 50000 | R-454B
215487410 | 2.92 | Yes | No | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CHPEA4830*3A* | D*96VC0804CNA* | 35000 | 18.5 | 10.5 | 8.1 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216972296 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P17*+TXV | 59TN6C080C17**14 | 48000 | 18 | 12 | 9 | 48500 | 49500 | 102.1% | 1.96 | 48000 | R-454B
214862363 | 2.68 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | H,PG48936 | 987MC60060C21*** | 32200 | 17 | 11.5 | 8.1 | 31400 | 24600 | 78.34% | 1.94 | 30800 | R-410A
216988975 | 1.48 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ18AA3 | PL36H175P15*+TXV | 8(0,1)*SB36070M14*** | 17800 | 15.2 | 11 | 10.5 | 18400 | 17300 | 94.02% | 2 | 13900 | R-454B
216681531 | 1.95 | No | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X24AAL | *97VTN0802120A* | 23400 | 16 | 9.8 | 9 | 26000 | 23800 | 91.54% | 1.86 | 19100 | R-410A
213366552 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | A36VCA+TXV | Z8ES080B12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
212624752 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TPLC100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624801 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TL8E080C16UH11 | 30600 | 17.1 | 9.6 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624817 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TL8E080C16UH11 | 33400 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624853 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.4 | 34000 | 30200 | 88.82% | 2.83 | 27000 | R-410A
212624883 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | CP9C100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624886 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | CP9C100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624936 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624968 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM8Y100C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625018 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y100C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625036 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625050 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9V100C16MP12 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625117 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TP9C100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625152 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TP9C100C16MP13 | 33400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625202 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625267 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TL8E100C20UH11 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
215415511 | 3.88 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | DFVE60DP1300A* |  | 46500 | 17.5 | 10 | 8.8 | 47500 | 33600 | 70.74% | 2 | 29000 | R-32
212614017 | 2.45 | Yes | No | MOOVAIR | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DMA30HOS20230E7 | HG33936+TD |  | 29400 | 15.2 | 10 | 9.35 | 31200 | 26600 | 85.26% | 1.8 | 21600 | R-410A
215674668 | 3.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN1202422B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215675438 | 3.88 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *97CMN0602120B* | 46500 | 18 | 9.5 | 9 | 50000 | 37000 | 74% | 1.98 | 46000 | R-454B
215675568 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CTL0902120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
216972344 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L18*+TXV | 59TN6C100C21**22 | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
215669615 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU1002120A* | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
216972351 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P29*+TXV | 59TN7A080C21**20 | 48000 | 19 | 10.5 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
216972353 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | V,C60H210P29*+TXV | 59TN7A080C21**20 | 48000 | 19 | 10.5 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
215933980 | 3.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU1002120A* | 43500 | 20.5 | 10.5 | 9.5 | 48000 | 36600 | 76.25% | 2 | 39500 | R-454B
215934300 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU1002120A* | 45500 | 21 | 11 | 9.5 | 48500 | 36800 | 75.88% | 2 | 40000 | R-454B
215934450 | 3.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0901716B* | 43500 | 20 | 11 | 9 | 48500 | 35800 | 73.81% | 1.86 | 38000 | R-454B
215934500 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN1002122B* | 44000 | 20 | 10.5 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
215934600 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0801714B* | 44000 | 19.5 | 11 | 9 | 49000 | 36400 | 74.29% | 1.84 | 39000 | R-454B
215934650 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X30M17A*+WALLCON | *97CMN0601714B* | 34000 | 20 | 11 | 8.1 | 38000 | 27200 | 71.58% | 2 | 30600 | R-454B
215934950 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *96CTN1002122B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
212625269 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TL8E100C20UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625354 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625469 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625585 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM8V120C20MP12 | 31200 | 16.4 | 8.8 | 8.4 | 32200 | 27600 | 85.71% | 2.7 | 25000 | R-410A
212625587 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8V120C20MP12 | 29600 | 15.9 | 8 | 8.5 | 32200 | 27600 | 85.71% | 2.7 | 25000 | R-410A
212625654 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TMLV120C20MP12 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625670 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625671 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CPLC100C20MP13 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
214272298 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | V,C36H175P159 | 58TN*B090C17**16 | 32200 | 17 | 11.7 | 8.5 | 31000 | 24600 | 79.35% | 1.98 | 30400 | R-410A
214272299 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | C36A***L539 | 58TN*B090C17**16 | 32400 | 18 | 11.5 | 8.5 | 30400 | 24600 | 80.92% | 2 | 30200 | R-410A
213366533 | 1.82 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B241 | H,YG7J936 | Z8ET080B12LMPS1 | 21800 | 17 | 9.5 | 8.1 | 22000 | 15600 | 70.91% | 1.86 | 14500 | R-410A
214271649 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | C36A***L159 | 58TN*B070C14**12 | 32600 | 19 | 11.7 | 9 | 35200 | 27400 | 77.84% | 2.04 | 31800 | R-410A
214271699 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | C36A***L539 | 58TN*B090C17**16 | 33800 | 20 | 12.5 | 9 | 34800 | 27000 | 77.59% | 2.06 | 31400 | R-410A
215942476 | 2.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *80CSU0601716A* | 35800 | 22 | 12 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
215942626 | 2.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0802120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
214385722 | 2.58 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | H,YA10936 | *80CSU0601716A* | 31000 | 17 | 10.5 | 8.1 | 31600 | 24000 | 75.95% | 1.86 | 30200 | R-410A
215675638 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN1002122B* | 48000 | 19 | 10.5 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215668919 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CMN1002122B* | 33200 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.84 | 31000 | R-454B
216973024 | 4.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | PL60H210P29*+TXV | 59MN7C100C21**22 | 54500 | 18 | 11 | 8.5 | 58500 | 46000 | 78.63% | 2.02 | 47000 | R-454B
215224751 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG7J936 | 59MN7C060C17**14 | 23200 | 19 | 13 | 10 | 25200 | 19600 | 77.78% | 2.36 | 24200 | R-410A
215870972 | 3.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH600C*C+TXV | Y91E100C20SMPS1 | 45000 | 17 | 11.5 | 8.45 | 45000 | 33600 | 74.67% | 1.98 | 32800 | R-454B
215731274 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | V,Y36H175P78*+TXV+AEFE4B* |  | 34000 | 19 | 11.7 | 9 | 30800 | 24800 | 80.52% | 2.1 | 25600 | R-454B
215870955 | 2.63 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CV361**C+TXV | YPLC080B12MP13 | 31600 | 16 | 10.5 | 8.2 | 28600 | 24800 | 86.71% | 1.94 | 25800 | R-454B
215870937 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH360**C+TXV | YP9C060B12MP13 | 22200 | 17 | 11 | 8.65 | 21200 | 17200 | 81.13% | 1.94 | 16900 | R-454B
212625688 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | CPLC120C20MP13 | 32400 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625704 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8V100C20MP12 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625720 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8V120C20MP12 | 31400 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625721 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8V120C20MP12 | 31400 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625736 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8V120C20MP12 | 32600 | 16.5 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625738 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8V120C20MP12 | 32800 | 16.5 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625754 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TMLV120C20MP12 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625820 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9Y120D20MP11 | 32800 | 16.5 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625822 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9Y120D20MP11 | 33000 | 16.5 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625836 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625837 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | CP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625853 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V120D20MP12 | 31600 | 17 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625887 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TP9C120D20MP13 | 32200 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625888 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
215670489 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU1002122B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
215670589 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1002122B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 30000 | R-454B
215670139 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0601716A* | 34000 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30600 | R-454B
215670389 | 2.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0601716A* | 34600 | 17 | 9.5 | 8.5 | 34600 | 25000 | 72.25% | 1.8 | 30000 | R-454B
215669935 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU0401712A* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
216972728 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C48A***L15*+TXV | 58CU*B060C17**16 | 43500 | 21 | 11 | 9.5 | 46000 | 36200 | 78.7% | 1.9 | 38500 | R-454B
216972739 | 3.58 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H175P78*+TXV | 58TN*B070C17**16 | 43000 | 20 | 10.5 | 9 | 46500 | 36800 | 79.14% | 2 | 39000 | R-454B
216972762 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H175P15*+TXV | 58TN*B090C17**16 | 43500 | 20 | 11 | 9 | 46500 | 35400 | 76.13% | 1.86 | 37000 | R-454B
216972778 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H210P16*+TXV | 58TN*B090C21**20 | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 1.92 | 38000 | R-454B
215224769 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG49960 | 59MN7C120C24**22 | 44500 | 21 | 12 | 9.5 | 44000 | 36000 | 81.82% | 2.26 | 42500 | R-410A
216972131 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C48A***L16*+TXV | 59CU5B080C21**20 | 48500 | 18 | 10.5 | 10.5 | 50500 | 52000 | 103% | 1.96 | 49500 | R-454B
216972267 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L18*+TXV | 59MN7C100C21**22 | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216972349 | 4.04 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | V,C60H245P76*+TXV | 59TN6C120C24**22 | 48500 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
212625956 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9E100C20MP12 | 32400 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626036 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8Y060A12MP11 | 32400 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626037 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8Y060A12MP11 | 30400 | 17.6 | 9.6 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626038 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626039 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8Y060A12MP11 | 32400 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626069 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8Y080B12MP11 | 31000 | 17.7 | 9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626072 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8Y080B12MP11 | 33000 | 18 | 10 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626073 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8Y080B12MP11 | 32600 | 18 | 10 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
209880045 | 3.71 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF96TV510021M4S*A | 44500 | 19 | 10.9 | 8.5 | 43500 | 45000 | 103.4% | 2 | 41000 | R-410A
215726301 | 4.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV+AEFE5* |  | 53500 | 19 | 12 | 9 | 51000 | 37400 | 73.33% | 2.1 | 35200 | R-454B
214389872 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG53936 | 58TN*B070C14**12 | 24200 | 20 | 13 | 10.5 | 24800 | 19300 | 77.82% | 2.54 | 23800 | R-410A
214389889 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG32936 | 58TN*B110C21**20 | 23200 | 20 | 13 | 10 | 25000 | 19300 | 77.2% | 2.44 | 23800 | R-410A
214271581 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | C36A***L139 | 58TN*B045C17**12 | 23200 | 20 | 12.5 | 10.5 | 25000 | 19500 | 78% | 2.42 | 24000 | R-410A
213815131 | 2.83 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CA*F3137*6A*+MBVK12BP1X00A*+TXV |  | 34000 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213773040 | 1.95 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X36L21A*+WALLCON | *80CTL0451712B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213773340 | 2.03 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X37L21A*+WALLCON | *97CMN1002122B* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
215675788 | 3.96 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN0602120B* | 47500 | 18.5 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215735534 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE33*36+TXV-BLEED | TM9V040A10MP12 | 22400 | 16 | 10.5 | 8.8 | 21400 | 17100 | 79.91% | 1.96 | 16800 | R-454B
216972780 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L16*+TXV | 58TN*B090C21**20 | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 1.92 | 38000 | R-454B
216972805 | 3.5 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL48H210P75*+TXV | 59CU5B060C17**16 | 42000 | 20 | 10 | 9.4 | 47000 | 36200 | 77.02% | 1.98 | 38500 | R-454B
216972819 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L16*+TXV | 59CU5B080C21**20 | 43500 | 21 | 10.5 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972837 | 3.58 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL60H210P29*+TXV | 59MN7C060C21**20 | 43000 | 20 | 10 | 9.5 | 46500 | 37000 | 79.57% | 2 | 39500 | R-454B
216972869 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C48A***L16*+TXV | 59MN7C080C21**20 | 43500 | 20 | 10.5 | 9.5 | 46000 | 36200 | 78.7% | 2 | 38500 | R-454B
216972889 | 3.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL60H210P29*+TXV | 59TN6C080C17**14 | 42500 | 20 | 11 | 9 | 46500 | 34800 | 74.84% | 2 | 34800 | R-454B
216972894 | 3.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C48A***L15*+TXV | 59TN6C080C17**14 | 42500 | 20 | 11 | 9 | 46500 | 34800 | 74.84% | 2 | 34800 | R-454B
213772446 | 2.02 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**B* | CSPH*4812AL*+UI | 88*TB48070C17*** | 24200 | 16.5 | 10.5 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
212626237 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626272 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8E120C16MP11 | 32000 | 18 | 10 | 8.1 | 33600 | 28600 | 85.12% | 2.64 | 26000 | R-410A
212626288 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.1 | 33600 | 28600 | 85.12% | 2.67 | 26000 | R-410A
212626321 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM8E080B12MP11 | 29800 | 17.4 | 9 | 8.3 | 33600 | 28000 | 83.33% | 2.59 | 25600 | R-410A
212626338 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626370 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TL8E080C16UH11 | 29600 | 16.9 | 9.5 | 8.3 | 33600 | 27600 | 82.14% | 2.64 | 25400 | R-410A
212626388 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9E100C16MP12 | 33000 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626405 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8Y100C20MP11 | 32200 | 18 | 9.5 | 8.3 | 33600 | 30000 | 89.29% | 2.81 | 26800 | R-410A
214389972 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | H,PG53936 | 58TN*B070C17**16 | 32400 | 17 | 11.5 | 8.5 | 30600 | 24600 | 80.39% | 1.98 | 30400 | R-410A
214272383 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | C36A***L539 | 59TN6C100C21**22 | 32400 | 18 | 11.5 | 8.5 | 30400 | 24400 | 80.26% | 2 | 30200 | R-410A
216997234 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | H,PG7J*36+TXV | 59MN7C060C17**14 | 23000 | 17 | 10 | 9 | 22200 | 16300 | 73.42% | 1.98 | 19000 | R-454B
215675988 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL0902120B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.1 | 46500 | R-454B
215676438 | 3.96 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0451712B* | 47500 | 18 | 9.5 | 9 | 50000 | 37600 | 75.2% | 1.98 | 47500 | R-454B
215676908 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN0602120B* | 48000 | 19 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215676958 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *96CTN1202422B* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
215675368 | 3.92 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CSU0802120A* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
212975756 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *96VTN0601412B* | 23400 | 16.5 | 10 | 8.1 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
216972905 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL48H210P75*+TXV | 59TN6C080C21**20 | 43500 | 20 | 10.5 | 9.5 | 46000 | 36200 | 78.7% | 2 | 38500 | R-454B
216972971 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | PL60H210P17*+TXV | 58TN*B070C21**20 | 55500 | 18 | 11 | 8.1 | 58500 | 46000 | 78.63% | 1.95 | 46500 | R-454B
216972973 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | C60A***L18*+TXV | 58TN*B070C21**20 | 55500 | 18 | 11 | 8.1 | 58500 | 46000 | 78.63% | 1.95 | 46500 | R-454B
216972978 | 4.58 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | C60A***L16*+TXV | 58TN*B090C21**20 | 55000 | 18 | 11 | 8.5 | 58500 | 45000 | 76.92% | 2.06 | 46000 | R-454B
215487385 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CHPEA3026*3A* | D*80VC0604B*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
216972939 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C48A***L53*+TXV | 59TN7A080C17**16 | 44500 | 20 | 11 | 9 | 47000 | 37200 | 79.15% | 2 | 39500 | R-454B
216972955 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | A60VHA*+TXV | 59TN7A100C21**22 | 44500 | 21 | 11 | 9.5 | 46000 | 36000 | 78.26% | 2 | 38000 | R-454B
216972996 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | PL60H210P17*+TXV | 59CU5B080C21**20 | 55500 | 18 | 11 | 8.1 | 58500 | 45500 | 77.78% | 1.95 | 46000 | R-454B
216973014 | 4.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | C60A***L18*+TXV | 59MN7C060C21**20 | 54500 | 18 | 10 | 8.5 | 59000 | 47000 | 79.66% | 2 | 48000 | R-454B
212626406 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8Y100C20MP11 | 32200 | 18 | 9.5 | 8.3 | 33600 | 30000 | 89.29% | 2.81 | 26800 | R-410A
212626422 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM9V100C20MP12 | 29200 | 16.7 | 8.9 | 8.5 | 33600 | 28200 | 83.93% | 2.7 | 25800 | R-410A
216974745 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | V,C36H175P15*+TXV | 83*CA36040C17*** | 33400 | 20 | 11.5 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
216974746 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | PL36H210P74*+TXV | 83*CA36040C17*** | 32800 | 20 | 11 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
213145924 | 2.53 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | C36A***L159+AEFE3A* |  | 30400 | 15.2 | 9 | 8.5 | 33400 | 27000 | 80.84% | 1.82 | 22600 | R-410A
216972421 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L53*+TXV | 58CU*B040C17**12 | 33800 | 20 | 11.7 | 9.5 | 32600 | 25600 | 78.53% | 2.06 | 29000 | R-454B
216972485 | 2.78 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L15*+TXV | 58TN*B070C14**12 | 33400 | 19 | 11 | 9 | 33600 | 26600 | 79.17% | 1.92 | 30000 | R-454B
216972512 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L15*+TXV | 58TN*B070C17**16 | 32600 | 19 | 11 | 9.5 | 33600 | 26600 | 79.17% | 2 | 30000 | R-454B
216680586 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3012AL* | 59TP7A080V17**16 | 23800 | 16 | 10 | 9 | 26000 | 22800 | 87.69% | 1.76 | 19100 | R-410A
216972781 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL60H210P17*+TXV | 58TN*B090C21**20 | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972784 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L19*+TXV | 58TN*B090C21**20 | 45000 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972798 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C60H245P76*+TXV | 58TN*B135C24**22 | 44000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 2 | 38000 | R-454B
216972817 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H210P16*+TXV | 59CU5B080C21**20 | 43500 | 21 | 10.5 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972834 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C60H210P17*+TXV | 59CU5B100C21**22 | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972835 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L18*+TXV | 59CU5B100C21**22 | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972848 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L18*+TXV | 59MN7C060C21**20 | 43500 | 20 | 10 | 9.5 | 46500 | 37000 | 79.57% | 2 | 39500 | R-454B
216972849 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L19*+TXV | 59MN7C060C21**20 | 44000 | 20 | 10 | 9.5 | 46500 | 37000 | 79.57% | 2 | 39500 | R-454B
216972932 | 3.58 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H175P78*+TXV | 59TN7A080C17**16 | 43000 | 20 | 10.5 | 9.5 | 46500 | 37000 | 79.57% | 2 | 39000 | R-454B
216972965 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L19*+TXV | 59TN7A100C21**22 | 44500 | 21 | 11 | 9.5 | 46000 | 36000 | 78.26% | 2 | 38000 | R-454B
216972400 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | A36VCA*+TXV | 58CU*B040C17**12 | 32800 | 20 | 11.5 | 9.5 | 33200 | 26200 | 78.92% | 2.02 | 29600 | R-454B
216972447 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L53*+TXV | 58CU*B060C17**16 | 33800 | 20 | 11.7 | 9.5 | 32800 | 25600 | 78.05% | 2.06 | 29000 | R-454B
216972465 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P15*+TXV | 58TN*B045C17**12 | 33000 | 19 | 10.5 | 9 | 33800 | 26800 | 79.29% | 1.9 | 30000 | R-454B
216972467 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 58TN*B045C17**12 | 32200 | 19 | 10.5 | 9 | 34200 | 27200 | 79.53% | 1.88 | 30400 | R-454B
216972500 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H175P14*+TXV | 58TN*B070C17**16 | 32600 | 19 | 11 | 9.5 | 33600 | 26600 | 79.17% | 2 | 30000 | R-454B
216972601 | 2.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 59CU5B080C21**20 | 31600 | 19 | 11 | 9.35 | 32800 | 25600 | 78.05% | 2.02 | 29000 | R-454B
216972631 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L15*+TXV | 59MN7C060C17**14 | 32800 | 19 | 11 | 9.5 | 32400 | 25600 | 79.01% | 2.04 | 28800 | R-454B
216972634 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P45*+TXV | 59MN7C060C17**14 | 33800 | 19 | 11 | 9.5 | 32600 | 25800 | 79.14% | 2.06 | 29000 | R-454B
216972648 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P13*+TXV | 59MN7C080C17**14 | 32400 | 19 | 11 | 9.5 | 33800 | 26800 | 79.29% | 2 | 30000 | R-454B
216972682 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P45*+TXV | 59TN6C080C17**14 | 33200 | 20 | 11 | 9.5 | 33200 | 26200 | 78.92% | 2.02 | 29600 | R-454B
216972684 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 59TN6C080C21**20 | 32800 | 20 | 11 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29200 | R-454B
216972698 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 59TN7A060C17**16 | 32400 | 19 | 10.5 | 9 | 33800 | 26600 | 78.7% | 1.9 | 30000 | R-454B
216972700 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P13*+TXV | 59TN7A060C17**16 | 32400 | 19 | 10.5 | 9 | 34000 | 27000 | 79.41% | 1.88 | 30400 | R-454B
216972717 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H210P74*+TXV | 59TN7A080C21**20 | 32800 | 20 | 11 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29200 | R-454B
215938386 | 3.79 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN1002122B* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.9 | 43500 | R-454B
213872342 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG9J936 | TM9V100C16MP12 | 34000 | 17 | 10 | 8.5 | 32400 | 23600 | 72.84% | 2.1 | 24400 | R-410A
215735564 | 3.63 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE1K*48+TXV-BLEED | TM9Y100C16MP11 | 43500 | 16 | 10.5 | 8.45 | 42500 | 33400 | 78.59% | 1.98 | 32000 | R-454B
216981026 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P19*+TXV-BLEED | Y92E080C16SMPS1 | 44000 | 18 | 11 | 9 | 43000 | 32400 | 75.35% | 2 | 32200 | R-454B
216997200 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | H,PG35*48+TXV | 58TN*B090C17**16 | 43500 | 20 | 11 | 9 | 46500 | 35400 | 76.13% | 1.86 | 37000 | R-454B
216997065 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA048A*030* | H,PG48*60+TXV | 58TN*B110C21**20 | 45000 | 18 | 10 | 9 | 45500 | 33000 | 72.53% | 2.08 | 40500 | R-454B
214389921 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG3K960 | 58TN*B070C17**16 | 44500 | 20 | 11 | 9 | 44500 | 36200 | 81.35% | 2.3 | 42500 | R-410A
215669155 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0901716B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215934710 | 2.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X32M17A*+WALLCON | *96CTN0601714B* | 35200 | 21 | 11.7 | 8.5 | 38000 | 28000 | 73.68% | 2.06 | 32000 | R-454B
215669005 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL0902120B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215933370 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *95CSU0601716B* | 33400 | 18.5 | 11 | 9 | 35200 | 27000 | 76.7% | 1.92 | 31000 | R-454B
215933590 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0902120B* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30400 | R-454B
215669355 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU1002122B* | 34400 | 18 | 10 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
215669575 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN1002122B* | 34800 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215669625 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0702120B* | 34800 | 18.5 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215669675 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *95CSU1002122B* | 35000 | 18.5 | 10 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
215669759 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU1002120A* | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.78 | 30800 | R-454B
215828362 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | C60A***L169 | 59MN7C080C21**20 | 43500 | 21 | 11.7 | 9 | 44500 | 36000 | 80.9% | 2.26 | 42500 | R-410A
215676688 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CSU0601716A* | 48500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215934430 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU1002120A* | 44000 | 20 | 10.5 | 9 | 48500 | 36600 | 75.46% | 1.8 | 39500 | R-454B
215938390 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN1002122B* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.9 | 43500 | R-454B
216972630 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 59MN7C060C17**14 | 32400 | 19 | 10.5 | 9.5 | 32400 | 25600 | 79.01% | 2.04 | 28800 | R-454B
216972669 | 2.78 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L53*+TXV | 59TN6C060C17**14 | 33400 | 20 | 10.5 | 9.4 | 32200 | 25200 | 78.26% | 2.05 | 28600 | R-454B
216972696 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H175P15*+TXV | 59TN7A060C17**16 | 33000 | 19 | 11 | 9 | 33800 | 26600 | 78.7% | 1.9 | 30000 | R-454B
216972705 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L13*+TXV | 59TN7A080C17**16 | 32400 | 19 | 11 | 9.5 | 33600 | 26800 | 79.76% | 2 | 30000 | R-454B
216679410 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3617AL* | 59TP7A060V17**16 | 23600 | 17 | 10 | 9 | 25800 | 23200 | 89.92% | 1.82 | 18900 | R-410A
213145906 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129+AEFE3A* |  | 23600 | 17 | 10 | 9 | 25600 | 25200 | 98.44% | 2.14 | 18600 | R-410A
212498507 | 1.45 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CE1801C+TXV |  | 17400 | 17 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
213782160 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X48AAL+WALLCON | *97CMN1202422B* | 32600 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31600 | R-410A
213782310 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X60AAL+WALLCON | *97CMN1002122B* | 33000 | 16.5 | 11.5 | 8.1 | 32200 | 24800 | 77.02% | 2 | 31200 | R-410A
216681799 | 3.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *97VTN1002120A* | 36200 | 16.5 | 10 | 9 | 38000 | 34400 | 90.53% | 1.96 | 29000 | R-410A
214862347 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE9J936 | 987MC66120C24*** | 23800 | 16 | 11 | 8.1 | 19800 | 16200 | 81.82% | 1.96 | 19600 | R-410A
215669585 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0601714B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30200 | R-454B
215669095 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0401712A* | 33800 | 18 | 9.5 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
216972966 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C60H245P76*+TXV | 59TN7A120C24**22 | 43500 | 21 | 11 | 9.45 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
214574318 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 59TN6C080C21**20 | 32600 | 17.5 | 11 | 8.5 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
215669012 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL1102120B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215669028 | 2.87 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *95CSU0802120B* | 34400 | 17.5 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215669194 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0802120B* | 33800 | 17.5 | 9.5 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215669244 | 2.82 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0802120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215669394 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1202422B* | 34400 | 18.5 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215670319 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN1202422B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215670219 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL1102120B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
216973030 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | C60A***L18*+TXV | 59MN7C100C21**22 | 55500 | 18 | 11 | 8.5 | 58500 | 46000 | 78.63% | 2.02 | 47000 | R-454B
213258953 | 1.97 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VTN1002120A* | 23600 | 17 | 9.5 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
214385571 | 1.95 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,YE35936 | *95MSU0401712A* | 23400 | 17 | 10 | 8.5 | 24400 | 24000 | 98.36% | 2.02 | 18000 | R-410A
216776398 | 3.79 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | AD-61(P,U)******+TXV-BLEED | Y91E100C20SMPS1 | 45500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 32800 | R-454B
216977875 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH365B*C+TXV | Y91E060B12SMPS1 | 32800 | 16 | 10.5 | 8.4 | 29400 | 25000 | 85.03% | 1.98 | 26600 | R-454B
216776400 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | AD-37(P,U)******+TXV-BLEED | Y81E080B12SMPS1 | 32800 | 17 | 11.5 | 8.4 | 28800 | 24400 | 84.72% | 1.98 | 25800 | R-454B
216679872 | 3.03 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *97VTN0801716A* | 36400 | 15.5 | 10 | 9 | 38500 | 34400 | 89.35% | 1.96 | 29200 | R-410A
216679956 | 2.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *97VTN0801716A* | 35600 | 15.2 | 10 | 8.5 | 39000 | 34600 | 88.72% | 1.8 | 29400 | R-410A
212441627 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YE8J936 | TM9E040A10MP12 | 32200 | 17 | 9.5 | 8.5 | 32400 | 23000 | 70.99% | 1.98 | 24800 | R-410A
213753839 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SP6A100V21**20 | 35200 | 16 | 9.5 | 8.1 | 39000 | 31800 | 81.54% | 2.51 | 29400 | R-410A
212976039 | 1.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *96VTN0801716B* | 23600 | 17 | 10 | 8.5 | 26000 | 24200 | 93.08% | 2.02 | 19000 | R-410A
215441394 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CV365B*C+TXV+AEF48BXP* |  | 33000 | 19 | 11.5 | 8.85 | 29400 | 24800 | 84.35% | 1.98 | 24800 | R-454B
215441376 | 2.83 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | H,YG80736 | TM9E080C16MP12 | 34000 | 18 | 10 | 8.1 | 32000 | 23400 | 73.12% | 2.08 | 24200 | R-410A
215731722 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG53*48+TXV | Y81E120C16SMPS1 | 44000 | 18 | 12 | 8.5 | 42000 | 32600 | 77.62% | 2 | 31200 | R-454B
215735533 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE31*30+TXV-BLEED | TM9V040A10MP12 | 21800 | 16 | 10 | 8.5 | 21200 | 17100 | 80.66% | 1.9 | 16700 | R-454B
215679248 | 2.83 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *80CSU0601716B* | 34000 | 17 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.86 | 30600 | R-454B
215679298 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *80CSU0601716B* | 34600 | 17.5 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
210598028 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *95CSU1002122A* | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
210598048 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *97CMN0602120A* | 24000 | 16.5 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20600 | R-410A
216733492 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *96VSN0601412B* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216733810 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *80CSU0401712A* | 22800 | 17 | 11 | 8.5 | 21200 | 19000 | 89.62% | 1.94 | 17900 | R-454B
215675326 | 3.79 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1002122B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
216017532 | 1.92 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | V,Y36H175P13*+TXV-BLEED+TD |  | 23000 | 15.2 | 11 | 8.5 | 21400 | 17000 | 79.44% | 2 | 17800 | R-454B
216776393 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AD-34(P,U)******+TXV-BLEED | Y91E060B12SMPS1 | 23000 | 17 | 11.7 | 9.5 | 21400 | 18700 | 87.38% | 2 | 16900 | R-454B
215942526 | 2.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN0802120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215675346 | 3.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | FCMA5B60L0D*+WALLCON |  | 46500 | 19.5 | 10.5 | 9.5 | 47000 | 33000 | 70.21% | 2.2 | 41000 | R-454B
215668693 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL1102120B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215668741 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0801714B* | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
216736003 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96VTN0601716B* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216737066 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MS(N,L)0702116A* | 22400 | 15.2 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.9 | 17700 | R-454B
213881440 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P749 | 58TP*B090V21**20 | 35200 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
216980999 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | V,Y36H175P13*+TXV-BLEED | Y82E080B12LMPS1 | 23000 | 18 | 12 | 9.5 | 21400 | 18000 | 84.11% | 2 | 16800 | R-454B
213080824 | 3.05 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**4321AL* | 59SU5B080M21**20 | 36600 | 16 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2.08 | 29200 | R-410A
215487420 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CA*EA6030*3A* | D*96VC1005CNA* | 40500 | 16.5 | 10 | 8.8 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
216981012 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | V,Y36H175P38*+TXV-BLEED | Y92E060B12SMPS1 | 33400 | 18 | 11 | 8.5 | 30000 | 23800 | 79.33% | 2 | 27200 | R-454B
215487370 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*96VC0803BNA* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
213366553 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | A36VDA+TXV | Z8ES080B12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
215670369 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN1202422B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215933580 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0901716B* | 33600 | 19.5 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215933700 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN0601714B* | 33400 | 19 | 11 | 9 | 34200 | 26000 | 76.02% | 1.94 | 30000 | R-454B
215933750 | 2.82 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0451712B* | 33800 | 19 | 11 | 9 | 35200 | 26800 | 76.14% | 1.92 | 30800 | R-454B
215679348 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *96CTN0802120B* | 33200 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215679498 | 2.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0401712B* | 34000 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215679898 | 2.82 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN0601716A* | 33800 | 16 | 9 | 8.5 | 35600 | 25600 | 71.91% | 1.78 | 30800 | R-454B
215679948 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
215679998 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1002122A* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.82 | 30000 | R-454B
215678058 | 4.5 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0701716B* | 54000 | 16.5 | 9 | 8.5 | 59000 | 41500 | 70.34% | 1.9 | 51000 | R-454B
215682588 | 4.63 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CSU0802120B* | 55500 | 18.5 | 9 | 8.5 | 58500 | 41000 | 70.09% | 2.04 | 50500 | R-454B
215682638 | 4.63 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712B* | 55500 | 18 | 9 | 8.5 | 58500 | 41000 | 70.09% | 2.04 | 50500 | R-454B
215935480 | 3 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL1352422B* | 36000 | 22.5 | 12.5 | 8.5 | 37600 | 28200 | 75% | 2.04 | 32200 | R-454B
216972982 | 4.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | C60A***L19*+TXV | 58TN*B090C21**20 | 56500 | 19 | 11.5 | 8.5 | 58500 | 46000 | 78.63% | 2.04 | 46500 | R-454B
216776394 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AD-30(P,U)******+TXV-BLEED | Y92E060B12SMPS1 | 22400 | 17 | 11 | 9.25 | 21400 | 18100 | 84.58% | 1.96 | 16900 | R-454B
215669245 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0802120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215669645 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1102120B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
215487437 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA6030*3A* | D*96VC1005DNA* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
213611678 | 1.92 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | LEC309C05 |  | 23000 | 19 | 13 | 8.4 | 20600 | 14500 | 70.39% | 2.04 | 13400 | R-410A
215669830 | 2.8 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU0601716B* | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215670178 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0701716B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
215731481 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG55*60+TXV | TM8V120C20MP12 | 53000 | 19 | 11 | 8.5 | 52000 | 38500 | 74.04% | 2 | 36200 | R-454B
215731496 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG55*60+TXV | TM9V120D20MP12 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36600 | R-454B
215731499 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG74*60+TXV-BLEED | TM9V120D20MP12 | 53000 | 19 | 11 | 8.5 | 52000 | 38500 | 74.04% | 2 | 36400 | R-454B
215731514 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG54*60+TXV | TM9Y080C16MP11 | 44000 | 17 | 11 | 8.5 | 42500 | 33400 | 78.59% | 2 | 32000 | R-454B
215731531 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG86*48+TXV-BLEED | TM9Y080C16MP11 | 44000 | 17 | 11 | 8.5 | 42500 | 33400 | 78.59% | 2 | 32000 | R-454B
215933830 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU0601716B* | 34000 | 19 | 11 | 9 | 34800 | 26400 | 75.86% | 1.92 | 30400 | R-454B
215933880 | 2.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0801714B* | 34000 | 19 | 11 | 9 | 34800 | 26400 | 75.86% | 1.94 | 30400 | R-454B
215933530 | 2.8 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU1002120A* | 33600 | 19.5 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215934970 | 2.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X48M21A*+WALLCON | *96CTN0601714B* | 34600 | 20.5 | 11.5 | 8.5 | 38000 | 27600 | 72.63% | 2.05 | 31200 | R-454B
215935050 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *80CTL1102120B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.02 | 32600 | R-454B
216972983 | 4.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | PL60H210P29*+TXV | 58TN*B110C21**20 | 56000 | 18 | 11.5 | 8.1 | 59000 | 45500 | 77.12% | 2 | 46000 | R-454B
216733750 | 1.85 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M14A* | *96MSN0601412A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.9 | 17700 | R-454B
206771389 | 2.65 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *80CTL0701716A* | 31800 | 17 | 11 | 8.1 | 33200 | 24600 | 74.1% | 1.88 | 31400 | R-410A
206772316 | 2.7 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EN(A,D,W)4X48L21**+WALLCON | *96CTN1002122A* | 32400 | 17.5 | 11.7 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31400 | R-410A
215936450 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL0902120B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32600 | R-454B
215682808 | 4.67 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0401712B* | 56000 | 18 | 9.5 | 8.5 | 60500 | 43500 | 71.9% | 2.12 | 54000 | R-454B
215682858 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVM5X60M21A*+WALLCON | *97CTN1002122A* | 56500 | 18.5 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56000 | R-454B
215682908 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN1002122A* | 56500 | 18.5 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
215683008 | 4.67 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU0601716B* | 56000 | 18.5 | 9.5 | 8.5 | 60000 | 43000 | 71.67% | 2.12 | 54000 | R-454B
216765794 | 1.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3+P0V0B000M40SD |  | 22800 | 17.1 | 12.5 | 8.7 | 21400 | 17000 | 79.44% | 1.99 | 15100 | R-454B
206772920 | 2.72 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X48AAL+WALLCON | *96CTN1202422A* | 32600 | 17 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.98 | 31600 | R-410A
206773109 | 2.73 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X43L21A*+WALLCON | *80CSU0601716A* | 32800 | 17 | 11 | 8.5 | 33000 | 25200 | 76.36% | 1.96 | 31800 | R-410A
206773420 | 2.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X37L21A*+WALLCON | *95CSU0802120A* | 33000 | 17.5 | 11.5 | 8.5 | 32800 | 25000 | 76.22% | 2 | 31800 | R-410A
206773643 | 2.68 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X36AAL+WALLCON | *95CSU1002122A* | 32200 | 16.5 | 11 | 8.1 | 33200 | 24600 | 74.1% | 1.94 | 31400 | R-410A
214802733 | 1.87 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)30A34+TDR | R801V1004A17UHN | 22400 | 16.4 | 11.8 | 8.1 | 22800 | 16200 | 71.05% | 2.95 | 16900 | R-410A
215731566 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG86*48+TXV | TM9Y100C16MP11 | 44000 | 17 | 11 | 8.5 | 42500 | 33400 | 78.59% | 2 | 32000 | R-454B
215731583 | 4.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG74*60+TXV-BLEED | TM9Y100C20MP11 | 52500 | 18 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36600 | R-454B
215731597 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG51*60+TXV-BLEED | TM9Y120D20MP11 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36800 | R-454B
215487364 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3022*3A* | D*80VC0803B*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215487377 | 1.93 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA2410A* | CA*EA3626*3A* | D*80VC0805C*A* | 23200 | 19 | 11 | 8.6 | 23200 | 17000 | 73.28% | 2 | 15800 | R-32
215731598 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG51*60+TXV | TM9Y120D20MP11 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36800 | R-454B
215731632 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG86*48+TXV | Y81E080C16SMPS1 | 44500 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
215731730 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG74*60+TXV | Y81E120C16SMPS1 | 44000 | 18 | 12 | 8.5 | 41500 | 32600 | 78.55% | 2 | 31000 | R-454B
216797122 | 2.57 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2C100D5PSC+LRP | 30800 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.71 | 38000 | R-454B
214862395 | 2.68 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | H,PG83936 | 987MC42080C17*** | 32200 | 17 | 11.5 | 8.1 | 31400 | 24600 | 78.34% | 1.94 | 30800 | R-410A
215669937 | 2.83 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU0401712A* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215683058 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN0802120B* | 56500 | 18 | 9 | 9 | 63500 | 44500 | 70.08% | 2.08 | 56000 | R-454B
215936470 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *80CTL1352422B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32600 | R-454B
213607719 | 2.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | FT4BN(B,X)C36L* |  | 35400 | 16.5 | 10 | 8.5 | 38000 | 35200 | 92.63% | 1.86 | 29400 | R-410A
216765830 | 1.83 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | S9X1B080D4PSB | 22000 | 15.2 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2.02 | 15100 | R-454B
216765846 | 1.83 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | S9X2B080D4PSB | 22000 | 15.2 | 12 | 8.7 | 21200 | 17000 | 80.19% | 2.02 | 15100 | R-454B
216765860 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | S9X1B040U3PSB | 23800 | 17.1 | 12.5 | 9 | 21800 | 17400 | 79.82% | 2.08 | 15500 | R-454B
216765862 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | S9X1B060U4PSB | 23800 | 17.1 | 12.5 | 9 | 21800 | 17400 | 79.82% | 2.08 | 15400 | R-454B
216765880 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD04AS3 | S8V2B060M4PDB | 23400 | 17.1 | 12.5 | 8.1 | 22400 | 17300 | 77.23% | 1.84 | 15400 | R-454B
216765912 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3+P0V0A000M30SD |  | 23800 | 17.1 | 12.5 | 8.7 | 22200 | 17400 | 78.38% | 1.98 | 15600 | R-454B
216766028 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S9X2B060U4PSB | 32400 | 16 | 11.7 | 8.7 | 32600 | 24200 | 74.23% | 2.12 | 21400 | R-454B
216766128 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C005AS3+P0V0C000M50SD |  | 32800 | 16.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.16 | 21200 | R-454B
216766146 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 | S9X1C080U5PSB | 34200 | 17.1 | 12 | 9 | 33000 | 24400 | 73.94% | 2.21 | 21600 | R-454B
216766230 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD09AS3 | S8V2C100M5PCB | 34200 | 17.1 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.17 | 21200 | R-454B
216766262 | 2.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*DD10AS3 | S9X2D120D5PSB | 33800 | 15.2 | 12 | 9 | 32400 | 24000 | 74.07% | 2.21 | 21200 | R-454B
216766328 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9X1B080U4PSB | 33600 | 16.5 | 12 | 8.7 | 32800 | 24400 | 74.39% | 2.18 | 21600 | R-454B
216766346 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 | S8V2C100M5PCB | 32600 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.13 | 21200 | R-454B
216766348 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC005AS3 | S9V2C080U5VSB | 32400 | 16.5 | 12 | 8.7 | 32000 | 23800 | 74.38% | 2.13 | 21000 | R-454B
213613332 | 3.67 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA481EA* | DFVE60DP1400B* |  | 44000 | 17 | 10 | 8.6 | 44000 | 31000 | 70.45% | 2 | 28000 | R-410A
215936550 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *96CTN1202422B* | 35600 | 22 | 12.5 | 8.5 | 38500 | 28400 | 73.77% | 2.04 | 32800 | R-454B
213773840 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X48L24A*+WALLCON | *97CMN1002122B* | 24200 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
216972969 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | A60VHA*+TXV | 58TN*B070C21**20 | 55500 | 18 | 11 | 8.1 | 58500 | 46000 | 78.63% | 1.95 | 46500 | R-454B
216972998 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | C60A***L18*+TXV | 59CU5B080C21**20 | 55500 | 18 | 11 | 8.1 | 58500 | 45500 | 77.78% | 1.95 | 46000 | R-454B
216973012 | 4.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | PL60H210P17*+TXV | 59MN7C060C21**20 | 54500 | 18 | 10 | 8.5 | 59000 | 47000 | 79.66% | 2 | 48000 | R-454B
212500136 | 1.98 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | LH29/36F9 | SL297UH040NV36B* | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216770086 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*C005AS3 | *UHMC100CCV4 | 23000 | 17.1 | 12.7 | 8.7 | 21400 | 16900 | 78.97% | 1.99 | 15000 | R-454B
215731732 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG52*48+TXV | Y81E120C16SMPS1 | 44000 | 18 | 12 | 8.5 | 42000 | 32600 | 77.62% | 2 | 31200 | R-454B
215726318 | 2.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG36*36+TXV-BLEED | TM8V080C16MP12 | 33600 | 18 | 11 | 8.5 | 30000 | 25200 | 84% | 2 | 26800 | R-454B
215731833 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG48*36+TXV-BLEED | Y81E120C16SMPS1 | 33400 | 19 | 11.7 | 8.5 | 29600 | 24800 | 83.78% | 2 | 24800 | R-454B
215423203 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV-BLEED | TM8E080B12MP11 | 33200 | 17 | 11 | 8.5 | 29800 | 25000 | 83.89% | 2 | 26600 | R-454B
215423204 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV | TM8E080B12MP11 | 33200 | 17 | 11 | 8.5 | 29800 | 25000 | 83.89% | 2 | 26600 | R-454B
215423219 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV | TM8E100B12MP11 | 33200 | 17 | 11 | 8.5 | 29600 | 25000 | 84.46% | 2 | 26400 | R-454B
215423236 | 2.78 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE34*36+TXV | TM8E120C20MP11 | 33400 | 16 | 10.5 | 8.35 | 30400 | 25200 | 82.89% | 1.98 | 25400 | R-454B
215487444 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*80VC0805D*A* | 45500 | 17 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
209880047 | 3.71 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF97MV510021DHS*A | 44500 | 19 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
215487429 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA4830*3A* | D*96VC1005DNA* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
216682099 | 2.52 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *97VTN1002120A* | 30200 | 15.2 | 9 | 9 | 34000 | 27200 | 80% | 1.75 | 23400 | R-410A
216682810 | 2.5 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *97VTN1002122A* | 30000 | 15.2 | 9 | 8.5 | 34000 | 27200 | 80% | 1.75 | 23400 | R-410A
215423252 | 2.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE35*36+TXV | TM8V100C16MP12 | 33600 | 18 | 11 | 8.5 | 30000 | 25200 | 84% | 2 | 26800 | R-454B
215487463 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*96VC0804CNA* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215423271 | 2.78 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE34*36+TXV | TM8Y100C20MP11 | 33400 | 18 | 10.5 | 8.35 | 30600 | 25400 | 83.01% | 1.98 | 25400 | R-454B
215423320 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE80*36+TXV | TM9V080B12MP12 | 33000 | 18 | 11 | 8.5 | 29200 | 24800 | 84.93% | 2 | 26000 | R-454B
215423352 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE35*36+TXV | TM9Y100C16MP11 | 33200 | 18 | 11 | 8.5 | 29400 | 24800 | 84.35% | 2 | 26400 | R-454B
215423353 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV-BLEED | TM9Y100C16MP11 | 32400 | 18 | 10.5 | 8.5 | 29400 | 23800 | 80.95% | 2 | 25000 | R-454B
215423386 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE34*36+TXV | Y81E100C20SMPS1 | 33200 | 18 | 10.5 | 8.35 | 30000 | 25000 | 83.33% | 1.98 | 25000 | R-454B
215731784 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG54*60+TXV | Y81E130D20SMPS1 | 54000 | 19 | 11.7 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36400 | R-454B
216766412 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC009AS3 | S9X1C080U5PSB | 34400 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.22 | 21400 | R-454B
216765914 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3 | S9X1B040D3PSB | 23600 | 17.1 | 12.5 | 8.5 | 22200 | 17300 | 77.93% | 1.96 | 15400 | R-454B
213772850 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X30L17A*+WALLCON | *80CTL0701412B* | 23600 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.9 | 20800 | R-410A
206771605 | 2.63 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L24A*+WALLCON | *97CMN0602120A* | 31600 | 17 | 11 | 8.1 | 33400 | 24600 | 73.65% | 1.88 | 31600 | R-410A
213815132 | 2.83 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ9VCA3610A* | CA*F3743*6D*+MBVK12BP1X00A*+TXV |  | 34000 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
209880044 | 3.71 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF98MV508521UPS*A | 44500 | 19 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
213773498 | 1.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L24A*+WALLCON | *80CTL0902120B* | 23800 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
216766780 | 1.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S9V2B040D3VSB | 21800 | 15.5 | 11.5 | 8.5 | 21200 | 16900 | 79.72% | 1.94 | 15000 | R-454B
216766782 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S9X1B040U3PSB | 23200 | 16.5 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2.01 | 15400 | R-454B
215423470 | 4.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48*60+TXV | TL9E100C20UH11 | 52000 | 18 | 11 | 8.5 | 51500 | 38000 | 73.79% | 2 | 35800 | R-454B
215423471 | 4.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE54*60+TXV | TL9E100C20UH11 | 52000 | 19 | 11 | 8.5 | 51500 | 38000 | 73.79% | 2 | 35800 | R-454B
215423486 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48*60+TXV | TM8E080C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
215423488 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE54*60+TXV | TM8E080C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
215423489 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE55*60+TXV | TM8E080C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
215670062 | 2.83 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN0802120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215423503 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE49*60+TXV | TM8E080C20MP11 | 53500 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
216981010 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | V,Y36H175P38*+TXV-BLEED | TM8V080B12MP12 | 33000 | 17 | 11 | 8.5 | 29400 | 24800 | 84.35% | 2 | 26200 | R-454B
215670209 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0902120B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215487425 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA4830*3A* | D*80VC0805D*A* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
204298977 | 2.63 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L21A*+WALLCON | *97CMN0801714A* | 31600 | 17 | 11 | 8.1 | 33400 | 24800 | 74.25% | 1.86 | 31600 | R-410A
215423520 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE49*60+TXV | TM8E100C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
215423538 | 3.67 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36*48+TXV | TM8E120C16MP11 | 44000 | 17 | 10.5 | 8.4 | 43500 | 33800 | 77.7% | 1.98 | 33000 | R-454B
215423553 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE86*60+TXV | TM8E120C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33000 | R-454B
215423589 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE54*48+TXV | TM8V080C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215423603 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE3K*60+TXV | TM8V100C16MP12 | 43500 | 17 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215423402 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE35*36+TXV | Y82E080B12LMPS1 | 32800 | 19 | 11.7 | 8.5 | 28400 | 24400 | 85.92% | 2 | 25400 | R-454B
215667783 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0801714B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19900 | R-454B
215678228 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CSU0401712B* | 24000 | 17 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215678378 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *97CTN0801716A* | 23800 | 17 | 10 | 9 | 23400 | 16500 | 70.51% | 2 | 19900 | R-454B
215423404 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV | Y82E080B12LMPS1 | 32800 | 18 | 11.7 | 8.5 | 28400 | 24400 | 85.92% | 2 | 25400 | R-454B
214271882 | 1.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | V,C36H175P149 | 58TN*B045C17**12 | 23600 | 16 | 10.5 | 8.1 | 20000 | 16300 | 81.5% | 1.94 | 19800 | R-410A
215424440 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE7J*30+TXV | TL9E060B12UH11 | 22400 | 17 | 11 | 8.8 | 21400 | 17700 | 82.71% | 1.96 | 17600 | R-454B
216735518 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80VSL0701716B* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18300 | 88.83% | 1.96 | 17400 | R-454B
216735869 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96VSN0601716B* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216972362 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L16*+TXV | 59TN7A080C21**20 | 48000 | 19 | 10.5 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
215941163 | 3.67 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0601716B* | 44000 | 20 | 11 | 9 | 48500 | 36600 | 75.46% | 1.8 | 39500 | R-454B
215487445 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CA*EA6030*3A* | D*96VC1005DNA* | 45500 | 16.5 | 10 | 8.8 | 47000 | 33600 | 71.49% | 2 | 29000 | R-32
213075988 | 3.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D,W)4X48L21** | *95MSU1002120A* | 36200 | 16.5 | 10.5 | 8.1 | 38500 | 35000 | 90.91% | 2.02 | 29200 | R-410A
213076338 | 3.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D)4X48L24** | *95MSU1002122A* | 36200 | 16.5 | 10.5 | 8.1 | 38500 | 35000 | 90.91% | 2.02 | 29200 | R-410A
213773548 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L24A*+WALLCON | *96CTN1002122B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
216736133 | 1.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80CSU0601716A* | 22800 | 16 | 10.5 | 8.5 | 21600 | 19300 | 89.35% | 1.94 | 18200 | R-454B
216736334 | 1.87 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80MSU0401712A* | 22400 | 15.5 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.85 | 17800 | R-454B
215424488 | 1.9 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE8J*36+TXV | TM8V080B12MP12 | 22800 | 17 | 10.5 | 8.9 | 21400 | 17700 | 82.71% | 1.98 | 17600 | R-454B
215424505 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE7J*30+TXV | TM9E026A08MP12 | 22400 | 16 | 10.5 | 8.8 | 21400 | 17200 | 80.37% | 1.96 | 16900 | R-454B
213076656 | 2.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *80VTL0902120B* | 35200 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.88 | 29400 | R-410A
213076841 | 3.03 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D,W)4X48L21** | *80VTL1102122B* | 36400 | 16.5 | 10.5 | 8.1 | 38500 | 35000 | 90.91% | 2.02 | 29200 | R-410A
215423438 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE9J*36+TXV-BLEED | YP9C100C16MP13 | 33400 | 17 | 11 | 8.5 | 29400 | 24800 | 84.35% | 2 | 26200 | R-454B
215726368 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG81*36+TXV | TM9Y080C16MP11 | 32800 | 19 | 11 | 8.5 | 29400 | 23800 | 80.95% | 2 | 25000 | R-454B
215735541 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE31*30+TXV-BLEED | TM9Y060B12MP11 | 21800 | 17 | 11 | 8.5 | 21200 | 17300 | 81.6% | 1.9 | 17000 | R-454B
208587413 | 3.75 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA1 | FHRAVM6021SJZECA |  | 45000 | 19 | 12 | 8.5 | 40000 | 42000 | 105% | 1.8 | 41500 | R-410A
215939694 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CAA**4221AM*+UI | 59TN7A080C21**20 | 32600 | 19.5 | 11.7 | 9.5 | 34800 | 26800 | 77.01% | 2.02 | 30600 | R-454B
215939894 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CAA**6124AM*+UI | 59TN6C080C21**20 | 34400 | 20.5 | 12 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
215940244 | 2.85 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CSAH*6012AM*+UI | 59TN7A120C24**22 | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
215940314 | 2.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA4421XMA*+UI | 59TN7A100C21**22 | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215940364 | 2.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA4921XMA*+UI | 59TN7A080C17**16 | 35400 | 21 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33400 | R-454B
215940414 | 2.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA6021XMA*+UI | 58CU*B060C17**16 | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215726399 | 2.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG36*36+TXV-BLEED | Y81E080C20SMPS1 | 34600 | 19 | 11 | 8.5 | 30800 | 25400 | 82.47% | 2 | 27400 | R-454B
215726401 | 2.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG37*36+TXV-BLEED | Y81E080C20SMPS1 | 34600 | 19 | 11 | 8.5 | 30800 | 25400 | 82.47% | 2 | 27400 | R-454B
215423638 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE84*60+TXV | TM8V120C20MP12 | 53000 | 19 | 11 | 8.5 | 52000 | 38500 | 74.04% | 2 | 36200 | R-454B
215423689 | 4.33 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36*60+TXV-BLEED | TM8Y120C20MP11 | 52000 | 18 | 10.5 | 8.3 | 53000 | 39500 | 74.53% | 1.96 | 37000 | R-454B
215726436 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG80*36+TXV | Y81E120C16SMPS1 | 33400 | 19 | 11.7 | 8.5 | 29400 | 24800 | 84.35% | 2 | 24800 | R-454B
215726451 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG80*36+TXV-BLEED | Y82E080B12LMPS1 | 32800 | 19 | 11.7 | 8.5 | 28400 | 24400 | 85.92% | 2 | 25400 | R-454B
215423736 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE37*60+TXV | TM9E100C16MP12 | 44500 | 17 | 11 | 8.5 | 44000 | 34000 | 77.27% | 2 | 33400 | R-454B
215423739 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE3K*60+TXV | TM9E100C16MP12 | 44500 | 18 | 11 | 8.5 | 44000 | 34000 | 77.27% | 2 | 33400 | R-454B
215424524 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE7J*36+TXV | TM9E060A10MP12 | 22400 | 16 | 10.5 | 8.8 | 21400 | 17700 | 82.71% | 1.96 | 17700 | R-454B
215424540 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE7J*36+TXV-BLEED | TM9E080B12MP12 | 23000 | 17 | 11.7 | 9 | 21400 | 18300 | 85.51% | 2 | 18000 | R-454B
213077040 | 2.9 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L21A* | *96VSN0802120B* | 34800 | 16 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.82 | 29400 | R-410A
213077240 | 2.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L24A* | *96VSN1202422B* | 35400 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.9 | 29400 | R-410A
215726452 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG80*36+TXV | Y82E080B12LMPS1 | 32800 | 19 | 11.7 | 8.5 | 28400 | 24400 | 85.92% | 2 | 25400 | R-454B
215731298 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG48*36+TXV | TM9Y080C16MP11 | 32800 | 19 | 11 | 8.5 | 29400 | 23800 | 80.95% | 2 | 25000 | R-454B
215487396 | 2.9 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA4830*3A* | D*96VC1005DNA* | 34800 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216796784 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X2C100U5PSB | 31800 | 15.2 | 11.7 | 8.1 | 31400 | 22400 | 71.34% | 3.01 | 21800 | R-454B
215487395 | 2.9 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA4830*3A* | D*96VC1205DNA* | 34800 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
215487397 | 2.9 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA4830*3A* | D*96VC1005CNA* | 34800 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
213077442 | 2.98 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *96VTN0801716B* | 35800 | 15.5 | 10 | 8.1 | 39000 | 35200 | 90.26% | 1.96 | 29400 | R-410A
213077726 | 2.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *96VTN1002122B* | 35400 | 16.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.88 | 29400 | R-410A
215670249 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU0802120B* | 34200 | 16.5 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215670569 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0601714B* | 34200 | 16.5 | 9.5 | 8.5 | 34800 | 25200 | 72.41% | 1.78 | 30200 | R-454B
216981002 | 1.9 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | V,Y36H***P21*+TXV-BLEED | Y92E040A10SMPS1 | 22800 | 16 | 11.7 | 8.9 | 21400 | 16800 | 78.5% | 1.98 | 16200 | R-454B
209880040 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF98MV306017UPS*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43500 | 127.2% | 2.2 | 41000 | R-410A
216972412 | 2.78 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P15*+TXV | 58CU*B040C17**12 | 33400 | 20 | 11.7 | 9.5 | 32800 | 25800 | 78.66% | 2.04 | 29200 | R-454B
216972469 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | C36A***L15*+TXV | 58TN*B045C17**12 | 32800 | 19 | 10.5 | 9 | 33800 | 26800 | 79.29% | 1.9 | 30000 | R-454B
216972471 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P13*+TXV | 58TN*B045C17**12 | 32200 | 19 | 10.5 | 9 | 34200 | 27200 | 79.53% | 1.88 | 30400 | R-454B
216972476 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P45*+TXV | 58TN*B045C17**12 | 33800 | 19 | 11 | 9 | 33600 | 26400 | 78.57% | 1.92 | 29800 | R-454B
216972494 | 2.83 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P29*+TXV | 58TN*B070C17**16 | 34000 | 19 | 11.5 | 9 | 33000 | 26000 | 78.79% | 1.94 | 29200 | R-454B
213077810 | 2.98 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D)4X48L24** | *96VTN1202422B* | 35800 | 16.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 2 | 29200 | R-410A
213078261 | 2.92 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L17A* | *80MS(N,L)0901714A* | 35000 | 16 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.82 | 29400 | R-410A
215424556 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*36+TXV | TM9V060B12MP12 | 22200 | 17 | 11 | 8.65 | 21200 | 17200 | 81.13% | 1.94 | 16900 | R-454B
215424574 | 1.85 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*36+TXV | TM9Y040A10MP11 | 22200 | 16 | 10.5 | 8.2 | 20800 | 16900 | 81.25% | 1.94 | 16500 | R-454B
215487414 | 2.92 | Yes | No | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CHPEA4830*3A* | D*80VC0804C*A* | 35000 | 18.5 | 10.5 | 8.1 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216453762 | 3.5 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48C44+TDR | U98MV1005A21UPS | 42000 | 17 | 11 | 8.5 | 45500 | 35600 | 78.24% | 2.79 | 33400 | R-410A
216980996 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | V,Y36H175P13*+TXV-BLEED | TM8V080B12MP12 | 22600 | 17 | 11.7 | 8.85 | 21400 | 18100 | 84.58% | 1.98 | 17200 | R-454B
209880036 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF98MV307017UPS*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43500 | 127.2% | 2.2 | 41000 | R-410A
216981016 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P19*+TXV-BLEED | TM8V080C16MP12 | 44000 | 18 | 11.7 | 9 | 42500 | 33200 | 78.12% | 2 | 31800 | R-454B
216776169 | 3.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | FE*TT4*60+TXV-BLEED |  | 46000 | 19 | 12 | 9 | 44000 | 33600 | 76.36% | 2.1 | 34600 | R-454B
213078426 | 2.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L24A* | *80MS(N,L)0902116A* | 35200 | 16.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.88 | 29400 | R-410A
213078793 | 2.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L24A* | *80MS(N,L)1552420A* | 35600 | 16.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.9 | 29400 | R-410A
213079111 | 2.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *80MSU0601716A* | 35200 | 16.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.86 | 29200 | R-410A
213079831 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D)4X48L24** | *92MSN1002120A* | 36000 | 16.5 | 10.5 | 8.1 | 38500 | 34800 | 90.39% | 2 | 29200 | R-410A
215424608 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE8J*30+TXV | Y81E060A12SMPS1 | 22600 | 17 | 11.7 | 8.9 | 21000 | 16900 | 80.48% | 1.98 | 16600 | R-454B
215424609 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE8J*36+TXV | Y81E060A12SMPS1 | 22600 | 17 | 11.7 | 8.9 | 21000 | 16900 | 80.48% | 1.98 | 16600 | R-454B
215423740 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48*60+TXV-BLEED | TM9E100C16MP12 | 44500 | 18 | 11 | 8.5 | 44000 | 34000 | 77.27% | 2 | 33400 | R-454B
213076930 | 2.93 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L17A* | *96VSN0801716B* | 35200 | 15.2 | 9.5 | 8.1 | 39000 | 35400 | 90.77% | 1.82 | 29600 | R-410A
213076950 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X37L17A* | *96VSN0801716B* | 36000 | 15.5 | 10 | 8.5 | 38500 | 35200 | 91.43% | 2 | 29400 | R-410A
213077030 | 2.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D,W)4X48L21** | *96VSN0801716B* | 35600 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.98 | 29200 | R-410A
213077250 | 3 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L24A* | *96VSN1202422B* | 36000 | 16.5 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.04 | 29000 | R-410A
215423755 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48*60+TXV-BLEED | TM9E100C20MP12 | 53500 | 18 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
213079914 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D)4X48L24** | *92MSN1002122A* | 36000 | 16.5 | 10.5 | 8.1 | 38500 | 35000 | 90.91% | 2 | 29200 | R-410A
213080033 | 3.03 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X37L21A* | *96MSN0801716A* | 36400 | 15.5 | 10 | 8.5 | 38000 | 35000 | 92.11% | 2.06 | 29200 | R-410A
215424625 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE8J*36+TXV | Y81E100B12SMPS1 | 23000 | 18 | 12 | 9 | 21400 | 18200 | 85.05% | 2 | 17900 | R-454B
214776315 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH240A*C+TXV | TM9E026A08MP12 | 22400 | 16 | 10.5 | 8.7 | 21200 | 17200 | 81.13% | 1.94 | 16900 | R-454B
214776331 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CX360A*35+TXV | TM9E060A10MP12 | 22200 | 16 | 10.5 | 8.65 | 21200 | 17700 | 83.49% | 1.94 | 17600 | R-454B
213077468 | 2.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D,W)4X48L21** | *96VTN0801716B* | 35600 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.98 | 29200 | R-410A
213077535 | 3.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *96VTN0802120B* | 36200 | 16 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.04 | 29000 | R-410A
213078051 | 2.9 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L21A* | *80MS(N,L)0701716A* | 34800 | 16 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.82 | 29400 | R-410A
213078135 | 2.98 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *80MS(N,L)0701716A* | 35800 | 15.5 | 10 | 8.1 | 38500 | 35200 | 91.43% | 1.96 | 29400 | R-410A
213078201 | 2.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L24A* | *80MS(N,L)0702116A* | 35200 | 16.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.88 | 29400 | R-410A
213078835 | 2.92 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L21A* | *80MSU1002120A* | 35000 | 16 | 9.5 | 8.5 | 38500 | 35200 | 91.43% | 1.8 | 29400 | R-410A
213079403 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X37L17A* | *92MSN0601714A* | 36000 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2 | 29400 | R-410A
206133788 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *95CSU1002122A* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
209880037 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF98MV508521UPS*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
215669839 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU0802120B* | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
216776402 | 2.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | AD-33(P,U)******+TXV-BLEED | Y91E080B12SMPS1 | 33600 | 18 | 11 | 8.5 | 29800 | 25200 | 84.56% | 2 | 26800 | R-454B
216770102 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8X2C100M5PSC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
216776168 | 2 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | FE*G33*30+TXV-BLEED |  | 24000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
210868912 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF75214LT80Y | 34200 | 19 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
214776346 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CV363**C+TXV | TM9V040A10MP12 | 22400 | 16 | 10.5 | 8.8 | 21400 | 17100 | 79.91% | 1.96 | 16800 | R-454B
215423771 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE49*60+TXV | TM9E120D20MP12 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36800 | R-454B
215423772 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE84*60+TXV | TM9E120D20MP12 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36800 | R-454B
215423786 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE54*60+TXV | TM9V080C16MP12 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
215423789 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE74*48+TXV | TM9V080C16MP12 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
215423790 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE84*60+TXV | TM9V080C16MP12 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
215423805 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE55*60+TXV | TM9V100C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215423820 | 4.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE49*60+TXV | TM9V100C20MP12 | 52000 | 19 | 11 | 8.5 | 51500 | 38000 | 73.79% | 2 | 36000 | R-454B
213079573 | 3.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *92MSN0801716A* | 36200 | 16.5 | 10 | 8.5 | 38000 | 34800 | 91.58% | 2.04 | 29000 | R-410A
213080057 | 3.03 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *96MSN0801716A* | 36400 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2.06 | 29200 | R-410A
213080141 | 2.93 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L21A* | *96MSN0802120A* | 35200 | 16 | 9.5 | 8.1 | 39000 | 35200 | 90.26% | 1.84 | 29600 | R-410A
213080273 | 2.93 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L21A* | *96MSN1002120A* | 35200 | 16 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.8 | 29400 | R-410A
213080309 | 2.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L24A* | *96MSN1002120A* | 35400 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.88 | 29400 | R-410A
215735545 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE31*30+TXV-BLEED | Y82E060A12LMPS1 | 21800 | 18 | 11 | 8.5 | 21200 | 17300 | 81.6% | 1.9 | 17100 | R-454B
216797132 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | *UHMD120CCV5+LRP | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.81 | 51500 | R-454B
215940983 | 3.63 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN0802120A* | 43500 | 20.5 | 10.5 | 9.5 | 48000 | 36600 | 76.25% | 1.92 | 39500 | R-454B
215667437 | 1.92 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CTL0701716B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.96 | 20200 | R-454B
215667935 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN1002122B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215668671 | 2.87 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0702120B* | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
213772950 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0701412B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.92 | 20800 | R-410A
213080674 | 3 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X37L17A* | *95MSU0601716A* | 36000 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2 | 29400 | R-410A
215936600 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0701716B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 33000 | R-454B
215935950 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *80CSU0401712A* | 34400 | 21 | 11.7 | 8.5 | 38500 | 28400 | 73.77% | 2.04 | 32400 | R-454B
215423857 | 3.63 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36*60+TXV | TM9Y100C16MP11 | 43500 | 16 | 10.5 | 8.4 | 42500 | 33400 | 78.59% | 1.98 | 32000 | R-454B
215423907 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48*60+TXV | Y81E080C16SMPS1 | 44500 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
215423920 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE48*60+TXV-BLEED | Y81E080C20SMPS1 | 44000 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 31600 | R-454B
215423940 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE54*60+TXV | Y81E100C16SMPS1 | 44000 | 18 | 12 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31400 | R-454B
215423973 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE49*60+TXV | Y81E120C16SMPS1 | 44000 | 18 | 12 | 8.5 | 41500 | 32600 | 78.55% | 2 | 31000 | R-454B
215423988 | 4.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE86*60+TXV | Y81E120C20SMPS1 | 52500 | 19 | 11.7 | 8.5 | 51500 | 38000 | 73.79% | 2 | 35600 | R-454B
215424005 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36*60+TXV | Y91E080C16SMPS1 | 44500 | 17 | 11.5 | 8.4 | 45000 | 33400 | 74.22% | 1.98 | 32200 | R-454B
213080165 | 2.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *96MSN0802120A* | 35600 | 16 | 10 | 8.1 | 38500 | 35200 | 91.43% | 1.9 | 29400 | R-410A
213080398 | 2.93 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *96MSN1002122A* | 35200 | 16 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.88 | 29400 | R-410A
215424024 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE37*60+TXV | Y91E080C20SMPS1 | 44500 | 17 | 12 | 8.5 | 44500 | 33000 | 74.16% | 2 | 31600 | R-454B
215424039 | 3.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE36*60+TXV-BLEED | Y91E100C16SMPS1 | 45000 | 17 | 11.5 | 8.4 | 45000 | 33800 | 75.11% | 1.98 | 33200 | R-454B
215424055 | 3.79 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE86*60+TXV | Y91E100C16SMPS1 | 45500 | 18 | 11.7 | 8.5 | 45000 | 33800 | 75.11% | 2 | 33200 | R-454B
215424071 | 3.79 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE74*48+TXV | Y91E100C20SMPS1 | 45500 | 18 | 11.7 | 8.5 | 45000 | 33600 | 74.67% | 2 | 32800 | R-454B
215424089 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE86*60+TXV | Y91E120D20SMPS1 | 53500 | 18 | 11.7 | 8.5 | 51500 | 38500 | 74.76% | 2 | 36000 | R-454B
215424107 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE86*60+TXV | YP9C080C16MP13 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
215424121 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE55*60+TXV | YP9C100C16MP13 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
213258369 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE30924 | *96VTN0601714A* | 23000 | 16 | 9.5 | 8.5 | 25200 | 24000 | 95.24% | 2.02 | 18400 | R-410A
209880046 | 3.67 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF96TV507021M4S*A | 44000 | 18 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
216453759 | 3.5 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48C44+TDR | R962V0855A21M4 | 42000 | 17 | 11 | 8.5 | 45500 | 35200 | 77.36% | 2.77 | 33200 | R-410A
213366567 | 3.96 | Yes | Yes | TOSOT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TU60-24WADU | HE49960+AEFE5* |  | 47500 | 16 | 11 | 9 | 46000 | 38500 | 83.7% | 1.8 | 30400 | R-410A
215424123 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE74*48+TXV | YP9C100C16MP13 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215424124 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE84*60+TXV | YP9C100C16MP13 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215726466 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG50*60+TXV-BLEED | TM8V080C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215726467 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG50*48+TXV | TM8V080C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215726469 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG52*60+TXV-BLEED | TM8V080C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215726483 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG48*60+TXV | TM8V100C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215726499 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV-BLEED | TM8V100C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215726519 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG48*60+TXV | TM8V120C20MP12 | 44000 | 18 | 11.7 | 8.5 | 42500 | 33200 | 78.12% | 2 | 32000 | R-454B
213258952 | 2.02 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VTN0801716A* | 24200 | 16 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
216981005 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YG8J*36+TXV-BLEED | Y92E060B12SMPS1 | 23000 | 18 | 11.7 | 9.5 | 21400 | 18100 | 84.58% | 2 | 16900 | R-454B
216056056 | 3.5 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES100C20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
215726533 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG48*48+TXV | TM9V120D20MP12 | 44000 | 18 | 11.7 | 8.5 | 42500 | 33000 | 77.65% | 2 | 31800 | R-454B
215726553 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG49*60+TXV | TM9Y080C16MP11 | 44000 | 17 | 11 | 8.5 | 42500 | 33400 | 78.59% | 2 | 32000 | R-454B
215726585 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG86*60+TXV-BLEED | TM9Y100C16MP11 | 44000 | 17 | 11 | 8.5 | 42500 | 33400 | 78.59% | 2 | 32000 | R-454B
215726600 | 4.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV | TM9Y100C20MP11 | 52500 | 18 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36600 | R-454B
215726616 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG37*48+TXV | Y81E080C16SMPS1 | 44500 | 17 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
215726619 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG48*48+TXV | Y81E080C16SMPS1 | 44500 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
215726700 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG49*60+TXV | Y81E120C16SMPS1 | 44000 | 18 | 12 | 8.5 | 42000 | 32600 | 77.62% | 2 | 31200 | R-454B
216618741 | 3.75 | No | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WFPU18Z483C | V,G60H210D169+AEFE5* |  | 45000 | 16 | 9.5 | 8.1 | 44500 | 32600 | 73.26% | 1.82 | 30000 | R-410A
216797140 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S8V2B060M4PDB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
216972496 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | A36VCA*+TXV | 58TN*B070C17**16 | 32600 | 19 | 11 | 9.5 | 33600 | 26600 | 79.17% | 2 | 30000 | R-454B
216972646 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P74*+TXV | 59MN7C080C17**14 | 32400 | 19 | 11 | 9.5 | 33800 | 26800 | 79.29% | 2 | 30000 | R-454B
216972671 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H210P29*+TXV | 59TN6C080C17**14 | 33200 | 20 | 11 | 9.5 | 33200 | 26200 | 78.92% | 2.02 | 29600 | R-454B
216972694 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | PL36H175P14*+TXV | 59TN7A060C17**16 | 32400 | 19 | 10.5 | 9 | 33800 | 26600 | 78.7% | 1.9 | 30000 | R-454B
216972714 | 2.8 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | V,C36H175P45*+TXV | 59TN7A080C17**16 | 33600 | 20 | 11 | 9 | 33200 | 26200 | 78.92% | 1.92 | 29400 | R-454B
216766798 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3+P0V0A000M30SD |  | 23200 | 17 | 12 | 8.7 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
216766832 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S9X2B060D3PSB | 23800 | 17.5 | 12.7 | 8.5 | 22200 | 17400 | 78.38% | 1.97 | 15500 | R-454B
216766841 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*BD06AS3 | S8V2B080M4PCB | 23800 | 17.1 | 12.7 | 8.5 | 22200 | 17400 | 78.38% | 1.96 | 15500 | R-454B
216766855 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8V2A040M3PDB | 23200 | 16.5 | 12 | 8.7 | 21800 | 17300 | 79.36% | 2.01 | 15500 | R-454B
216766864 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8V2B060M4PCB | 23200 | 17 | 12 | 8.7 | 21800 | 17300 | 79.36% | 2.01 | 15400 | R-454B
213773100 | 1.95 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X36L21A*+WALLCON | *97CMN0601714B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213773470 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X42L21A*+WALLCON | *96CTN0601714B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.94 | 20800 | R-410A
213773670 | 2.03 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X43L21A*+WALLCON | *96CTN0801714B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
215668855 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CTL1102120B* | 33200 | 18 | 10 | 9 | 35800 | 25600 | 71.51% | 1.84 | 30800 | R-454B
215668871 | 2.77 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *95CSU0802120B* | 33200 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
209880039 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF96TV304017M4S*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43500 | 127.2% | 2.2 | 41000 | R-410A
208587411 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA1 | FHRAVM2421HJZECA |  | 22800 | 20 | 12.5 | 8.5 | 22800 | 24800 | 108.8% | 2 | 24200 | R-410A
215940514 | 2.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAVA3621XMA*+UI | 58CU*B040C17**12 | 34600 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
215940564 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAVA3621XMA*+UI | 59TN7A100C21**22 | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
213607720 | 2.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | FG4ANXC36L* |  | 35400 | 16.5 | 10 | 8.5 | 38000 | 35200 | 92.63% | 1.86 | 29400 | R-410A
216990372 | 4.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | C60A***L19*+TXV | 88*TB60090C21*** | 56000 | 19 | 9 | 9 | 57500 | 41000 | 71.3% | 2.02 | 50000 | R-454B
215726719 | 4.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG50*60+TXV | Y81E120C20SMPS1 | 52500 | 19 | 11.7 | 8.5 | 51500 | 38000 | 73.79% | 2 | 35600 | R-454B
215726734 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG50*60+TXV | Y81E130D20SMPS1 | 54000 | 19 | 11.7 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36400 | R-454B
215731330 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG3K*60+TXV | TM8V080C16MP12 | 43500 | 17 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
215425325 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE72*60+TXV | TL9E080C16UH11 | 44500 | 18 | 11 | 8.5 | 44000 | 34000 | 77.27% | 2 | 33400 | R-454B
215425359 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE84*48+TXV | TM8E100C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
215425376 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE72*60+TXV | TM8E130D20MP11 | 54000 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
215425392 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE3K*48+TXV | TM8V100C16MP12 | 43500 | 17 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
216766866 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S8V2A040M3PDB | 23800 | 17.1 | 12.7 | 9 | 22000 | 17500 | 79.55% | 2.06 | 15500 | R-454B
216981020 | 3.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P19*+TXV-BLEED | Y82E100C16LMPS1 | 45000 | 17 | 11 | 9 | 43500 | 32200 | 74.02% | 2 | 33000 | R-454B
216776399 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | AD-61(P,U)******+TXV-BLEED | Y92E120D20SMPS1 | 54000 | 18 | 11 | 9 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
215425426 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE49*48+TXV | TM8Y100C16MP11 | 44000 | 18 | 11.7 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
215425427 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE74*60+TXV | TM8Y100C16MP11 | 44000 | 18 | 11.7 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
215425442 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE53*48+TXV | TM9E080C16MP12 | 44500 | 18 | 11 | 8.5 | 43500 | 34000 | 78.16% | 2 | 33200 | R-454B
214776412 | 3.67 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH600C*C+TXV | TL8E080C16UH11 | 44000 | 17 | 10.5 | 8.45 | 43500 | 33800 | 77.7% | 1.98 | 33000 | R-454B
214776414 | 3.67 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH600D*C+TXV | TL8E080C16UH11 | 44000 | 17 | 10.5 | 8.4 | 43500 | 33800 | 77.7% | 1.98 | 33000 | R-454B
214776430 | 4.21 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV600**C+TXV | TL8E100C20UH11 | 50500 | 18 | 10.5 | 8.3 | 51500 | 38000 | 73.79% | 1.96 | 35800 | R-454B
214776431 | 4.25 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV601**C+TXV | TL8E100C20UH11 | 51000 | 18 | 10.5 | 8.35 | 51500 | 38000 | 73.79% | 1.98 | 35800 | R-454B
214776513 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV605**C+TXV | TM9E100C16MP12 | 44500 | 18 | 11 | 8.5 | 44000 | 34000 | 77.27% | 2 | 33400 | R-454B
214776530 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV607**C+TXV | TM9E100C20MP12 | 53500 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
214776533 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV609**A+TXV | TM9E100C20MP12 | 53500 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
214776563 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV602D*A+TXV | TM9V080C16MP12 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
214776565 | 3.54 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH480C*C+TXV | TM9V100C16MP12 | 42500 | 17 | 11 | 8.3 | 42000 | 32800 | 78.1% | 1.96 | 31200 | R-454B
214776579 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH602**A+TXV | TM9V100C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
214776580 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV602D*A+TXV | TM9V100C16MP12 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
214776630 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CX601C*35+TXV | TMLE080C20MP11 | 53500 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
214776633 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV606**C+TXV | TMLE080C20MP11 | 53500 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
214776647 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV601**C+TXV | TMLE100C16MP11 | 44500 | 17 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
214776648 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CX601C*35+TXV | TMLE100C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
214776649 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH605D*C+TXV | TMLE100C16MP11 | 44500 | 18 | 11 | 8.5 | 43500 | 33800 | 77.7% | 2 | 33200 | R-454B
214776716 | 4.33 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH600C*C+TXV | TMLV120C20MP12 | 52000 | 18 | 10.5 | 8.3 | 52000 | 38500 | 74.04% | 1.96 | 36200 | R-454B
214776731 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH604**C+TXV | Y81E080C16SMPS1 | 44500 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 32000 | R-454B
214776748 | 4.29 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH600D*C+TXV | Y81E080C20SMPS1 | 51500 | 18 | 10.5 | 8.3 | 52000 | 38500 | 74.04% | 1.96 | 36200 | R-454B
214776766 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH605D*C+TXV | Y81E100C20SMPS1 | 44500 | 18 | 12 | 8.5 | 42500 | 33000 | 77.65% | 2 | 31800 | R-454B
214776782 | 4.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV606**C+TXV | Y81E120C20SMPS1 | 52500 | 19 | 11.7 | 8.5 | 51500 | 38000 | 73.79% | 2 | 35600 | R-454B
214776797 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CX601C*35+TXV | YP9C080C16MP13 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
214776799 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV605**C+TXV | YP9C080C16MP13 | 43500 | 18 | 11 | 8.5 | 42000 | 33000 | 78.57% | 2 | 31600 | R-454B
214776832 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV602D*A+TXV | YP9C120D20MP13 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36600 | R-454B
214776833 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV609**A+TXV | YP9C120D20MP13 | 53000 | 19 | 11 | 8.5 | 52500 | 39000 | 74.29% | 2 | 36600 | R-454B
214776847 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV607**C+TXV | YPLC080C16MP13 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
214776850 | 3.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV609**A+TXV | YPLC080C16MP13 | 43500 | 18 | 11.7 | 8.5 | 42000 | 32800 | 78.1% | 2 | 31200 | R-454B
214776864 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV605**C+TXV | YPLC100C20MP13 | 44000 | 18 | 11.7 | 8.5 | 42500 | 33200 | 78.12% | 2 | 32000 | R-454B
212603108 | 2.07 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P159 | *80ES(N,L)0701716A* | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212603109 | 2.07 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | V,G36H175P159 | *80ES(N,L)0701716A* | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
215669705 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1002122B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215932040 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0401712A* | 32200 | 19.5 | 11 | 9.5 | 35200 | 27200 | 77.27% | 1.98 | 31000 | R-454B
215670071 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN1002122B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215670103 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0801714B* | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
216734924 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80MS(N,L)0701412A* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17500 | R-454B
215669831 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU0601716B* | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215669863 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN0602120B* | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215669895 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN1202422B* | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215669911 | 2.78 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN0601714B* | 33400 | 16 | 9 | 8.5 | 36000 | 25800 | 71.67% | 1.76 | 31000 | R-454B
215670047 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN0601714B* | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 30800 | R-454B
215670095 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0601714B* | 33600 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 30800 | R-454B
216990558 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | C36A***L15*+TXV | 88*TB36045C17*** | 32800 | 19 | 10.5 | 9 | 33800 | 26800 | 79.29% | 1.9 | 30000 | R-454B
216990591 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | C36A***L15*+TXV | 88*TB48090C17*** | 33200 | 20 | 11.5 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
211257311 | 1.54 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | FJ4DN*B24L* |  | 18500 | 15.5 | 10.5 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
208587412 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA1 | FHRAVM6021SJZECA |  | 34200 | 20 | 12.5 | 8.5 | 32000 | 40500 | 126.6% | 2.1 | 38000 | R-410A
216990525 | 4.08 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | C60A***L18*+TXV | 88*TB60070C21*** | 49000 | 19 | 11 | 10.5 | 51000 | 53500 | 104.9% | 1.92 | 50000 | R-454B
215833649 | 4.5 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | A60VHA*+TXV+AEFE5* |  | 54000 | 19 | 11.7 | 9 | 52000 | 38000 | 73.08% | 2.1 | 36200 | R-454B
209880049 | 4.38 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA | FCCA6021SZEA | FF96TV510021M4S*A | 52500 | 18 | 10 | 8.1 | 52500 | 50500 | 96.19% | 1.9 | 51500 | R-410A
212505529 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PG81936 | 88*TA36070C14*** | 24200 | 17 | 11 | 8.1 | 19600 | 17800 | 90.82% | 2.22 | 19600 | R-410A
216734975 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80VSL0701412B* | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.94 | 17600 | R-454B
216735325 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VTN0401712B* | 22800 | 16 | 10.5 | 8.5 | 20800 | 18600 | 89.42% | 1.96 | 17700 | R-454B
216735456 | 1.92 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)0451714A* | 23000 | 15.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17500 | R-454B
213752469 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC6A080M17**16 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.88 | 20200 | R-410A
213752539 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SP6A080V21**20 | 23800 | 16 | 9 | 8.1 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213752546 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SP6A080V21**20 | 23800 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
216981024 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | V,Y60H210P19*+TXV-BLEED | Y82E120C20LMPS1 | 54000 | 19 | 12 | 9 | 52000 | 38000 | 73.08% | 2 | 35800 | R-454B
215735527 | 3.54 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE35*48+TXV-BLEED | TM9V080C16MP12 | 42500 | 17 | 10.5 | 8.3 | 42000 | 33000 | 78.57% | 1.96 | 31600 | R-454B
215679258 | 2.8 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *97CTN0601716A* | 33600 | 17 | 9 | 9 | 36000 | 25800 | 71.67% | 1.88 | 31000 | R-454B
216797054 | 1.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | D(A,C,E)30A4J+TDR | S9V2B040U3VSB+LRP | 20400 | 18 | 11.2 | 8.5 | 24400 | 24400 | 100% | 3.04 | 28600 | R-454B
216644277 | 1.51 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ18AA3 | CAA**2517AM* | 59SU5B060M17**16 | 18100 | 15.2 | 11 | 9 | 19700 | 17600 | 89.34% | 1.9 | 14700 | R-454B
216776403 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | AD-33(P,U)******+TXV-BLEED | Y92E080B12SMPS1 | 33400 | 18 | 11 | 8.5 | 29800 | 23600 | 79.19% | 2 | 27000 | R-454B
215679408 | 2.77 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CTN1002122A* | 33200 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.84 | 31000 | R-454B
215679428 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CSU0401712B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215679458 | 2.85 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CTN0801716A* | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215679558 | 2.87 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN0802120B* | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215679728 | 2.82 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU0601716B* | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
215679978 | 2.87 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0801716A* | 34400 | 16 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
215669415 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1202422B* | 34400 | 18.5 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215669715 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1202422B* | 34800 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
214229140 | 2.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X25L17A* | *80MSU0601716A* | 24200 | 17.5 | 10 | 8.5 | 25200 | 21200 | 84.13% | 1.8 | 18700 | R-410A
214229173 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *80MSU0601716A* | 24000 | 17.5 | 10 | 8.5 | 25600 | 21600 | 84.38% | 1.82 | 18800 | R-410A
214229206 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *80MSU0601716A* | 23600 | 17 | 10.5 | 8.5 | 25600 | 24000 | 93.75% | 2 | 18800 | R-410A
216766921 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S9V2B040D3VSB | 32600 | 16 | 11.5 | 8.2 | 33600 | 24600 | 73.21% | 1.97 | 21800 | R-454B
216766964 | 2.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S9X1C100U5PSB | 33600 | 15.2 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216766973 | 2.83 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S9X1C100U5PSB | 34000 | 15.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.2 | 21200 | R-454B
215670199 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0901716B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
216776401 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | AD-37(P,U)******+TXV-BLEED | Y82E080B12LMPS1 | 32800 | 18 | 11.5 | 8.9 | 28800 | 24400 | 84.72% | 1.98 | 25800 | R-454B
216767005 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*D008AS3 | S8V2D120M5PDB | 34200 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.21 | 21400 | R-454B
216767032 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S8V2B060M4PCB | 32000 | 16 | 11.7 | 8.5 | 32200 | 24000 | 74.53% | 2.09 | 21200 | R-454B
216767048 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X1B060U4PSB | 33000 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
216767064 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3 | S8V2C100M5PDB | 32600 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.12 | 21200 | R-454B
216767066 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC007AS3+P0V0C000M50SD |  | 34000 | 17.1 | 12 | 9 | 32600 | 24000 | 73.62% | 2.21 | 21200 | R-454B
216770022 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8X1C080M5PTC | 43500 | 16 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.22 | 29200 | R-454B
216974769 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | V,C36H175P14*+TXV | 83*CB36040C17*** | 32800 | 20 | 11.5 | 9.5 | 33200 | 26200 | 78.92% | 2.02 | 29600 | R-454B
215677838 | 4.54 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 54500 | 18 | 8.5 | 8.5 | 59500 | 42000 | 70.59% | 1.9 | 51000 | R-454B
213080710 | 3.05 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *95MSU0601716A* | 36600 | 16 | 10 | 8.5 | 38500 | 35000 | 90.91% | 2.06 | 29200 | R-410A
213739871 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P069 | *80VSL0451412B* | 23600 | 17 | 10.5 | 8.5 | 24600 | 24200 | 98.37% | 2.04 | 18100 | R-410A
213739887 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG80936 | *80VTL0451412B* | 23600 | 17 | 10.5 | 8.5 | 24600 | 24200 | 98.37% | 2.04 | 18100 | R-410A
213739912 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | V,G36H175P159 | *95MSU0401712A* | 23400 | 17 | 10 | 8.5 | 24400 | 24000 | 98.36% | 2.02 | 18000 | R-410A
213739919 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG32936 | *96MSN0261410A* | 23400 | 16 | 10 | 8.5 | 25400 | 25800 | 101.6% | 2.2 | 18500 | R-410A
212603160 | 1.97 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG32936 | *80VTL0701716A* | 23600 | 17 | 10 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
214776349 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CV360**C+TXV | TM9V060B12MP12 | 21800 | 17 | 11 | 8.45 | 21200 | 17200 | 81.13% | 1.9 | 16900 | R-454B
209880027 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF98MV307017UPS*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
212603173 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG32936 | *92ESN0801716A* | 24000 | 17 | 10 | 8.5 | 25200 | 23400 | 92.86% | 1.96 | 18400 | R-410A
212603207 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG80936 | *96VSN0601412A* | 23600 | 16 | 10 | 8.5 | 24200 | 23000 | 95.04% | 1.94 | 17900 | R-410A
215731313 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG48*36+TXV | Y82E080B12LMPS1 | 32800 | 19 | 11.7 | 8.5 | 28400 | 24400 | 85.92% | 2 | 25400 | R-454B
216797141 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S8V2B080M4PCB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.7 | 52000 | R-454B
209880024 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF97MV306017DHS*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
215938396 | 3.79 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN1202422B* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.95 | 43000 | R-454B
216735606 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80CTL0701716B* | 23200 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216770016 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | L8V1C100U5VSB | 43500 | 16.5 | 12 | 8.7 | 43500 | 32000 | 73.56% | 2.22 | 29000 | R-454B
216770030 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8X2C080M5PTC | 43500 | 16 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.22 | 29200 | R-454B
215667151 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CSU0401712A* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
213369636 | 2.48 | Yes | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-30-O | *G8J936+TD |  | 29800 | 15.2 | 10.5 | 9.5 | 31400 | 26600 | 84.71% | 1.82 | 21600 | R-410A
215224756 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG31930 | 59MN7C080C17**14 | 22800 | 20 | 12.5 | 10 | 25200 | 19600 | 77.78% | 2.38 | 24000 | R-410A
215487485 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA3022*3A* | D*80VC0603B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
216766875 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3+P0V0B000M40SD |  | 23400 | 17.1 | 13 | 8.7 | 21600 | 17100 | 79.17% | 2.03 | 15200 | R-454B
216766880 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9X1B040U3PSB | 23800 | 17.5 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2.06 | 15500 | R-454B
214385797 | 1.92 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,YA10936 | *95MSU0401712A* | 23000 | 16 | 9.5 | 8.5 | 25400 | 25800 | 101.6% | 2.2 | 18500 | R-410A
210868916 | 3.71 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF75214LT80Y | 44500 | 19 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
215281561 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | SL9939 |  | 33000 | 18 | 10.5 | 8.7 | 31600 | 22800 | 72.15% | 2.1 | 23600 | R-410A
215487409 | 2.92 | Yes | No | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CHPEA4830*3A* | D*96VC1005CNA* | 35000 | 18.5 | 10.5 | 8.1 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216981023 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV-BLEED | Y82E100C20LMPS1 | 54000 | 19 | 12 | 9 | 51500 | 37600 | 73.01% | 2 | 35600 | R-454B
216770113 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC009AS3 | L9X1C100U5VSA | 33200 | 16 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.16 | 21200 | R-454B
215683594 | 1.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2417AM*+UI | 986TD30040C14*** | 22400 | 15.5 | 9 | 8.5 | 24400 | 17200 | 70.49% | 1.82 | 20800 | R-454B
215683614 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2517AM*+UI | 986TD42060C17*** | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2.02 | 19800 | R-454B
215683678 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3717AM*+UI | 987MC42060C17*** | 23600 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 19900 | R-454B
215683696 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 88*TB60070C21*** | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215683712 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 987MC66100C21*** | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215683714 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 986TD42060C17*** | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
213366532 | 1.82 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B241 | H,YG34936 | Z8ET080B12LMPS1 | 21800 | 17 | 9.5 | 8.1 | 22000 | 15600 | 70.91% | 1.86 | 14500 | R-410A
216766448 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S8V2C080M5PCB | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
216766512 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*D010AS3 | S9V2C080U5VSB | 43500 | 16.5 | 12.5 | 8.7 | 43500 | 32000 | 73.56% | 2.23 | 29000 | R-454B
216766548 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S9V2D120D5VSB | 43500 | 16 | 12 | 8.7 | 44500 | 32400 | 72.81% | 2.2 | 29600 | R-454B
216981011 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | V,Y36H175P38*+TXV-BLEED | Y82E080B12LMPS1 | 33200 | 19 | 11.7 | 9 | 28800 | 24400 | 84.72% | 2 | 25800 | R-454B
216766564 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9X1C100U5PSB | 43500 | 15.2 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29200 | R-454B
216766612 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S9V2C080U5VSB | 43500 | 16.5 | 12.5 | 8.7 | 43500 | 32000 | 73.56% | 2.22 | 29000 | R-454B
216990540 | 4.13 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | A60VHA*+TXV | 88*TB60110C21*** | 49500 | 19 | 11.5 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
216990542 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | C48A***L16*+TXV | 88*TB60110C21*** | 48500 | 19 | 11 | 10.5 | 50500 | 52500 | 104% | 1.96 | 49500 | R-454B
215940964 | 3.58 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | CAA**4821AM*+UI | 59TN7A080C17**16 | 43000 | 20 | 10.5 | 9.5 | 48500 | 37400 | 77.11% | 2 | 40000 | R-454B
216453751 | 2.85 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R962V0403A17M4 | 34200 | 17 | 10.5 | 8.5 | 34200 | 24600 | 71.93% | 2.81 | 23800 | R-410A
216990239 | 2.73 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | A36VCA*+TXV | 88*TB36045C17*** | 32800 | 17 | 9 | 9 | 33600 | 25000 | 74.4% | 1.88 | 29600 | R-454B
216770034 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8X2C100M5PTC | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
216755380 | 2.58 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ30AA3 | CAA**3721AM* | 58SP*B110V21**22 | 31000 | 15.2 | 9.5 | 9 | 34200 | 30200 | 88.3% | 1.8 | 21200 | R-454B
213369635 | 2.45 | Yes | No | Dettson | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | EVD-30-O | *G33936+TD |  | 29400 | 15.2 | 10 | 9.35 | 31200 | 26600 | 85.26% | 1.8 | 21600 | R-410A
214625024 | 2.33 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)30B34+TDR |  | 28000 | 15.4 | 10.3 | 9 | 32400 | 27000 | 83.33% | 1.85 | 22400 | R-410A
216757953 | 2.6 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ30AA3 | CAA**4321AM* | 59SU5B100M21**20 | 31200 | 15.5 | 9.5 | 9 | 34200 | 30200 | 88.3% | 1.8 | 21400 | R-454B
216644663 | 1.54 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ18AA3 | FM(C,U)5Z30**AL* |  | 18500 | 15.5 | 11.5 | 12 | 20600 | 18600 | 90.29% | 2.08 | 15700 | R-454B
214229473 | 2.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EN(A,D)4X48L24** | *80MSU1002120A* | 35800 | 16.5 | 10 | 8.5 | 38500 | 34800 | 90.39% | 2 | 29200 | R-410A
216766630 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3+P0V0C000M50SD |  | 44000 | 17.1 | 12.5 | 9 | 43500 | 32000 | 73.56% | 2.24 | 29000 | R-454B
216766632 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S9X1D120U5PSB | 44000 | 16 | 12 | 9 | 44000 | 32400 | 73.64% | 2.24 | 29400 | R-454B
211755880 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE080C16MP11 | 32600 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.57 | 26000 | R-410A
211755884 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
216972744 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL60H210P17*+TXV | 58TN*B070C17**16 | 43500 | 20 | 10.5 | 9 | 47000 | 37000 | 78.72% | 2 | 39500 | R-454B
212505547 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | H,PG83936 | 987MB66120C24*** | 32800 | 17 | 11.5 | 8.1 | 30400 | 27200 | 89.47% | 2.2 | 30200 | R-410A
215487404 | 2.92 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA3610A* | CA*EA6030*3A* | D*80VC0805D*A* | 35000 | 18.5 | 10.5 | 8.5 | 35000 | 28400 | 81.14% | 2 | 22000 | R-32
216770036 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9V2C080U5PSC | 43500 | 16.5 | 12 | 8.7 | 43500 | 32000 | 73.56% | 2.22 | 29000 | R-454B
216770052 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8X2D120M5PTC | 43500 | 17.1 | 12 | 8.7 | 44500 | 32800 | 73.71% | 2.22 | 29800 | R-454B
216990272 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | A36VCA*+TXV | 88*TB48090C17*** | 33200 | 18 | 10 | 9 | 34200 | 25200 | 73.68% | 1.86 | 30000 | R-454B
216990273 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | C36A***L13*+TXV | 88*TB48090C17*** | 33200 | 18 | 10 | 9 | 34200 | 25200 | 73.68% | 1.86 | 30000 | R-454B
214320254 | 2.77 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | PL36H175P389 | R962V0703A17M4S | 33200 | 18 | 9.5 | 8.1 | 32600 | 29200 | 89.57% | 1.9 | 30400 | R-410A
215487486 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CA*EA2418*3A* | D*80VC0603B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
212864635 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | H,PG32930 | 88*TA36045C17*** | 23000 | 20 | 13 | 10 | 25200 | 19600 | 77.78% | 2.4 | 24000 | R-410A
216453752 | 2.78 | No | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)37A44+TDR | R962V0603A17M4 | 33400 | 17 | 9.8 | 8.5 | 34200 | 25000 | 73.1% | 2.77 | 24000 | R-410A
216453753 | 2.85 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R962V0603A17M4 | 34200 | 17 | 10.5 | 8.5 | 34200 | 25000 | 73.1% | 2.83 | 24000 | R-410A
215487481 | 1.42 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH6VSA1810A* | CHPEA2422*3A* | D*80VC0604B*A* | 17000 | 19 | 12 | 8.8 | 16800 | 13000 | 77.38% | 2.1 | 10800 | R-32
215224764 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG48960 | 59MN7C080C21**20 | 44500 | 21 | 12 | 9 | 44500 | 36000 | 80.9% | 2.26 | 42500 | R-410A
215425275 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE1K*36+TXV | TM8E080C16MP11 | 32800 | 19 | 11 | 8.5 | 29200 | 23600 | 80.82% | 2 | 25000 | R-454B
215425308 | 2.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YE1K*36+TXV | Y81E080C20SMPS1 | 34600 | 19 | 11 | 8.5 | 30800 | 25400 | 82.47% | 2 | 27400 | R-454B
214849129 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH360*9 | Y81E040A12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.06 | 25600 | R-410A
214776897 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV607**C+TXV | YPLC120C20MP13 | 53000 | 19 | 11 | 8.5 | 52000 | 38500 | 74.04% | 2 | 36200 | R-454B
215224758 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG9J936 | 59MN7C080C17**14 | 23400 | 20 | 13 | 10.5 | 25000 | 19400 | 77.6% | 2.46 | 23800 | R-410A
214849147 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CV361*9 | Y81E080B12SMPS1 | 33200 | 18 | 10 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
214849162 | 2.77 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CX361B935 | Y82E080B12LMPS1 | 33200 | 18 | 9.5 | 8.5 | 31400 | 23000 | 73.25% | 2.04 | 25400 | R-410A
215487438 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA6030*3A* | D*96VC1205DNA* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
214385473 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | H,YE35936 | *80CSU0601716A* | 31800 | 17 | 11.5 | 8.1 | 31400 | 24400 | 77.71% | 1.96 | 30600 | R-410A
216981003 | 1.9 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YG9J*30+TXV-BLEED | Y92E040A10SMPS1 | 22800 | 16 | 11.7 | 9 | 21400 | 16800 | 78.5% | 2 | 16200 | R-454B
215643930 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH360B*C+TXV | Y81E080B12SMPS1 | 22200 | 18 | 11 | 9.1 | 21200 | 17500 | 82.55% | 1.94 | 17200 | R-454B
214385716 | 1.93 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | H,YA10936 | *80CSU0401712A* | 23200 | 16 | 10.5 | 8.1 | 20400 | 16400 | 80.39% | 1.9 | 20000 | R-410A
215670359 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN1002122B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215670509 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0602120B* | 34400 | 16 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
214385386 | 2.5 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | H,YE35936 | *80MSU0601716A* | 30000 | 15.2 | 9 | 8.1 | 32600 | 27200 | 83.44% | 1.8 | 22400 | R-410A
212498512 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CE2403A+TXV |  | 23800 | 17 | 10 | 8.85 | 25600 | 25400 | 99.22% | 2.14 | 18500 | R-410A
206136076 | 2.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X37L21A*+WALLCON | *95CSU0802120A* | 33000 | 17.5 | 11.5 | 8.5 | 32800 | 25000 | 76.22% | 2 | 31800 | R-410A
206136126 | 2.65 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L24A*+WALLCON | *95CSU1002122A* | 31800 | 17.5 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
216770048 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8X2C100M5PTC | 43500 | 16.5 | 11.7 | 8.7 | 45000 | 33000 | 73.33% | 2.21 | 30200 | R-454B
215281559 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | SL6937 |  | 33000 | 18 | 10.5 | 8.7 | 31600 | 22800 | 72.15% | 2.1 | 23600 | R-410A
216770114 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC009AS3 | S8X2C100M5PSC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216797067 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | *UHMC100CCV4+LRP | 29800 | 18 | 9.8 | 8.5 | 32400 | 32400 | 100% | 2.81 | 37600 | R-454B
216797085 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2B080M4PDB | 29600 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.63 | 37600 | R-454B
216797102 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B060D3PSC+LRP | 30200 | 18 | 9.8 | 8.5 | 33800 | 33800 | 100% | 2.76 | 38500 | R-454B
216770026 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8X1C100M5PTC | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
213772698 | 1.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *96CTN0601714B* | 23200 | 16 | 10 | 8.1 | 22000 | 16800 | 76.36% | 1.88 | 21000 | R-410A
212626506 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.2 | 33800 | 29200 | 86.39% | 2.65 | 26400 | R-410A
212626641 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9V080B12MP12 | 31400 | 17 | 9.5 | 8.3 | 33800 | 29200 | 86.39% | 2.67 | 26400 | R-410A
211755932 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755775 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8V060A12MP12 | 31000 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
216972764 | 3.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H175P78*+TXV | 58TN*B090C17**16 | 42500 | 20 | 11 | 9.5 | 46500 | 35600 | 76.56% | 2 | 37400 | R-454B
216972794 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL60H210P17*+TXV | 58TN*B110C21**20 | 45000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 2 | 38000 | R-454B
216972796 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L18*+TXV | 58TN*B110C21**20 | 45000 | 21 | 11 | 9.5 | 46000 | 35800 | 77.83% | 2 | 38000 | R-454B
216972862 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | PL60H210P29*+TXV | 59MN7C080C21**20 | 43500 | 20 | 10.5 | 9.5 | 46000 | 36200 | 78.7% | 2 | 38500 | R-454B
215678258 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *97CTN0801716A* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2.02 | 19800 | R-454B
215678338 | 1.92 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *97CTN0801716A* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
206767543 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *95CSU0802120A* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
214505163 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA2422*4B*+MBVC1600**-1A* |  | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
206136176 | 2.7 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L21A*+WALLCON | *95CSU1002122A* | 32400 | 17.5 | 11.5 | 8.5 | 32600 | 24800 | 76.07% | 2 | 31400 | R-410A
213252519 | 2.52 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CF361E* |  | 30200 | 15.2 | 9 | 8.4 | 33400 | 27000 | 80.84% | 1.8 | 22600 | R-410A
216972864 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | A60VHA*+TXV | 59MN7C080C21**20 | 44500 | 21 | 10.5 | 9.5 | 46500 | 36600 | 78.71% | 2 | 39000 | R-454B
216972887 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | C60A***L19*+TXV | 59MN7C100C21**22 | 45000 | 21 | 10.5 | 9.5 | 46500 | 36400 | 78.28% | 2 | 39000 | R-454B
211755789 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
216972028 | 3.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | V,C48H175P78*+TXV | 58TN*B045C17**12 | 47000 | 17 | 10.5 | 11.5 | 50000 | 51000 | 102% | 1.9 | 49000 | R-454B
216972160 | 4.13 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P17*+TXV | 59CU5B100C21**22 | 49500 | 19 | 11.5 | 10.5 | 50000 | 52500 | 105% | 1.98 | 49500 | R-454B
214320245 | 2.77 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | PL36H175P389 | R921V0603A17M4S | 33200 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 1.9 | 30600 | R-410A
211627549 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TL8E060A12UH11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
214441912 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | V,C48H175P789 | 88*TB48070C17*** | 43500 | 20 | 11 | 9 | 45000 | 36600 | 81.33% | 2.14 | 43000 | R-410A
216972203 | 3.96 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | V,C48H175P78*+TXV | 59MN7C080C17**14 | 47500 | 17 | 11 | 12.5 | 49500 | 50500 | 102% | 1.98 | 48500 | R-454B
216972210 | 3.96 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C48A***L16*+TXV | 59MN7C080C17**14 | 47500 | 17 | 11 | 12.5 | 49500 | 50500 | 102% | 1.98 | 48500 | R-454B
216972262 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | PL60H210P17*+TXV | 59MN7C100C21**22 | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216972312 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C48A***L16*+TXV | 59TN6C080C21**20 | 48000 | 19 | 10.5 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
216972321 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L18*+TXV | 59TN6C080C21**20 | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
216972371 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | C60A***L19*+TXV | 59TN7A080C21**20 | 49000 | 19 | 11 | 10.5 | 50500 | 53000 | 105% | 1.94 | 50000 | R-454B
216797116 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B080U4VSB+LRP | 30200 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.72 | 37600 | R-454B
215726296 | 2.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | H,YG81*36+TXV+AEFE3A* |  | 34000 | 19 | 11.5 | 8.85 | 30000 | 24800 | 82.67% | 1.98 | 25000 | R-454B
216972946 | 3.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA348A*030* | V,C48H210P16*+TXV | 59TN7A080C21**20 | 43500 | 21 | 10.5 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216972376 | 4 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | V,C60H210P29*+TXV | 59TN7A100C21**22 | 48000 | 19 | 10.5 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
216770120 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TAM5D07AC51 |  | 51500 | 15.2 | 11 | 8.5 | 50500 | 38000 | 75.25% | 2.15 | 33400 | R-454B
211627688 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.2 | 25800 | 32600 | 126.4% | 2.88 | 26000 | R-410A
211628024 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM9V100C20MP12 | 31200 | 17.4 | 9.3 | 8.3 | 25800 | 32600 | 126.4% | 2.86 | 26000 | R-410A
216766914 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B006AS3 | S9X2B060U4PSB | 33000 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
216766941 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S8V2B080M4PDB | 32400 | 16 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.04 | 21200 | R-454B
216766955 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S8V2C080M5PDB | 32400 | 16 | 11.7 | 8.5 | 32400 | 24000 | 74.07% | 2.11 | 21200 | R-454B
216766966 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C007AS3 | S9V2C100U5VSB | 33600 | 17 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.18 | 21400 | R-454B
216766982 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD05AS3 | S8V2C100M5PDB | 32800 | 16 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.99 | 21600 | R-454B
216766989 | 2.8 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S8V2C100M5PCB | 33600 | 16.5 | 12 | 8.5 | 33400 | 24400 | 73.05% | 2.11 | 21600 | R-454B
216766998 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3+P0V0C000M50SD |  | 34400 | 17.1 | 12.5 | 8.7 | 32200 | 23800 | 73.91% | 2.17 | 21000 | R-454B
216453756 | 2.78 | No | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)37A44+TDR | U98MV0603A17UPS | 33400 | 17 | 9.8 | 8.5 | 34200 | 25000 | 73.1% | 2.77 | 24000 | R-410A
216767016 | 2.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*DD10AS3 | S9X2D120D5PSB | 33800 | 15.5 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.2 | 21200 | R-454B
215683880 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3717AM*+UI | 935CB48060C17*** | 33800 | 17 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
216767039 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X2B060D3PSB | 31400 | 15.5 | 11.2 | 8.7 | 31600 | 23600 | 74.68% | 2.13 | 21000 | R-454B
216767041 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X2B060U4PSB | 33000 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.15 | 21200 | R-454B
214385649 | 1.43 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,YA10936 | *95MSU0401712A* | 17100 | 16 | 10 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
206135814 | 2.68 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L24A*+WALLCON | *80CSU1002120A* | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.96 | 31400 | R-410A
211755957 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211755966 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
215683914 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 935CB66100C21*** | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215683982 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 88*TB60070C21*** | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
214570514 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X42L21A*+WALLCON | *95CSU1002122B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
214570664 | 2.03 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X43L21A*+WALLCON | *96CTN0802120B* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
214571164 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X42L21**+WALLCON | *95CSU0802120B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
216796721 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X1B060D3PSB | 31200 | 15.5 | 12 | 8.1 | 31800 | 22600 | 71.07% | 2.88 | 22000 | R-454B
214571214 | 2.02 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X48L21**+WALLCON | *80CTL0702120B* | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
215297507 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | V,Y36H210P177 | Y81E100C20SMPS1 | 34000 | 17 | 9.5 | 8.5 | 31800 | 23200 | 72.96% | 2.08 | 24000 | R-410A
216770020 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8X1C080M5PSC | 43500 | 16 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.22 | 29200 | R-454B
216767044 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X1B060D3PSB | 31400 | 15.5 | 11.2 | 8.7 | 31600 | 23600 | 74.68% | 2.13 | 21000 | R-454B
216767045 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9X1B040D3PSB | 31600 | 15.5 | 11 | 8.7 | 32000 | 24000 | 75% | 2.12 | 21400 | R-454B
216767046 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9V2B040D3VSB | 31400 | 15.5 | 11.2 | 8.7 | 31400 | 23600 | 75.16% | 2.12 | 20800 | R-454B
216770104 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8X1C100M5PSC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
214572484 | 2.62 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X36L21A*+WALLCON | *95CSU0802120B* | 31400 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.86 | 31200 | R-410A
216797071 | 2.45 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | L8V1A060U3VSB+LRP | 29400 | 17.5 | 9.8 | 8.1 | 33200 | 33200 | 100% | 2.7 | 38000 | R-454B
213252518 | 2.6 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CF371E* |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
216776397 | 4.29 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | AD-60(P,U)******+TXV-BLEED | Y91E100C20SMPS1 | 51500 | 18 | 10.5 | 8.3 | 52000 | 38000 | 73.08% | 1.96 | 36200 | R-454B
216797048 | 1.58 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | D(A,C,E)30A4J+TDR | *DHMB060CCV3+LRP | 18900 | 18 | 9.8 | 8.5 | 23200 | 23200 | 100% | 2.76 | 27800 | R-454B
216797080 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2B060M4PCB | 30400 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.69 | 38000 | R-454B
216797082 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2B060M4PDB | 30400 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.69 | 38000 | R-454B
210868911 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF75173LT80X | 34200 | 20 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
209880031 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF98MV510021UPS*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43500 | 127.2% | 2.2 | 41000 | R-410A
214573604 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X60L24**+WALLCON | *96CTN0802120B* | 32800 | 19 | 12 | 8.5 | 32200 | 24600 | 76.4% | 1.98 | 31200 | R-410A
211756093 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
214573654 | 2.63 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X36L21A*+WALLCON | *97CMN0802120B* | 31600 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.86 | 31200 | R-410A
214574074 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X60L24A*+WALLCON | *97CMN0802120B* | 32800 | 17.5 | 11.5 | 8.5 | 31600 | 24800 | 78.48% | 2 | 31000 | R-410A
216797087 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2C080M5PCB | 29800 | 18 | 9.8 | 8.5 | 32600 | 32600 | 100% | 2.85 | 37600 | R-454B
216797098 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B040U3PSC+LRP | 30200 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.72 | 37600 | R-454B
214574124 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X61L21A*+WALLCON | *97CMN0602120B* | 33000 | 17.5 | 11 | 8.5 | 32200 | 25000 | 77.64% | 1.98 | 31400 | R-410A
214574204 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X61L24A*+WALLCON | *96CTN0802120B* | 33200 | 18.5 | 11.5 | 8.5 | 31800 | 24800 | 77.99% | 2.02 | 31200 | R-410A
216797123 | 2.5 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2C100U4VSB+LRP | 30000 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.82 | 37000 | R-454B
214574354 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X48AAL+WALLCON | *95CSU1002122B* | 32600 | 17.5 | 11 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31600 | R-410A
216797119 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2C100D4VSB+LRP | 30200 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.67 | 37800 | R-454B
215669295 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CSU1002120A* | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215670129 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0401712A* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215940594 | 2.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAVA3817XMA*+UI | 59TN7A060C17**16 | 35200 | 20.5 | 11.5 | 8.5 | 39000 | 29400 | 75.38% | 2 | 33600 | R-454B
215942400 | 2.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA6021XMA*+UI | 59MN7C060C17**14 | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
215441377 | 2.83 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | V,Y36H210P177 | TM9E100C16MP12 | 34000 | 18 | 10 | 8.1 | 32000 | 23400 | 73.12% | 2.08 | 24200 | R-410A
216990308 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | PL48H210P75*+TXV | 88*TB48090C17*** | 44000 | 17 | 9.5 | 9 | 46500 | 33800 | 72.69% | 2.06 | 41500 | R-454B
211257747 | 1.55 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 58S(B,C)*A045E14**12 | 18600 | 16.5 | 11 | 8.5 | 18500 | 17500 | 94.59% | 2.14 | 12400 | R-410A
211257797 | 1.47 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 58TP*A045V14**12 | 17600 | 16.5 | 10.5 | 8.5 | 18500 | 19100 | 103.2% | 2.3 | 12400 | R-410A
211257830 | 1.51 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | OVMAAB042112 | 18100 | 15.5 | 10.5 | 8.5 | 19100 | 18900 | 98.95% | 2.26 | 12700 | R-410A
215669069 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CMN1002122B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215669135 | 2.8 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0701716B* | 33600 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
215669285 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN1002122B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215669505 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0601716B* | 34600 | 17.5 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215669635 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0902120B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
211257895 | 1.52 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3014AL* | 59SC2D060E14**12 | 18200 | 16 | 10.5 | 8.5 | 18700 | 18400 | 98.4% | 2.22 | 12500 | R-410A
211257915 | 1.55 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 58SU*A040E17**12 | 18600 | 16.5 | 11 | 9 | 19000 | 18200 | 95.79% | 2.22 | 12700 | R-410A
211257945 | 1.53 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | OVMAAB036098 | 18300 | 16 | 10.5 | 8.5 | 18900 | 18400 | 97.35% | 2.22 | 12600 | R-410A
211257946 | 1.52 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | OVLAAB036098 | 18200 | 15.5 | 10.5 | 8.5 | 18800 | 18400 | 97.87% | 2.22 | 12600 | R-410A
211257982 | 1.5 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CNPV*2414AL* | 59SC5B026E14**10 | 18000 | 15.5 | 10.5 | 8.5 | 19000 | 18700 | 98.42% | 2.24 | 12700 | R-410A
211257997 | 1.47 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CNPV*2417AL* | 59SU5A040E17**12 | 17600 | 16 | 11 | 8.5 | 18500 | 18800 | 101.6% | 2.26 | 12400 | R-410A
211258029 | 1.54 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CNPV*2417AL* | 59SC2D080E17**16 | 18500 | 16 | 11 | 8.5 | 19500 | 18400 | 94.36% | 2.24 | 12900 | R-410A
211258113 | 1.44 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | FB4CNP024L |  | 17300 | 16 | 10.5 | 8.5 | 18200 | 19400 | 106.6% | 2.34 | 12300 | R-410A
213607585 | 1.51 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | FG4ANXB24L* |  | 18100 | 16.5 | 11 | 8.5 | 18200 | 18200 | 100% | 2.2 | 12400 | R-410A
211628108 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9Y100C20MP11 | 32800 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.44 | 25600 | R-410A
215224757 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG7J936 | 59MN7C080C17**14 | 23200 | 20 | 13 | 10 | 25200 | 19500 | 77.38% | 2.4 | 24000 | R-410A
209880050 | 4.38 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA | FCCA6021SZEA | FF97MV510021DHS*A | 52500 | 18 | 10 | 8.1 | 52500 | 50500 | 96.19% | 1.9 | 51000 | R-410A
215939683 | 2.7 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CTN0601716A* | 32400 | 19 | 10.5 | 9 | 35600 | 27400 | 76.97% | 1.88 | 31400 | R-454B
215940383 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN0802120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 33000 | R-454B
215940433 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *97CTN0601716A* | 35200 | 21 | 11.7 | 8.5 | 38500 | 29400 | 76.36% | 2.02 | 33800 | R-454B
206767552 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *95CSU1002122A* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
215674119 | 3.67 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0802120B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.06 | 42500 | R-454B
211263060 | 1.47 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *80VTL0451412A* | 17600 | 16 | 11 | 8.5 | 18500 | 18800 | 101.6% | 2.26 | 12400 | R-410A
215674049 | 3.67 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0901716B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.06 | 42500 | R-454B
215674249 | 3.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
216770108 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TAMXD04AV31 |  | 33200 | 16 | 12 | 8.7 | 32800 | 24000 | 73.17% | 2.15 | 21200 | R-454B
208587414 | 4.42 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA1 | FHRAVM6021SJZECA |  | 53000 | 19 | 10 | 8.1 | 48500 | 45500 | 93.81% | 1.8 | 46500 | R-410A
211197886 | 4.38 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA | FCCA6021SZEA | FF98MV510021UPS*A | 52500 | 18 | 10 | 8.1 | 52000 | 49500 | 95.19% | 2 | 50000 | R-410A
215487431 | 3.38 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4210A* | CHPEA6030*3A* | D*80VC0804C*A* | 40500 | 17 | 10 | 8.6 | 41000 | 31000 | 75.61% | 2 | 28000 | R-32
215674239 | 3.75 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0602120B* | 45000 | 17.5 | 9.5 | 9 | 47500 | 34000 | 71.58% | 2.06 | 42000 | R-454B
215674419 | 3.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0802120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
211627571 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TL8E100C20UH11 | 32000 | 17.5 | 9.9 | 8.5 | 25400 | 31600 | 124.4% | 2.89 | 25400 | R-410A
211627662 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.2 | 25800 | 32600 | 126.4% | 2.88 | 26000 | R-410A
211627766 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 25200 | 31400 | 124.6% | 2.85 | 25200 | R-410A
211628091 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.2 | 25800 | 32600 | 126.4% | 2.86 | 26000 | R-410A
215669685 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0602120B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215669855 | 2.78 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CMN0601714B* | 33400 | 16 | 9 | 8.1 | 36000 | 25800 | 71.67% | 1.8 | 31000 | R-454B
215681318 | 3.67 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716B* | 44000 | 17 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.04 | 42500 | R-454B
215681468 | 3.83 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0802120B* | 46000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
215681488 | 3.79 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0801716A* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34200 | 71.25% | 2.06 | 42500 | R-454B
216767051 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S8V2B080M4PCB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
213773718 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L21A*+WALLCON | *80CTL0902120B* | 24000 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
215940583 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X38M17A*+WALLCON | *80CSU0401712B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215940683 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *97CTN1002122A* | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
215940903 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M24A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215681988 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *80CSU0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36200 | 72.4% | 2.12 | 46000 | R-454B
215682038 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *96CTN0802120B* | 48500 | 19 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
215682438 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0802120B* | 48500 | 19 | 10.5 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
216770092 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TAMXC03AV31 |  | 23800 | 17.1 | 12.7 | 8.5 | 22000 | 17200 | 78.18% | 1.95 | 15300 | R-454B
211168163 | 3.83 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4A6V0X48A1 | 4PXFH009AZ3+TDR | *UD2C080ACV4 | 46000 | 19 | 11.7 | 8.2 | 41500 | 41500 | 100% | 2.26 | 35800 | R-410A
216643568 | 1.53 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ18AA3 | CAA**1917AM* | 58SU*B040M17**12 | 18400 | 15.5 | 11.5 | 9.5 | 20000 | 17700 | 88.5% | 2 | 14900 | R-454B
215941053 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712B* | 45500 | 21.5 | 11.5 | 9.5 | 48500 | 36800 | 75.88% | 2 | 40000 | R-454B
206136276 | 2.7 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EN(A,D,W)4X48L21**+WALLCON | *95CSU0802120A* | 32400 | 17.5 | 11.7 | 8.1 | 32800 | 24800 | 75.61% | 1.96 | 31400 | R-410A
216735474 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)0701716A* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
216735493 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)0901714A* | 23000 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
215670289 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0801714B* | 34000 | 16.5 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215940763 | 2.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN1202422A* | 35000 | 21.5 | 12 | 8.5 | 38000 | 28200 | 74.21% | 2.02 | 32600 | R-454B
215670023 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *95CSU0601716B* | 33800 | 16 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
215670055 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN0801714B* | 33800 | 16.5 | 9 | 8.5 | 35800 | 25400 | 70.95% | 1.78 | 30800 | R-454B
215670439 | 2.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0901716B* | 34600 | 17 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
215670539 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN1002122B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 30000 | R-454B
209880048 | 4.38 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA | FCCA6021SZEA | FF96TV507021M4S*A | 52500 | 18 | 10 | 8.1 | 52500 | 50500 | 96.19% | 1.9 | 51500 | R-410A
216770082 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | L8V1C100U5VSB | 51500 | 15.2 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34200 | R-454B
213355364 | 2.93 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48D6 |  | 35200 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
215936620 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *80CTL0901716B* | 35600 | 22 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 33000 | R-454B
215936920 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0601714B* | 35600 | 21.5 | 12 | 8.5 | 37600 | 28200 | 75% | 2 | 32000 | R-454B
216990355 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | C60A***L19*+TXV | 88*TB60110C21*** | 45000 | 18 | 10 | 9 | 45500 | 33000 | 72.53% | 2.08 | 40500 | R-454B
213815733 | 3.67 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA481EA* | CA*EA6030*4A*+MBVK20DP1X00A* |  | 44000 | 17 | 10 | 8.6 | 44000 | 31000 | 70.45% | 2 | 28000 | R-410A
216734725 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VSN0801716B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
216453760 | 3.5 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48C44+TDR | R962V1005A21M4 | 42000 | 17 | 11 | 8.5 | 45500 | 35200 | 77.36% | 2.92 | 33200 | R-410A
212632718 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD30/36Y9 | EL296DF110XV60C* | 33400 | 20 | 13 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 32800 | R-410A
216766662 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S9X2C080U5PSB | 51000 | 15.2 | 10 | 8.7 | 52000 | 39000 | 75% | 2.18 | 34400 | R-454B
216766714 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S8V2D120M5PCB | 51000 | 15.2 | 11 | 8.7 | 51000 | 38500 | 75.49% | 2.19 | 33600 | R-454B
210868913 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF100215LT80X | 34200 | 20 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
214624881 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | V,C36H175P159 | 58SU*B040M17**12 | 35200 | 16 | 9.5 | 8.5 | 36200 | 34200 | 94.48% | 2.04 | 27800 | R-410A
214624897 | 2.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L139 | 58SU*B060M17**16 | 34200 | 16 | 9.5 | 8.5 | 36200 | 34200 | 94.48% | 2.06 | 28000 | R-410A
212603225 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG32936 | *96VTN0801716A* | 23800 | 16 | 10 | 8.5 | 25200 | 23000 | 91.27% | 1.92 | 18500 | R-410A
215940937 | 3.63 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0802120B* | 43500 | 20.5 | 10.5 | 9.5 | 48000 | 36600 | 76.25% | 2 | 39500 | R-454B
215940987 | 3.63 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN1002122A* | 43500 | 21 | 10.5 | 9.5 | 48000 | 36400 | 75.83% | 2 | 39500 | R-454B
216770070 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TAMXD07AV51 |  | 51000 | 15.2 | 11.2 | 8.7 | 50500 | 38000 | 75.25% | 2.16 | 33600 | R-454B
215670329 | 2.72 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN0401410B* | 32600 | 15.5 | 9 | 8.5 | 36000 | 25600 | 71.11% | 1.78 | 30800 | R-454B
215670579 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0801714B* | 34400 | 17 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
215670599 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1202422B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 30000 | R-454B
211628117 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9Y120D20MP11 | 31600 | 16.5 | 9.3 | 8.5 | 25400 | 31600 | 124.4% | 2.92 | 25400 | R-410A
215675348 | 3.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | FCMA5B60L0D*+WALLCON |  | 46500 | 19.5 | 10.5 | 9.5 | 47000 | 33000 | 70.21% | 2.2 | 41000 | R-454B
215675768 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *95CSU0802120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676618 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *80CTL0902120B* | 48000 | 19 | 10.5 | 9 | 50000 | 36400 | 72.8% | 2 | 46000 | R-454B
216770076 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S8X2D120M5PTC | 51500 | 16 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34400 | R-454B
215939837 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712B* | 34400 | 20.5 | 12 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 30000 | R-454B
215939867 | 2.85 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0801716A* | 34200 | 20 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30400 | R-454B
215937170 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CTL0901716B* | 44500 | 20.5 | 11.5 | 8.1 | 53500 | 37600 | 70.28% | 1.95 | 43000 | R-454B
215937840 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X48M21A*+WALLCON | *97CMN1002122B* | 44500 | 20 | 11 | 8.1 | 52000 | 38500 | 74.04% | 2 | 43500 | R-454B
216680592 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X30AAL | *97VTN0801716A* | 23800 | 16 | 10 | 9 | 26000 | 22800 | 87.69% | 1.76 | 19100 | R-410A
216681509 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *97VTN0802120A* | 24000 | 17 | 10 | 9 | 26000 | 22800 | 87.69% | 1.78 | 19000 | R-410A
215676668 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X60M24A*+WALLCON | *97CMN1202422B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
215682768 | 4.63 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0802120A* | 55500 | 17 | 8.5 | 8.5 | 60000 | 42000 | 70% | 1.9 | 51500 | R-454B
212348381 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | LEW30E4 |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
213205859 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A070E17**16 | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 22800 | 87.02% | 2.92 | 20600 | R-410A
213205861 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*A070E21**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.92 | 20200 | R-410A
213205895 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A090E21**20 | 23800 | 16 | 9.5 | 8.5 | 25800 | 22800 | 88.37% | 2.86 | 20400 | R-410A
214441914 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | V,C60H210P299 | 88*TB60090C21*** | 44000 | 21 | 12 | 9.5 | 44000 | 35600 | 80.91% | 2.28 | 42000 | R-410A
215683218 | 4.79 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X61M24A*+WALLCON | *97CTN0802120A* | 57500 | 18.5 | 9 | 9 | 64000 | 45000 | 70.31% | 2.08 | 56500 | R-454B
215669007 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL0902120B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215669023 | 2.87 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *95CSU0601716B* | 34400 | 17.5 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30600 | R-454B
215669507 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0601716B* | 34600 | 17.5 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215669557 | 2.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0801714B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215940187 | 2.85 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712B* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.94 | 29800 | R-454B
215940287 | 2.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CTN0601716A* | 35200 | 21 | 11.7 | 8.5 | 38500 | 29400 | 76.36% | 2 | 33400 | R-454B
214624847 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | V,C36H175P149 | 58SU*B060M17**16 | 29600 | 15.2 | 9 | 8.1 | 32200 | 27000 | 83.85% | 1.8 | 22400 | R-410A
214624849 | 2.48 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | PL36H175P159 | 58SU*B060M17**16 | 29800 | 15.2 | 9 | 8.1 | 32200 | 27000 | 83.85% | 1.8 | 22400 | R-410A
215940387 | 2.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
214624797 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L159 | 58SU*B060M17**16 | 23600 | 17 | 10.5 | 8.5 | 24000 | 23600 | 98.33% | 2 | 17800 | R-410A
213205928 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*A070V17**16 | 23800 | 16.5 | 9.5 | 8.1 | 25200 | 22600 | 89.68% | 2.91 | 20200 | R-410A
213205962 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*A110V21**22 | 23800 | 16.5 | 9.5 | 8.1 | 25000 | 22200 | 88.8% | 2.94 | 19900 | R-410A
215669825 | 2.82 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL1352422B* | 33800 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
213360270 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36U9 | EL297UH090XV60C* | 33600 | 21 | 13 | 8.6 | 32800 | 26200 | 79.88% | 1.8 | 29400 | R-410A
213360272 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/38X9 | EL297UH090XV60C* | 33600 | 21 | 13 | 8.6 | 32800 | 26200 | 79.88% | 1.8 | 29400 | R-410A
212632725 | 2.77 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Z9 | SL280DF060NV36B* | 33200 | 21 | 12.5 | 8.7 | 34400 | 29600 | 86.05% | 1.76 | 33000 | R-410A
212632770 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD24/35Y9 | SLP99DF110XV60C* | 33400 | 20 | 13 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 32800 | R-410A
214861576 | 4 | Yes | Yes | MDV | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOE30-48HFN10-M2X | MVBC-48HWFN10-MD2-D |  | 48000 | 17 | 10 | 10.2 | 50000 | 46000 | 92% | 2 | 40000 | R-454B
211756123 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
212498593 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CE1801A+TXV |  | 17400 | 17 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
213206129 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59SC5B080E21**20 | 23800 | 15.5 | 9.5 | 8.5 | 26000 | 22600 | 86.92% | 2.88 | 20400 | R-410A
213206178 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6B080V17**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.92 | 20200 | R-410A
213206211 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59TP6B100V21**20 | 23800 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.89 | 20000 | R-410A
216735578 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MSU0802120A* | 22800 | 16.5 | 11 | 8.5 | 20400 | 18300 | 89.71% | 1.98 | 17400 | R-454B
216765994 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB006AS3+P0V0B000M40SD |  | 23400 | 17.1 | 12.5 | 8.7 | 21600 | 17100 | 79.17% | 2.04 | 15200 | R-454B
212632693 | 1.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LD24/35Y9 | SLP99DF090XV36C* | 21800 | 20 | 12 | 9.3 | 20000 | 18200 | 91% | 1.76 | 23800 | R-410A
215669977 | 2.82 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0701716B* | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
215670041 | 2.83 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *95CSU1002122B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215670291 | 2.83 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0801714B* | 34000 | 16.5 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215670341 | 2.82 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN0601714B* | 33800 | 16 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
215670511 | 2.87 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0602120B* | 34400 | 16 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
213204110 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80ES(N,L)1102120A* | 23800 | 15.5 | 9 | 8.5 | 26200 | 27600 | 105.3% | 2.7 | 25000 | R-410A
213204192 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *92ESN1002120A* | 23800 | 16 | 9 | 8.5 | 26000 | 28200 | 108.5% | 2.61 | 25800 | R-410A
206765700 | 1.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0701412A* | 23600 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
206765934 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *80CTL0701716A* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213815727 | 1.92 | No | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DZ6VSA241EA* | CA*EA2422*4A*+MBVK16CP1X00A* |  | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
213739551 | 1.46 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | PL36H175P789 | *92MSN0601412A* | 17500 | 16 | 11 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
213739576 | 1.45 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG33936 | *96MSN0401410A* | 17400 | 16 | 10.5 | 8.5 | 16900 | 19100 | 113% | 2.34 | 11400 | R-410A
213739603 | 1.43 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG33936 | *96VSN0401410B* | 17100 | 17 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
213739642 | 1.45 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | PL36H175P789 | *96VTN0401712B* | 17400 | 16 | 10.5 | 8.5 | 16400 | 18400 | 112.2% | 2.24 | 11200 | R-410A
212603089 | 1.53 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG80936 | *92ESN0601412A* | 18300 | 16 | 11 | 8.5 | 17200 | 17900 | 104.1% | 2.22 | 11500 | R-410A
216747485 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80TV510021UH | 22800 | 20 | 13 | 8.5 | 22800 | 18400 | 80.7% | 1.8 | 20200 | R-454B
206136116 | 2.65 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L24A*+WALLCON | *95CSU0802120A* | 31800 | 17.5 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
206136166 | 2.7 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L21A*+WALLCON | *95CSU0802120A* | 32400 | 17.5 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 1.98 | 31400 | R-410A
212498559 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CP2403A+TXV+TD |  | 23000 | 16 | 10 | 8.5 | 24800 | 22600 | 91.13% | 1.84 | 18200 | R-410A
215670619 | 2.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | FCMA5B60L0D*+WALLCON |  | 35400 | 19.5 | 11.5 | 9.5 | 34000 | 24400 | 71.76% | 2.04 | 29400 | R-454B
215669951 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU1002120A* | 34000 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
212348390 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)W304+TDR |  | 23600 | 16 | 10 | 9 | 26200 | 23400 | 89.31% | 2.93 | 19200 | R-410A
213312839 | 1.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V36H***P039+CBPE3A* |  | 22800 | 17 | 9.5 | 8.6 | 25400 | 25400 | 100% | 2.1 | 18400 | R-410A
209880041 | 3.71 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF97MV508521DHS*A | 44500 | 19 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
215934540 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN1202422B* | 44500 | 20 | 10.5 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
214336387 | 3.67 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | C60A***L169 | 88*TA60090C21*** | 44000 | 21 | 12 | 9.5 | 44500 | 35800 | 80.45% | 2.28 | 42500 | R-410A
214395006 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*2417AL* | 59SC6A060M17**16 | 23400 | 16 | 10 | 9 | 26600 | 24200 | 90.98% | 2 | 19400 | R-410A
212348396 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | LEW30F4 |  | 23600 | 16 | 10 | 9 | 26200 | 23400 | 89.31% | 2.93 | 19200 | R-410A
215676718 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0701716B* | 48500 | 19 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215681698 | 3.79 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0802120B* | 45500 | 17 | 9.5 | 8.5 | 48000 | 33600 | 70% | 2.06 | 42000 | R-454B
215681868 | 3.96 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN0801716A* | 47500 | 18.5 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215681898 | 4 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN0802120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215682118 | 3.92 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X48M21A*+WALLCON | *80CSU0601716B* | 47000 | 18 | 9.5 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
212480132 | 2.03 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P159 | 59SU5A060E17**16 | 24400 | 17 | 10 | 8.5 | 24600 | 22000 | 89.43% | 1.86 | 18100 | R-410A
215942570 | 3 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAVA6124XMA*+UI | 59CU5B080C21**20 | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
212544188 | 1.49 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG80936 | *96VTN0401712A* | 17900 | 15.2 | 10.5 | 8.5 | 16900 | 18100 | 107.1% | 2.22 | 11400 | R-410A
212348387 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)W244+TDR |  | 23000 | 16 | 10 | 8.8 | 26000 | 23400 | 90% | 2.77 | 19000 | R-410A
216770103 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD09AS3 | S8X1C100M5PTC | 34400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
206136362 | 2.72 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X48AAL+WALLCON | *95CSU1002122A* | 32600 | 17 | 11 | 8.1 | 32800 | 24800 | 75.61% | 1.98 | 31600 | R-410A
216766977 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | S8V2C100M5PCB | 34200 | 17 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.2 | 21200 | R-454B
211264433 | 1.52 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *95ESN0261410A* | 18200 | 15.5 | 11 | 8.5 | 18800 | 18400 | 97.87% | 2.2 | 12600 | R-410A
211264700 | 1.52 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | OLV098A12* | 18200 | 15.5 | 11 | 8.5 | 18800 | 18400 | 97.87% | 2.2 | 12600 | R-410A
215670571 | 2.85 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0601714B* | 34200 | 16.5 | 9.5 | 8.5 | 34800 | 25200 | 72.41% | 1.78 | 30200 | R-454B
215224772 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | H,PG9J936 | 59MN7C080C17**14 | 33000 | 19 | 11.7 | 9.5 | 35200 | 25800 | 73.3% | 2.02 | 30400 | R-410A
216770119 | 4.33 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TAM5D06AC41 |  | 52000 | 15.5 | 11 | 8.5 | 50500 | 38000 | 75.25% | 2.15 | 33600 | R-454B
216770087 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*C007AS3 | *UHMC100CCV4 | 23600 | 17.5 | 13 | 9 | 21600 | 17100 | 79.17% | 2.05 | 15200 | R-454B
216734424 | 1.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80VSL0451412B* | 22200 | 16.5 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.94 | 17500 | R-454B
216776395 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AD-35(P,U)******+TXV-BLEED | Y92E060B12SMPS1 | 23000 | 18 | 11.7 | 9.5 | 21400 | 18100 | 84.58% | 2 | 16900 | R-454B
210868915 | 3.71 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF75214LT80X | 44500 | 19 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
216766979 | 2.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3+P0V0C000M50SD |  | 34400 | 17.1 | 12.5 | 9 | 32200 | 23800 | 73.91% | 2.22 | 21000 | R-454B
216766994 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S9V2C100D5VSB | 33400 | 16.5 | 12 | 8.5 | 33200 | 24400 | 73.49% | 2.1 | 21600 | R-454B
216766995 | 2.82 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S9X1C100D5PSB | 33800 | 15.5 | 11.7 | 8.7 | 33600 | 24600 | 73.21% | 2.11 | 21800 | R-454B
214624800 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 58SU*B060M17**16 | 23400 | 17 | 10 | 9 | 24600 | 25600 | 104.1% | 2.2 | 18100 | R-410A
211628109 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9Y100C20MP11 | 32200 | 15.5 | 9.4 | 8.1 | 34000 | 27400 | 80.59% | 2.45 | 25400 | R-410A
211628234 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 25400 | 31600 | 124.4% | 2.87 | 25400 | R-410A
215682568 | 4.04 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EVD5X61M24A*+WALLCON | *97CTN1202422A* | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36600 | 73.2% | 2.12 | 46500 | R-454B
213360279 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/38F9 | EL297UH110XV48C* | 33600 | 22 | 13 | 8.7 | 32800 | 26400 | 80.49% | 1.82 | 29600 | R-410A
213770628 | 2.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X25L17A*+WALLCON | *95CSU0601716B* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2.02 | 20600 | R-410A
213770828 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L17A*+WALLCON | *80CTL0701716B* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.94 | 20800 | R-410A
215941207 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0802120B* | 45000 | 20 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
216770110 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TAMXD06AV41 |  | 34000 | 17.1 | 12 | 8.7 | 32800 | 24200 | 73.78% | 2.18 | 21400 | R-454B
216770093 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TAMXD04AV31 |  | 23600 | 17.1 | 12.7 | 9 | 22000 | 17300 | 78.64% | 2.05 | 15400 | R-454B
214501071 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VM970803BNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
216643734 | 1.54 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ18AA3 | CAA**2517AM* | 58TP*B045V14**12 | 18500 | 15.2 | 11.7 | 9.5 | 20000 | 17600 | 88% | 2.02 | 14900 | R-454B
214522530 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36E34+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.5 | 33000 | 23200 | 70.3% | 2.02 | 25200 | R-410A
214522532 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36E34+TDR | Y81E080C16LMPS1 | 33000 | 18 | 10 | 8.5 | 33400 | 23600 | 70.66% | 2 | 25800 | R-410A
216734533 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80VTL0701716B* | 22400 | 16 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
214501073 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VM971005CNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214501055 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VC800603B*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214394629 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | U98MV1005A21UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214440914 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | V,C36H175P149 | 986TD42080C17*** | 32400 | 19 | 11.7 | 9 | 35000 | 27400 | 78.29% | 2.02 | 31800 | R-410A
215683626 | 1.92 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3017AM*+UI | 88*TB36045C17*** | 23000 | 16.5 | 10 | 8.5 | 24000 | 16800 | 70% | 1.86 | 20200 | R-454B
215683676 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3717AM*+UI | 88*TB48090C17*** | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
215683694 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 88*TB48070C17*** | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215683710 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 987MC42080C17*** | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
216728042 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | FTMA5X24L0B* |  | 23200 | 17 | 11 | 9 | 21400 | 19100 | 89.25% | 2 | 18000 | R-454B
215668807 | 2.75 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU1002120A* | 33000 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215677438 | 4.71 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V60*K*AAA* | EVD5X60M24A*+WALLCON | *80CSU1002120A* | 56500 | 18 | 9 | 9 | 63000 | 44500 | 70.63% | 2.08 | 55500 | R-454B
216766996 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*CD07AS3 | S8V2C080M5PCB | 33400 | 16.5 | 12 | 8.5 | 33400 | 24400 | 73.05% | 2.1 | 21600 | R-454B
216767011 | 2.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*D010AS3 | S8V2D120M5PDB | 34600 | 17.1 | 12.5 | 9 | 32400 | 24000 | 74.07% | 2.23 | 21200 | R-454B
215389816 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *96VTN0601716B* | 35400 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 1.94 | 29400 | R-410A
206136196 | 2.7 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L24A*+WALLCON | *95CSU1002122A* | 32400 | 17.5 | 11.5 | 8.5 | 32400 | 24800 | 76.54% | 2 | 31400 | R-410A
213796971 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149+CBPE4B* |  | 24000 | 16 | 10 | 8.9 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
213305977 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | CE2301C+TXV |  | 23400 | 17 | 9.5 | 8.75 | 25600 | 25400 | 99.22% | 2.12 | 18500 | R-410A
216675744 | 2.02 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X25M17A* | *80MS(N,L)0451714A* | 24200 | 15.2 | 10 | 8.5 | 23200 | 19100 | 82.33% | 1.96 | 18500 | R-454B
212603137 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P069 | *80VSL0451716A* | 23400 | 17 | 10 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212603139 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | FG32936 | *80VSL0451716A* | 23800 | 16 | 10 | 8.5 | 25200 | 23000 | 91.27% | 1.92 | 18500 | R-410A
212603153 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P789 | *80VSL0701716A* | 24000 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
213612051 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R802V0503A14DZ | 33000 | 15.4 | 10 | 8.1 | 34000 | 26600 | 78.24% | 2.79 | 25000 | R-410A
212603264 | 3.03 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | PL36H210P299 | *95ESU1002120A* | 36400 | 16 | 10.5 | 8.1 | 36800 | 34400 | 93.48% | 2.04 | 28200 | R-410A
216453141 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | 5PX*B006AS3 | S8V2B080M4PDB | 44000 | 19.2 | 11.7 | 9.4 | 47000 | 33400 | 71.06% | 2.1 | 42500 | R-454B
215869124 | 4.42 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X60A1 | 5PX*C007AS3 | S9V2C080U5VSB+LRP | 53000 | 18.1 | 10 | 8.5 | 56000 | 40500 | 72.32% | 2 | 49500 | R-454B
209880032 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF97MV510021DHS*A | 34200 | 19 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
215869126 | 4.42 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X60A1 | 5PX*C007AS3 | S9V2C100U5VSB+LRP | 53000 | 18.1 | 10 | 8.5 | 56000 | 40000 | 71.43% | 2 | 49500 | R-454B
216453091 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*B004AS3 | S8V2B060M4PCB | 34000 | 19.2 | 12 | 9.7 | 31400 | 25000 | 79.62% | 2.1 | 31400 | R-454B
216453111 | 3.02 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*D010AS3 | S8V2D120M5PCB | 36200 | 21 | 13 | 10 | 32000 | 24600 | 76.88% | 2.2 | 31200 | R-454B
215869108 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5TXCC005AS3 | S9V2C100U5VSB+LRP | 31800 | 18.1 | 10 | 8.5 | 32800 | 25600 | 78.05% | 2.1 | 31200 | R-454B
216770094 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCC005AS3 | *UHMC100CCV4 | 23000 | 17.1 | 12.7 | 8.7 | 21400 | 16900 | 78.97% | 1.99 | 15000 | R-454B
216770095 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCC007AS3 | *UHMC100CCV4 | 23600 | 17.5 | 13 | 9 | 21600 | 17100 | 79.17% | 2.05 | 15200 | R-454B
215375217 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R801V0755A21UHN | 45500 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375219 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R801V0755A21UHS | 44000 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375235 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R801V1005A21UHU | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
213350129 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y81E080C16LMPS1 | 32000 | 18 | 9.9 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213350130 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y81E080C16SMPS1 | 32000 | 18 | 9.9 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213350148 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E100B12SMPS1 | 32000 | 18.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214522508 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36C34+TDR | Y81E120C16LMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 23200 | 71.17% | 1.94 | 25000 | R-410A
212603164 | 2.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P789 | *80VTL0701716A* | 24200 | 17 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212603171 | 2.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | PL36H175P069 | *92ESN0801716A* | 24200 | 17 | 10.5 | 8.1 | 24600 | 22400 | 91.06% | 1.88 | 18100 | R-410A
213204385 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *80ES(N,L)0451412A* | 23400 | 16.3 | 10.2 | 8.4 | 26000 | 26200 | 100.8% | 2.71 | 25200 | R-410A
213204401 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0451712A* | 23800 | 17 | 10 | 8.5 | 26200 | 24800 | 94.66% | 2.57 | 24400 | R-410A
213204460 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80ES(N,L)0901714A* | 23600 | 16.9 | 10.3 | 8.4 | 25800 | 26000 | 100.8% | 2.76 | 25200 | R-410A
213204853 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92ESN0601412A* | 23600 | 17 | 10 | 8.5 | 25600 | 20000 | 78.12% | 2.87 | 18800 | R-410A
212293045 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TP9C120D20MP13 | 31800 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
214501049 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B*+MBVK12BP1X00A* |  | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
216770118 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TAMXD07AV51 |  | 43500 | 15.5 | 11.7 | 8.5 | 43500 | 32000 | 73.56% | 2.15 | 29200 | R-454B
216770121 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TAMXD06AV41 |  | 51500 | 15.5 | 11 | 8.5 | 51500 | 39000 | 75.73% | 2.14 | 34200 | R-454B
214501050 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B*+MBVK16CP1X00A* |  | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
213771928 | 1.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X30AAL+WALLCON | *80CTL0701412B* | 23800 | 16 | 10.5 | 8.1 | 21800 | 16800 | 77.06% | 1.98 | 21000 | R-410A
213772278 | 2.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *80CTL0701716B* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
212864643 | 2.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AD-32(P,U)*****9 | TM9E080B12MP12 | 34000 | 17 | 10 | 8.5 | 32200 | 23600 | 73.29% | 2.06 | 24400 | R-410A
215870945 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CX361B*35+TXV | Y81E100B12SMPS1 | 33000 | 18 | 11.7 | 8.5 | 28800 | 24400 | 84.72% | 2 | 25600 | R-454B
215870948 | 2.68 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH365B*C+TXV | YP9C060B12MP13 | 32200 | 16 | 10.5 | 8.4 | 29000 | 24800 | 85.52% | 1.98 | 26000 | R-454B
215870962 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH604**C+TXV | Y91E080C20SMPS1 | 44500 | 18 | 12 | 8.5 | 44500 | 33000 | 74.16% | 2 | 31600 | R-454B
215870979 | 3.79 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV606**C+TXV | Y91E100C20SMPS1 | 45500 | 18 | 11.7 | 8.5 | 45000 | 33600 | 74.67% | 2 | 32800 | R-454B
214522497 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36C34+TDR | Y81E080B12SMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 23600 | 72.39% | 2 | 25200 | R-410A
214522531 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36E34+TDR | Y81E080B12SMPS1 | 33000 | 18 | 9.5 | 8.5 | 33000 | 23400 | 70.91% | 2 | 25600 | R-410A
214522528 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36E34+TDR | Y81E040A12LMPS1 | 33200 | 18 | 10 | 8.5 | 33000 | 23400 | 70.91% | 1.94 | 25200 | R-410A
215375315 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R951V0855A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
215375345 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R962V1155A24M4S | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
216487739 | 4.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | CE(P,V)6021G48*+TXV | 88*TB60090C21*** | 55500 | 19 | 11 | 8.5 | 58500 | 46000 | 78.63% | 2.04 | 46500 | R-454B
216487754 | 4.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | CE(P,V)6024G48*+TXV | 987MC60080C21*** | 55500 | 18 | 11 | 8.1 | 58500 | 45500 | 77.78% | 1.95 | 46500 | R-454B
216487839 | 2.75 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CE(P,V)3617G34*+TXV | 986TD42080C17*** | 33000 | 18 | 9 | 9 | 33600 | 24800 | 73.81% | 1.88 | 29400 | R-454B
216487956 | 3.54 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)4821G1K*+TXV | 986TD42080C17*** | 42500 | 20 | 11 | 9 | 46500 | 34800 | 74.84% | 2 | 34800 | R-454B
215375251 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V0755A21DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375269 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R802V1005A21UHN | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375283 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1255A24UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375294 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R921V0705A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375303 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R921V1005A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375308 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R921V1155A24M4S | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375326 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R951V1155A24M4S | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375160 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R921V0403A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 31400 | 91.81% | 1.9 | 29600 | R-410A
216680650 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *97VTN0801716A* | 23400 | 16.5 | 10 | 9 | 25800 | 23800 | 92.25% | 1.78 | 18900 | R-410A
214501068 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VS960805CUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214500335 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4B*+MBVK12BP1X00A* |  | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
213350139 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E080C20SMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 28200 | 84.94% | 2.71 | 25600 | R-410A
212348373 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)W184+TDR |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
212348382 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | LEW30F4 |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
209880051 | 4.42 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1860MJAZCA | FCCA6021SZEA | FF96TV508521M4S*A | 53000 | 18 | 10 | 8.1 | 53000 | 50500 | 95.28% | 1.9 | 51500 | R-410A
212506454 | 2.92 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48A4 |  | 35000 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
213204930 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *95ESN0401712A* | 23800 | 15.2 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.82 | 19300 | R-410A
213204260 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *95ESN0601714A* | 23800 | 15.4 | 9.3 | 8.5 | 25400 | 24400 | 96.06% | 2.55 | 24200 | R-410A
213360222 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*35/36U9 | EL297UH070XV36B* | 22200 | 23 | 14 | 9.2 | 20000 | 20000 | 100% | 1.84 | 23200 | R-410A
216770084 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S9V2D120U5PSC | 51500 | 15.2 | 11.2 | 9 | 51500 | 39000 | 75.73% | 2.2 | 34200 | R-454B
215389818 | 2.95 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *96VTN0601716B* | 35400 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 1.94 | 29400 | R-410A
214393190 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R802V0504A17UHN | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393238 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R802V0754A17DZ | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394803 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | H,PG53936 | 59TN6C100C21**22 | 32400 | 18 | 11.5 | 8.5 | 30400 | 24400 | 80.26% | 2 | 30200 | R-410A
214595141 | 1.46 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M254+TDR |  | 17500 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214595142 | 1.5 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M304+TDR |  | 18000 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214609726 | 4.5 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4A6V0X60A1 | H,TG74960 | S8V2D120M5PCA | 54000 | 19 | 11.7 | 8.2 | 50000 | 39000 | 78% | 1.83 | 48500 | R-410A
216643595 | 1.48 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ18AA3 | CAA**2417AM* | 58SU*B060M17**16 | 17800 | 15.2 | 11 | 10 | 20600 | 18500 | 89.81% | 1.98 | 15600 | R-454B
214391641 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R801V0503A14DZ | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.84 | 15900 | R-410A
214391643 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R801V0503A14UH | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.88 | 15900 | R-410A
216797151 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S8V2C100M5PDB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.83 | 51000 | R-454B
216797168 | 3.75 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2C100D5PSC+LRP | 45000 | 18 | 10 | 8.1 | 45000 | 45000 | 100% | 2.59 | 51000 | R-454B
213350156 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E100C16SMPS1 | 32000 | 18 | 9.4 | 8.5 | 33400 | 28400 | 85.03% | 2.7 | 25800 | R-410A
215375379 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R962V1155A24M4S | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 50500 | 93.52% | 1.75 | 49000 | R-410A
215375112 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R801V0754A17DZ | 33000 | 18 | 10 | 8.1 | 34200 | 31400 | 91.81% | 1.9 | 29600 | R-410A
212506455 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48B4 |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
213258899 | 2.9 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D3G+TXV+JMVT12BC2N1+TDR |  | 34800 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
216770091 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TAM5C03AC21 |  | 23200 | 17.1 | 12.7 | 8.5 | 21800 | 16900 | 77.52% | 1.91 | 15100 | R-454B
215684032 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 935CB60080C21*** | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215684048 | 2.68 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 986TD30040C14*** | 32200 | 15.2 | 9 | 8.5 | 36200 | 25800 | 71.27% | 1.76 | 31200 | R-454B
215684082 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 935CB66100C21*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
204456843 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L17A*+WALLCON | *96CTN0801714A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.98 | 20800 | R-410A
209880038 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1836MJAZCA | FCCA6021SZEA | FF96TV307017M4S*A | 34200 | 19 | 12.5 | 8.5 | 35000 | 43000 | 122.9% | 2.2 | 37400 | R-410A
213796960 | 1.46 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P039+CBPE3A* |  | 17500 | 15.5 | 10.5 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
212292977 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM9Y100C20MP11 | 32200 | 15.5 | 9.4 | 8.1 | 34000 | 27400 | 80.59% | 2.45 | 25400 | R-410A
212986197 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *96MSN0401410A* | 23600 | 16 | 10 | 8.5 | 26200 | 24000 | 91.6% | 1.98 | 19200 | R-410A
212986906 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96MSN0601412A* | 23600 | 16.5 | 10 | 8.5 | 26200 | 23800 | 90.84% | 1.98 | 19100 | R-410A
212986956 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L14** | *96MSN0601412A* | 23400 | 16.5 | 10 | 8.1 | 26400 | 24200 | 91.67% | 2.02 | 19200 | R-410A
212987397 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96MSN0801716A* | 23600 | 17 | 10 | 8.5 | 26400 | 24200 | 91.67% | 2.02 | 19200 | R-410A
212987433 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *96MSN0801716A* | 24200 | 17 | 10 | 8.5 | 25200 | 22000 | 87.3% | 1.84 | 18800 | R-410A
209880029 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1824MJAZCA | FCCA2421HZEA | FF96TV307017M4S*A | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
215375230 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R801V1005A21UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375265 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R802V1005A21DZ | 45500 | 16 | 10 | 8.1 | 45500 | 32200 | 70.77% | 2.4 | 25200 | R-410A
213258897 | 2.9 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D36+JMVT12BC2N1+TDR |  | 34800 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
215941213 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN0802120B* | 45000 | 20 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
213796962 | 1.48 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P219+CBPE3A* |  | 17800 | 15.5 | 10.5 | 9 | 17100 | 19400 | 113.5% | 2.4 | 11500 | R-410A
214393775 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R951V0403A17UHU | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393792 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R951V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393825 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R951V0603A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393873 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R951V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393876 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V0703A17M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393926 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R951V0855A21M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215941483 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN1202422A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.95 | 43000 | R-454B
215941583 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X48M21A*+WALLCON | *97CTN1002122A* | 44500 | 20 | 11 | 8.1 | 52000 | 38500 | 74.04% | 2 | 43500 | R-454B
211168132 | 1.93 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4A6V8X24A1 | 4PXFH003AZ3+TDR | *DHMB060BCV3 | 23200 | 18 | 12 | 8.5 | 20200 | 19300 | 95.54% | 2.48 | 16800 | R-410A
211755778 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8V080B12MP12 | 32000 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.49 | 26400 | R-410A
216776392 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AD-30(P,U)******+TXV-BLEED | Y82E060A12LMPS1 | 21800 | 18 | 11 | 8.95 | 21200 | 18100 | 85.38% | 1.9 | 17100 | R-454B
213796973 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P219+CBPE3A* |  | 24000 | 16 | 10 | 8.9 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
214595157 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24I4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214393575 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R921V0403A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213613568 | 1.49 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24I4 |  | 17900 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
215224759 | 1.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG31930 | 59MN7C100C21**22 | 22600 | 20 | 12.5 | 10.5 | 25000 | 19300 | 77.2% | 2.48 | 23800 | R-410A
215941143 | 3.67 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN0802120B* | 44000 | 20 | 10.5 | 9 | 48500 | 36600 | 75.46% | 1.8 | 39500 | R-454B
214393690 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R921V0855A21M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393725 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R921V1005A21M4S | 33200 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394208 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | U802VA050317M | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394375 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | U97MV0603A17DHS | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213147357 | 2.58 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | C36A***L159+AEFE4B* |  | 31000 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
216439958 | 1.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | 5PX*B006AS3 | S9V2B060U4PSC+LRP | 22200 | 21.4 | 12 | 10 | 22600 | 18200 | 80.53% | 2.2 | 22200 | R-454B
214244037 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CNPV*3621AL*+UI | 59MN7C100C21**22 | 23200 | 19.5 | 13 | 9.5 | 26600 | 19900 | 74.81% | 2.38 | 25000 | R-410A
214624917 | 2.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | V,C36H175P139 | 58SU*B060M17**16 | 35000 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.86 | 28200 | R-410A
213350193 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y82E100C16LMPS1 | 32000 | 18 | 9.4 | 8.5 | 33400 | 28000 | 83.83% | 2.7 | 25600 | R-410A
213796969 | 1.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P039+CBPE3A* |  | 22800 | 16 | 9.5 | 8.6 | 25400 | 25400 | 100% | 2.1 | 18400 | R-410A
214569538 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4224AL*+UI | 58TN*B070C21**20 | 33200 | 19 | 11.5 | 9.5 | 37800 | 26600 | 70.37% | 2 | 32000 | R-410A
214569622 | 2.8 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*3612AL*+UI | 59CU5B080C21**20 | 33600 | 18 | 11.5 | 9 | 37000 | 26200 | 70.81% | 2.02 | 31600 | R-410A
214569624 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*3612AL*+UI | 59CU5B100C21**22 | 33800 | 18.5 | 11.5 | 9 | 37000 | 26200 | 70.81% | 2.02 | 31600 | R-410A
216990639 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | C60A***L19*+TXV | 88*TB60070C21*** | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
212348391 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | LEW30A4 |  | 23000 | 16 | 10 | 8.5 | 26000 | 23400 | 90% | 2.77 | 19000 | R-410A
213147347 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P219+AEFE3A* |  | 24000 | 18 | 10.5 | 8.9 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
214595154 | 1.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24F4 |  | 22800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214595156 | 1.98 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24H4 |  | 23800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
216440008 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*B004AS3 | S9V2B040U3PSC+LRP | 33200 | 18.4 | 12 | 9 | 32000 | 24200 | 75.62% | 2.1 | 30600 | R-454B
216440022 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*B006AS3 | S9V2B080D4PSC+LRP | 32000 | 17.2 | 11.7 | 9.4 | 31800 | 23600 | 74.21% | 2.1 | 30000 | R-454B
216440056 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*C005AS3 | S9V2C100D5PSC+LRP | 31600 | 17.2 | 11.7 | 9.4 | 31400 | 23400 | 74.52% | 2 | 29800 | R-454B
216440074 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*C007AS3+P0V0C000M50SD+LRP |  | 34200 | 20 | 12.7 | 9.4 | 32600 | 24200 | 74.23% | 2.1 | 30800 | R-454B
216440088 | 2.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*C009AS3 | S9V2C100U5PSC+LRP | 34800 | 20 | 12.7 | 9.4 | 32400 | 23800 | 73.46% | 2.1 | 30400 | R-454B
216440140 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5TXCB004AS3 | S9V2B040D3VSB+LRP | 31400 | 17 | 11.7 | 9.4 | 31400 | 23600 | 75.16% | 2 | 30000 | R-454B
216440142 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5TXCB004AS3 | S9V2B040D3PSC+LRP | 31400 | 17 | 11.7 | 9.4 | 31400 | 23600 | 75.16% | 2 | 29800 | R-454B
216440156 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5TXCB006AS3 | *DHMB080CCV3+LRP | 33200 | 18.2 | 11.7 | 9.7 | 31600 | 24600 | 77.85% | 2.1 | 31000 | R-454B
214776899 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH602**A+TXV | YPLC120C20MP13 | 53000 | 19 | 11 | 8.5 | 52000 | 38500 | 74.04% | 2 | 36200 | R-454B
214776964 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CX601C*35+TXV+AEF60CXP* |  | 54000 | 19 | 11.7 | 9 | 52000 | 38000 | 73.08% | 2 | 36200 | R-454B
214574061 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X60L24A*+WALLCON | *97CMN0602120B* | 32600 | 17.5 | 11 | 8.5 | 31800 | 25000 | 78.62% | 1.96 | 31200 | R-410A
214574411 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X60AAL+WALLCON | *95CSU1002122B* | 33000 | 18 | 11.5 | 8.5 | 32000 | 24800 | 77.5% | 2.02 | 31200 | R-410A
213738470 | 2.9 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | FG32936 | *80MS(N,L)0701712A* | 34800 | 16 | 9.5 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
211755910 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TP9C100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211755913 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.52 | 26000 | R-410A
211755929 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211755943 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YP9C080C16MP13 | 31200 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
211755944 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
211755945 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
211755946 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YP9C100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211755961 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YPLC080C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
214569420 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | CAP**6024AL*+UI | 58TN*B070C21**20 | 44500 | 21 | 11.5 | 10 | 46000 | 36400 | 79.13% | 2.32 | 43500 | R-410A
216981029 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV-BLEED | Y92E100C16SMPS1 | 44500 | 19 | 11 | 9 | 43500 | 32800 | 75.4% | 2 | 33000 | R-454B
216494128 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)4824G1K*+TXV | 88*TB48070C17*** | 44000 | 17 | 9.5 | 9 | 47000 | 34000 | 72.34% | 2.04 | 42000 | R-454B
211389574 | 2.77 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TM8Y100C16MP11 | 33200 | 18 | 10 | 8.5 | 33400 | 23400 | 70.06% | 2.06 | 26400 | R-410A
211389693 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DXXN1+TXV | TM8Y080B12MP11 | 34000 | 18 | 10 | 8.1 | 33600 | 23600 | 70.24% | 2.06 | 25200 | R-410A
211389926 | 2.83 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DXXN1+TXV | TM8V080C16MP12 | 34000 | 17 | 9.5 | 8.1 | 34000 | 24600 | 72.35% | 2.08 | 25600 | R-410A
211390310 | 2.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DBCN1 | LPLC080C16MP13 | 34000 | 17.5 | 10 | 8.5 | 33800 | 23800 | 70.41% | 2.08 | 25400 | R-410A
214569690 | 2.8 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CNPV*4824AL*+UI | 59MN7C060C21**20 | 33600 | 19 | 12 | 9 | 36800 | 26200 | 71.2% | 2.02 | 31400 | R-410A
214569704 | 2.85 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CNPV*6024AL*+UI | 59MN7C080C21**20 | 34200 | 20 | 12.5 | 9 | 36200 | 25600 | 70.72% | 2.02 | 30600 | R-410A
213779005 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**3721AL*+UI | 59MN7C080C17**14 | 32800 | 17 | 11 | 8.1 | 33000 | 25200 | 76.36% | 1.96 | 32000 | R-410A
213780805 | 2.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3621AL*+UI | 59MN7C100C21**22 | 31600 | 17 | 11 | 8.1 | 32800 | 24200 | 73.78% | 1.86 | 31000 | R-410A
211390792 | 2.8 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAUB36DXXN1+TXV | LPLC080B12MP13 | 33600 | 17 | 9.5 | 8.1 | 33600 | 23600 | 70.24% | 2.02 | 25400 | R-410A
211390845 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAUB30CXXN1+TXV | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 23600 | 70.24% | 2 | 26400 | R-410A
213780725 | 2.6 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3621AL*+UI | 58TN*B045C17**12 | 31200 | 16.5 | 10.5 | 8.1 | 33400 | 24600 | 73.65% | 1.82 | 31400 | R-410A
213781395 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4824AL*+UI | 58TN*B090C21**20 | 32400 | 17 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213781595 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6121AL*+UI | 59MN7C060C17**14 | 33000 | 17 | 11 | 8.1 | 32200 | 25200 | 78.26% | 1.94 | 31400 | R-410A
215375164 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R921V0703A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 31400 | 91.81% | 1.9 | 29600 | R-410A
213779505 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4824AL*+UI | 58TN*B135C24**22 | 32400 | 17.5 | 11.5 | 8.5 | 32400 | 24800 | 76.54% | 1.98 | 31200 | R-410A
213782015 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 59TN6C080C17**14 | 32400 | 16 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.92 | 31600 | R-410A
215375351 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R801V1005A21UHS | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
215375360 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R802V1005A21UHN | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
215375369 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R921V1005A21M4S | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 51000 | 94.44% | 1.75 | 49500 | R-410A
213781485 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6024AL*+UI | 58TN*B135C24**22 | 32800 | 17.5 | 11.5 | 8.1 | 31800 | 24600 | 77.36% | 1.98 | 30800 | R-410A
213779305 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4321AL*+UI | 59MN7C060C17**14 | 32600 | 16.5 | 11 | 8.1 | 33000 | 25400 | 76.97% | 1.94 | 32000 | R-410A
213779325 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4321AL*+UI | 59MN7C100C21**22 | 33000 | 17 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 1.98 | 31600 | R-410A
213779425 | 2.67 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4821AL*+UI | 59MN7C060C17**14 | 32000 | 16.5 | 10.5 | 8.1 | 32800 | 25200 | 76.83% | 1.94 | 31600 | R-410A
213779525 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**4824AL*+UI | 59MN7C120C24**22 | 32200 | 17 | 11 | 8.1 | 32600 | 24800 | 76.07% | 1.98 | 31200 | R-410A
214569438 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | CAP**6121AL*+UI | 59MN7C060C21**20 | 44500 | 20.5 | 11 | 9.5 | 46500 | 37000 | 79.57% | 2.3 | 44000 | R-410A
216487787 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)3614G34*+TXV | 986TD30040C14*** | 22600 | 16 | 9.5 | 8.5 | 23000 | 16600 | 72.17% | 1.84 | 19400 | R-454B
216487804 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)3614G34*+TXV | 986TD42080C17*** | 23200 | 17 | 10 | 9 | 22600 | 16200 | 71.68% | 1.98 | 19000 | R-454B
213780785 | 2.6 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3621AL*+UI | 59MN7C060C17**14 | 31200 | 16.5 | 10.5 | 8.1 | 33200 | 24600 | 74.1% | 1.82 | 31400 | R-410A
216761974 | 2.12 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG9J936 | 927TA48060V17*** | 25400 | 18 | 11.5 | 10 | 24400 | 32800 | 134.4% | 2.5 | 18700 | R-410A
214569488 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | CNPV*4821AL*+UI | 59MN7C080C21**20 | 44000 | 20.5 | 11.5 | 9 | 46500 | 36600 | 78.71% | 2.16 | 43500 | R-410A
213780075 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CSPH*4212AL*+UI | 59MN7C100C21**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
213780175 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CSPH*4812AL*+UI | 58TN*B090C21**20 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31400 | R-410A
214391652 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R801V1004A17UHN | 22400 | 16 | 11.9 | 8.3 | 23000 | 17000 | 73.91% | 3.03 | 16300 | R-410A
214391666 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R802V0754A17UH | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.87 | 15900 | R-410A
213781585 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6121AL*+UI | 59CU5B060C17**16 | 33000 | 17 | 11 | 8.1 | 32200 | 25000 | 77.64% | 1.96 | 31400 | R-410A
213781665 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6124AL*+UI | 58TN*B110C21**20 | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31000 | R-410A
213781935 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 58TN*B110C21**20 | 32600 | 16.5 | 11 | 8.1 | 32800 | 24600 | 75% | 1.94 | 31400 | R-410A
216494111 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)3621G34*+TXV | 987MC66100C21*** | 22600 | 17 | 9.5 | 9 | 22000 | 15900 | 72.27% | 2.02 | 18600 | R-454B
213782065 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 58TN*B070C17**16 | 32600 | 16.5 | 11 | 8.1 | 33200 | 25000 | 75.3% | 1.94 | 31600 | R-410A
213782115 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 59CU5B060C17**16 | 32400 | 16 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31800 | R-410A
216494129 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)4824G1K*+TXV | 88*TB48090C17*** | 44000 | 17 | 9.5 | 9 | 46500 | 33800 | 72.69% | 2.06 | 41500 | R-454B
213782135 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 59MN7C080C17**14 | 32400 | 16.5 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31800 | R-410A
214393754 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R951V0403A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393786 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V0403A17UHU | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393739 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R951V0403A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393774 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R951V0403A17UHU | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393872 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R951V0703A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393925 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R951V0855A21M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394023 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R962V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214391692 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R962V0703A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.88 | 15900 | R-410A
214392795 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R801V0504A17UHU | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392812 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R801V0504A17UHU | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392830 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R801V0704A17UHU | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393215 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R802V0504A17UHS | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
216681542 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X30AAL | *97VTN0802120A* | 23800 | 16 | 10 | 9 | 26000 | 22800 | 87.69% | 1.78 | 19100 | R-410A
213821188 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0701712A* | 23600 | 17.5 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.9 | 19000 | R-410A
213821236 | 1.88 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80VTL1102122B* | 22600 | 17.3 | 10.2 | 8.4 | 25400 | 20200 | 79.53% | 2.97 | 18800 | R-410A
213821240 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *80VTL1102122B* | 23000 | 17.5 | 10.3 | 8.5 | 25400 | 20200 | 79.53% | 2.99 | 18800 | R-410A
213821254 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *92MSN0601714A* | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213821270 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36C34+TDR | *92MSN1002120A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.93 | 19100 | R-410A
215375346 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R801V0755A21DZ | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 50500 | 93.52% | 1.75 | 49000 | R-410A
214394725 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R921V1005A21M4S | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214394778 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U97MV0855A21DHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214595162 | 1.98 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36C4 |  | 23800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213781375 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4821AL*+UI | 59TN6C080C17**14 | 32200 | 17 | 11 | 8.1 | 32800 | 25000 | 76.22% | 1.96 | 31400 | R-410A
214394655 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V1005A21UHS | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394664 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V1255A24DZ | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
213779675 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**6121AL*+UI | 59CU5B060C17**16 | 33000 | 17 | 11 | 8.1 | 32200 | 25000 | 77.64% | 1.96 | 31400 | R-410A
213779775 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CAP**6124AL*+UI | 59MN7C100C21**22 | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31000 | R-410A
215375364 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R802V1255A24UHS | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
215942399 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
215942419 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
215942569 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *80CTL0702120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215375372 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R951V0855A21M4S | 51500 | 16.9 | 9.8 | 8.1 | 54000 | 51000 | 94.44% | 1.75 | 49500 | R-410A
214394699 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R802V1255A24DZ | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394729 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R921V1155A24M4S | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
215942389 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
215941043 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0802120B* | 45000 | 21 | 11 | 9.5 | 48500 | 37000 | 76.29% | 2 | 40000 | R-454B
215941193 | 3.67 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1002122A* | 44000 | 20 | 10.5 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
212506472 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48B6 |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
215940893 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M24A*+WALLCON | *97CTN0802120A* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
213796974 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139+CBPE4B* |  | 24000 | 16 | 10 | 8.85 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
215940023 | 2.8 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0802120B* | 33600 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
214393795 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R951V0603A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393911 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R951V0855A21M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393927 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R951V0855A21M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214244053 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CNPV*4217AL*+UI | 59MN7C060C17**14 | 23600 | 19.5 | 13 | 10 | 26600 | 19900 | 74.81% | 2.44 | 25000 | R-410A
216439972 | 1.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | 5TAMXC03AV31 |  | 21800 | 22 | 12 | 9.7 | 22800 | 17900 | 78.51% | 2.2 | 22000 | R-454B
216738842 | 1.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *96VTN0801716B* | 22600 | 16 | 11 | 8.1 | 20800 | 18400 | 88.46% | 1.85 | 17500 | R-454B
216739011 | 2 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | FEVB0036**+NAVA53601CK |  | 24000 | 15.2 | 11 | 8.5 | 21800 | 19200 | 88.07% | 1.98 | 18200 | R-454B
215942493 | 2.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0901716B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.02 | 32600 | R-454B
215941673 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X60M21A*+WALLCON | *96CTN0802120B* | 45500 | 20.5 | 11 | 8.1 | 53000 | 38500 | 72.64% | 1.95 | 43500 | R-454B
214394056 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R962V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213780695 | 2.62 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3617AL*+UI | 59MN7C080C17**14 | 31400 | 16.5 | 10.5 | 8.1 | 33200 | 24400 | 73.49% | 1.82 | 31400 | R-410A
214393814 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R951V0603A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393865 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R951V0703A17M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393916 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R951V0855A21M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394068 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R962V0703A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
211756012 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.5 | 25200 | R-410A
211756027 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9E060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.46 | 25800 | R-410A
216680892 | 1.46 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EHD4X30AAL | *97VTN0801716A* | 17500 | 15.5 | 10.5 | 8.1 | 18000 | 18100 | 100.6% | 2 | 12200 | R-410A
214394696 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V1005A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394773 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U802VA125524Z | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394748 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R951V1155A24M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214394782 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U97MV1005A21DHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394789 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U98MV0855A21UPS | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
215939973 | 2.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CTN0601716A* | 33000 | 18 | 10.5 | 9 | 35600 | 27400 | 76.97% | 1.9 | 31400 | R-454B
215942629 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0802120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
214393717 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R921V1005A21M4S | 32800 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394200 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | U802VA050317M | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215675496 | 4 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU0601716A* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
214391661 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R802V0504A17UHN | 22400 | 16 | 11.9 | 8.3 | 23000 | 17200 | 74.78% | 3.06 | 16400 | R-410A
213780745 | 2.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3621AL*+UI | 58TN*B090C17**16 | 31600 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.84 | 31000 | R-410A
213780845 | 2.72 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3721AL*+UI | 58TN*B045C17**12 | 32600 | 16.5 | 10.5 | 8.1 | 33200 | 25400 | 76.51% | 1.94 | 32000 | R-410A
214394618 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | U98MV1005A21UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393229 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R802V0504A17UHS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393262 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R802V0754A17DZ | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393581 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R921V0403A17M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393650 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R921V0703A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213739496 | 1.47 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | PL36H175P159 | *80MS(N,L)0701412A* | 17600 | 16 | 11 | 8.5 | 16900 | 18700 | 110.7% | 2.3 | 11400 | R-410A
214392741 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R801V0504A17UHN | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214392752 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R801V0504A17UHN | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393568 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R921V0403A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393702 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R921V0855A21M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394248 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | U802VA075317Z | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394268 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | U802VA075317Z | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394449 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | U97MV0855A21DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
214393782 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R951V0403A17UHU | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394392 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | U97MV0603A17DHS | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214392870 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R801V0754A17DZ | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393590 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R921V0403A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214570431 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *80CTL0702120B* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
214570601 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L24A*+WALLCON | *96CTN0802120B* | 23800 | 17 | 11 | 8.5 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
214570751 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L24A*+WALLCON | *95CSU1002122B* | 24000 | 17 | 11 | 8.5 | 20800 | 16500 | 79.33% | 2.02 | 20400 | R-410A
214571201 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EN(A,D,W)4X42L21**+WALLCON | *96CTN0802120B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
214572521 | 2.63 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X36L21A*+WALLCON | *96CTN0802120B* | 31600 | 17.5 | 11 | 8.1 | 32800 | 24200 | 73.78% | 1.86 | 31000 | R-410A
214572671 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L24A*+WALLCON | *95CSU1002122B* | 31800 | 17.5 | 11 | 8.5 | 32800 | 24400 | 74.39% | 1.9 | 31200 | R-410A
214572741 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X43L21A*+WALLCON | *97CMN0602120B* | 32800 | 17 | 11 | 8.5 | 33000 | 25400 | 76.97% | 1.98 | 32000 | R-410A
214573191 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X48AAL+WALLCON | *80CTL0702120B* | 32600 | 17.5 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
213772748 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0901716B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
213772798 | 2.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *96CTN0601714B* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20600 | R-410A
213772848 | 1.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *80CTL0701412B* | 23600 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.9 | 20800 | R-410A
214393783 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R951V0403A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393933 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R951V1005A21M4S | 33000 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394016 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R962V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394066 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R962V0703A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393704 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R921V0855A21M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393711 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R921V1005A21M4S | 33200 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215940783 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN0802120A* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215940883 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN0802120B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
214393605 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R921V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393608 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R921V0603A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393724 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R921V1005A21M4S | 33200 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213780895 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3721AL*+UI | 59CU5B060C17**16 | 32800 | 17 | 11 | 8.5 | 33000 | 25200 | 76.36% | 1.96 | 31800 | R-410A
213781545 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6121AL*+UI | 58TN*B070C17**16 | 32800 | 17 | 11 | 8.1 | 32200 | 25000 | 77.64% | 1.96 | 31200 | R-410A
213781715 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6124AL*+UI | 59TN6C120C24**22 | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31000 | R-410A
215942459 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *97CMN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
213781945 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 58TN*B135C24**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.96 | 31400 | R-410A
213780225 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CSPH*4812AL*+UI | 59MN7C080C17**14 | 32400 | 16.5 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31800 | R-410A
214394608 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | U98MV1005A21UPS | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
212976070 | 2.05 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3721AL* | 59TP6C080V17**16 | 24600 | 17 | 10.5 | 8.5 | 25200 | 21200 | 84.13% | 1.78 | 18700 | R-410A
214393765 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R951V0403A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393799 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R951V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
213613569 | 1.5 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24J4 |  | 18000 | 15.2 | 10 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214394743 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R951V1005A21UHU | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394792 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U98MV1005A21UPS | 52000 | 17 | 9.8 | 8.1 | 54500 | 49500 | 90.83% | 1.75 | 51000 | R-410A
214394660 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V1005A21UHU | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214392728 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R801V0504A17UHN | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214392731 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R801V0504A17UHN | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214392780 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R801V0504A17UHS | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393815 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R951V0603A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393914 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R951V0855A21M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393949 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R951V1005A21M4S | 33200 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394049 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R962V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394450 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | U97MV0855A21DHS | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
214392798 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R801V0504A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392811 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R801V0504A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392848 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R801V0754A17DZ | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393598 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R921V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393648 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R921V0703A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393649 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R921V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
212293093 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | YP9C120D20MP13 | 31800 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
213307189 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM8Y100C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
213307205 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM9V120D20MP12 | 30800 | 16.8 | 9.2 | 8.3 | 32000 | 28000 | 87.5% | 2.74 | 25200 | R-410A
213307339 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TL9E080C16UH11 | 31200 | 17.4 | 9.3 | 8.1 | 33600 | 28000 | 83.33% | 2.62 | 25600 | R-410A
216767050 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9V2B060U4VSB | 33400 | 16.5 | 12 | 8.7 | 32600 | 24200 | 74.23% | 2.16 | 21400 | R-454B
212292872 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM8V100C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
213307177 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM8E100B12MP11 | 31400 | 17.8 | 9.8 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
213307350 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM8V080C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.62 | 25200 | R-410A
214522496 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36C34+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 23400 | 71.78% | 2 | 25800 | R-410A
212293113 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | YPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
213927825 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
216761957 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG21930 | 927TA48060V17*** | 17500 | 17 | 10.5 | 10 | 16600 | 29200 | 175.9% | 2.26 | 16800 | R-410A
213307169 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TL8E100C20UH11 | 31200 | 17.4 | 9.8 | 8.3 | 33600 | 27200 | 80.95% | 2.62 | 25200 | R-410A
213307188 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM8Y080C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
213739563 | 1.47 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG80936 | *95MSU0401712A* | 17600 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
211756060 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.44 | 25600 | R-410A
211756077 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLV060A12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211756096 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211756128 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | YPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
214393700 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R921V0855A21M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394785 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U97MV1155A24DHS | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394651 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V1005A21UHN | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394703 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R802V1255A24UHN | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394720 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R921V0705A21M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214391895 | 3.21 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | CP49B34+TDR | R802V1005A21DZ | 38500 | 15.3 | 11 | 8.1 | 40000 | 30000 | 75% | 2.94 | 28600 | R-410A
213307356 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM8Y080C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
215942489 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0702120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.02 | 32600 | R-454B
215939863 | 2.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0601716A* | 34000 | 19.5 | 11 | 9 | 35200 | 26800 | 76.14% | 1.94 | 30800 | R-454B
213307353 | 2.55 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM8V120C20MP12 | 30600 | 16.2 | 8.7 | 8.4 | 32000 | 27600 | 86.25% | 2.65 | 25000 | R-410A
213307372 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM9V100C20MP12 | 31200 | 17.4 | 9.3 | 8.1 | 33600 | 28200 | 83.93% | 2.65 | 25800 | R-410A
216761987 | 3.13 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG1K936 | 927TA48080V17*** | 37600 | 18 | 11 | 11.5 | 42000 | 41500 | 98.81% | 2.3 | 37400 | R-410A
216761988 | 3.21 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG48936 | 927TA60080V21*** | 38500 | 18 | 11.5 | 11.5 | 42500 | 41500 | 97.65% | 2.34 | 37400 | R-410A
211390878 | 2.78 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DXXN1+TXV | TMLV060A12MP12 | 33400 | 16.5 | 9.5 | 8.1 | 33600 | 23800 | 70.83% | 2.02 | 25200 | R-410A
212293065 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
212506452 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M48A4 |  | 32400 | 17 | 10 | 8.5 | 37200 | 28000 | 75.27% | 2.88 | 25200 | R-410A
214522660 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36C34+TDR | Y81E040A12LMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 23000 | 70.55% | 1.89 | 25800 | R-410A
212293117 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | YPLC120C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
212506451 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E4 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
215668725 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0601714B* | 34200 | 17.5 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.88 | 30600 | R-454B
215668845 | 2.77 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CTL0902120B* | 33200 | 18 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 30800 | R-454B
214394636 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V0755A21DZ | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214394668 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V1255A24UH | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
213772448 | 2.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *80CTL0701716B* | 24200 | 16.5 | 10.5 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213772528 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *97CMN1002122B* | 24200 | 16 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
215375253 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R802V0755A21DZ | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
214501064 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VC960603BNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
211178366 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | G*VS800604BUA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
211178373 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | G*VC960803BNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
216770024 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S8X1C100M5PSC | 43500 | 16.5 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29400 | R-454B
215375273 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R802V1005A21UHS | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375288 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R802V1505A24UHN | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
214394647 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V1005A21DZ | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394672 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V1505A24UH | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394722 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R921V0855A21M4S | 52000 | 17 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
213307185 | 2.55 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM8V120C20MP12 | 30600 | 16.2 | 8.7 | 8.4 | 32000 | 27600 | 86.25% | 2.65 | 25000 | R-410A
213307351 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM8V100C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.62 | 25200 | R-410A
216765916 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCA001AS3 | S8V2A040M3PDB | 21600 | 15.2 | 11.5 | 10.5 | 21200 | 16100 | 75.94% | 1.9 | 22000 | R-454B
216765918 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCA001AS3 | S8V2A040M3PCB | 21600 | 15.2 | 11.5 | 10.5 | 21200 | 16100 | 75.94% | 1.9 | 22000 | R-454B
214391942 | 3.17 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | CP61B34+TDR | U802VA100521M | 38000 | 15.5 | 10 | 8.2 | 39000 | 27600 | 70.77% | 2.83 | 27000 | R-410A
214391979 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | R801V1005A21DZ | 44000 | 15.3 | 10 | 8.1 | 45500 | 36000 | 79.12% | 2.99 | 33600 | R-410A
214392043 | 3.63 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | U802VA075421Z | 43500 | 15.3 | 10 | 8.1 | 45000 | 33800 | 75.11% | 2.99 | 32200 | R-410A
216019537 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YG7J(1,2)36+TXV-BLEED | TM9Y040A10MP11 | 22400 | 16 | 11.5 | 8.8 | 21400 | 17600 | 82.24% | 1.96 | 16600 | R-454B
215654003 | 1.98 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | F,PE*E31(1,2)25+TXV-BLEED |  | 23800 | 19 | 11.7 | 9.25 | 22400 | 16600 | 74.11% | 2.04 | 17400 | R-454B
214394708 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V1255A24UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394726 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R921V1005A21M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215375365 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R802V1505A24UHN | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
214394644 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V0755A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394659 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V1005A21UHU | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214394795 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U98MV1155A24UPS | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394675 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R802V0755A21DZ | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214392045 | 3.63 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | U802VA100521M | 43500 | 15.3 | 10 | 8.1 | 45000 | 33400 | 74.22% | 2.97 | 32000 | R-410A
213147367 | 3.02 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | V,C36H175P139+AEFE4B* |  | 36200 | 16 | 9.5 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
213774495 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CSPH*4212AL*+UI | 59MN7C120C24**22 | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
213369433 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG7J936 | 59TP6C080V21**20 | 35200 | 16 | 9.5 | 8.1 | 36800 | 34800 | 94.57% | 1.9 | 28400 | R-410A
211178351 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VC800603B*A* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
213821304 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96VTN0401410B* | 23200 | 16 | 10 | 8.5 | 26200 | 20400 | 77.86% | 2.85 | 19200 | R-410A
214501083 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4B* | G*VC801005C*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
216679974 | 2.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4821AL* | 59TP7A080V17**16 | 35600 | 16 | 10 | 8.5 | 38500 | 34400 | 89.35% | 1.8 | 29200 | R-410A
216494145 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CE(P,V)3621G34*+TXV | 88*TB60110C21*** | 32800 | 20 | 11.5 | 9.5 | 32800 | 25800 | 78.66% | 2.04 | 29200 | R-454B
215375222 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R801V1005A21DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32200 | 70.77% | 2.4 | 25200 | R-410A
215375239 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R801V1255A24DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375254 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R802V0755A21UHN | 44000 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375270 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R802V1005A21UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
214263959 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J(1,2)36+TXV | A96DS2V045B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
214263960 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J(1,2)36+TXV | A96DS2V070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
215375212 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R801V0755A21DZ | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375231 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R801V1005A21UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375232 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R801V1005A21UHS | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375245 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R801V1255A24UH | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
207455127 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/36F9 | SL280UH090V36B* | 33800 | 22 | 13 | 8.8 | 32800 | 25600 | 78.05% | 1.84 | 30000 | R-410A
207455174 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*23/37Z9 | SL280UH100NV60C* | 34000 | 21 | 13.5 | 8.8 | 33600 | 27000 | 80.36% | 1.82 | 31800 | R-410A
207455176 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/38X9 | SL280UH110V60C* | 34000 | 21 | 13.5 | 8.8 | 33800 | 27000 | 79.88% | 1.84 | 31800 | R-410A
207455241 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36U9 | SLP99UH070XV36B* | 33800 | 21 | 13 | 8.8 | 33000 | 25800 | 78.18% | 1.82 | 30200 | R-410A
207455242 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36S9 | SLP99UH070XV36B* | 33800 | 21 | 13 | 8.8 | 33000 | 25800 | 78.18% | 1.82 | 30200 | R-410A
207455257 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36U9 | SLP99UH090XV48C* | 34000 | 22 | 13.5 | 8.5 | 32200 | 27000 | 83.85% | 1.82 | 29400 | R-410A
215375248 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R801V1505A24UH | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
214501063 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VC960403BNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
211178359 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VM970803BNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
213612090 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R802V0755A21UH | 44000 | 15.4 | 10 | 8.1 | 45500 | 36600 | 80.44% | 3.03 | 34000 | R-410A
214394198 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | U802VA050317M | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214263893 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J936 | A80DS2V090B16 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.16 | 15800 | R-410A
215735537 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE31*30+TXV-BLEED | TM9V080B12MP12 | 21800 | 17 | 11 | 8.5 | 21200 | 17300 | 81.6% | 1.9 | 17000 | R-454B
215375260 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R802V0755A21UHS | 45500 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375299 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R921V0855A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
215375317 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R951V0855A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
215375342 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R962V1155A24M4S | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
214269891 | 1.95 | Yes | Yes | DUCANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | H,A,DG9J936 | EFV12BCA | 23400 | 19 | 12 | 8.5 | 22400 | 16000 | 71.43% | 2.18 | 15700 | R-410A
215375271 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1005A21UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375272 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R802V1005A21UHS | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375290 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R802V1505A24UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375323 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R951V1005A21UHU | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
216794474 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | L8V1B080U4VSB+LRP | 41500 | 19 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.76 | 51000 | R-454B
216794499 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S8V2B080M4PDB | 42000 | 19.2 | 11.7 | 9 | 47000 | 42500 | 90.43% | 2.75 | 50500 | R-454B
213612094 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R802V1005A21DZ | 44000 | 15.4 | 10 | 8.1 | 45500 | 36000 | 79.12% | 3.01 | 33600 | R-410A
213612096 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R802V1005A21UH | 44000 | 15.4 | 10 | 8.1 | 45500 | 36000 | 79.12% | 3.01 | 33600 | R-410A
213147363 | 2.97 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L129+AEFE4B* |  | 35600 | 16 | 9.5 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
215375307 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R921V1155A24M4S | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375320 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R951V1005A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375322 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R951V1005A21UHU | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375215 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R801V0755A21UHN | 44000 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375228 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R801V1005A21UHN | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375229 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R801V1005A21UHN | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375246 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R801V1505A24UH | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
207172511 | 1.97 | Yes | Yes | DUCANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | 42BX**+TXV | 80G2UH090BE12 | 23600 | 19 | 12 | 8.5 | 22400 | 19100 | 85.27% | 2.22 | 13300 | R-410A
213773720 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X48L21A*+WALLCON | *80CTL0902120B* | 24000 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
213204326 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0601714A* | 23600 | 15.5 | 9 | 8.1 | 25200 | 25800 | 102.4% | 2.67 | 24800 | R-410A
213204333 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0601714A* | 23800 | 15.5 | 9.5 | 8.1 | 25200 | 27000 | 107.1% | 2.74 | 25800 | R-410A
216763408 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | L8V1A060U3VSB | 23800 | 17.1 | 12.5 | 9 | 22000 | 17500 | 79.55% | 2 | 15500 | R-454B
216763410 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B006AS3 | L8V1B080U4VSB | 23600 | 17.1 | 12.5 | 9 | 21800 | 17300 | 79.36% | 2 | 15400 | R-454B
216763426 | 1.95 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD04AS3 | S9V2B040D3PSC | 23400 | 17.1 | 12.5 | 8.2 | 22200 | 17200 | 77.48% | 1.8 | 15400 | R-454B
215675476 | 3.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *96CTN0802120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
208665249 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LD42/61Y9 | SLP99DF110XV60C* | 45500 | 20 | 12 | 9 | 42000 | 35000 | 83.33% | 1.84 | 40000 | R-410A
214394667 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V1255A24UH | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394716 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V1505A24UHS | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394719 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R921V0705A21M4S | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214394733 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R951V0705A21M4S | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
216764127 | 1.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S9V2B040D3PSC | 21800 | 16 | 11.5 | 8.7 | 21200 | 16900 | 79.72% | 1.9 | 15000 | R-454B
216764143 | 1.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | *DHMB060CCV3 | 22000 | 16.5 | 11.7 | 9 | 21200 | 16900 | 79.72% | 2 | 15100 | R-454B
215937027 | 3.71 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CTL1102120B* | 44500 | 20 | 11 | 8.1 | 52000 | 38000 | 73.08% | 1.9 | 43500 | R-454B
216732510 | 1.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M14A* | *80MS(N,L)0701412A* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 17900 | R-454B
216732677 | 1.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *80MS(N,L)0701412A* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 17900 | R-454B
216732709 | 1.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *80MS(N,L)0901714A* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.98 | 18000 | R-454B
213307357 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM8Y100C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
216770097 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C009AS3 | L9X1C100U5VSA | 33200 | 16 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.16 | 21200 | R-454B
214263977 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J(1,2)36+TXV | A97DSMV070B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
215375262 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R802V1005A21DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32200 | 70.77% | 2.4 | 25200 | R-410A
215375279 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1255A24UHN | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375296 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R921V0705A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375298 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R921V0855A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
213886650 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG1K936 | A96DS2V070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
216687207 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF80TV507521UH | 45500 | 19 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
215375263 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1005A21DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32200 | 70.77% | 2.4 | 25200 | R-410A
216494146 | 2.68 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CE(P,V)3621G34*+TXV | 88*TB66135C24*** | 32200 | 20 | 11 | 9.5 | 32400 | 25400 | 78.4% | 2.06 | 28800 | R-454B
216797093 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2C100M5PDB | 29800 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.83 | 37800 | R-454B
216794367 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2B060M4PCB | 32800 | 20 | 12 | 9 | 32200 | 31600 | 98.14% | 2.9 | 39000 | R-454B
216794383 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2C100M5PCB | 33000 | 20 | 12 | 10 | 32200 | 31600 | 98.14% | 2.9 | 39000 | R-454B
216794440 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2C100D5VSB+LRP | 32000 | 19.9 | 12 | 9 | 32200 | 30200 | 93.79% | 2.68 | 36600 | R-454B
215937430 | 3.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN0801714B* | 44000 | 20 | 11.5 | 8.1 | 53500 | 37600 | 70.28% | 2 | 42500 | R-454B
215912377 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
216734144 | 1.83 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *96VSN0401410B* | 22000 | 15.5 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
213772898 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *97CMN0801714B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.9 | 20800 | R-410A
213772948 | 1.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0701412B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.92 | 20800 | R-410A
216733026 | 1.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *96CTN0601714B* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19200 | 91.43% | 1.94 | 18000 | R-454B
213773048 | 1.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *80CTL0701716B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.92 | 20800 | R-410A
213773698 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L21A*+WALLCON | *80CTL0701716B* | 24000 | 17 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
216794453 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | *DHMC100CCV4+LRP | 42000 | 19.6 | 11.7 | 9 | 46000 | 42500 | 92.39% | 2.61 | 51000 | R-454B
216794468 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | *UHMD120CCV5+LRP | 42000 | 20 | 12 | 9.5 | 47000 | 42500 | 90.43% | 2.72 | 50500 | R-454B
216794503 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S8V2C080M5PCB | 42000 | 20 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.74 | 51000 | R-454B
216794237 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | L8V1A040U3VSB+LRP | 19500 | 21 | 11.2 | 10 | 22400 | 21800 | 97.32% | 2.92 | 26800 | R-454B
216794318 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B080D4PSC+LRP | 19500 | 20.3 | 11 | 10 | 23000 | 22000 | 95.65% | 2.93 | 27000 | R-454B
216794520 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S8V2D120M5PCB | 43000 | 20.4 | 11.7 | 9.5 | 47000 | 42500 | 90.43% | 2.74 | 50500 | R-454B
216794571 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2C100U5PSC+LRP | 42000 | 20 | 12 | 9.5 | 46500 | 42000 | 90.32% | 2.79 | 50000 | R-454B
216797092 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2C100M5PCB | 30400 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.87 | 37600 | R-454B
216797110 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B080D4PSC+LRP | 30400 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.72 | 38500 | R-454B
216797111 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B080D4VSB+LRP | 29800 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.68 | 38500 | R-454B
213205003 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN0401712A* | 23000 | 16 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213821193 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0701716A* | 23000 | 17.5 | 10.3 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213821209 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0902116A* | 22800 | 17.4 | 10.3 | 8.5 | 25200 | 19900 | 78.97% | 2.99 | 18600 | R-410A
213821241 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *92MSN0401712A* | 23000 | 16 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
214263947 | 2 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J(1,2)36+TXV | A96DF1E045B12 | 24000 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
216770040 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S8X1C100M5PTC | 43500 | 16.5 | 11.7 | 8.7 | 45000 | 33000 | 73.33% | 2.21 | 30200 | R-454B
216797057 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | *DHMB060CCV3+LRP | 29600 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.72 | 39000 | R-454B
213826689 | 3.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV7X48A1 | 4TXCC009DS3 | S9V2C100U4VSB+LRP | 46500 | 17.1 | 11.7 | 8.5 | 40500 | 28400 | 70.12% | 1.8 | 37000 | R-410A
215375264 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R802V1005A21DZ | 45500 | 16 | 10 | 8.1 | 45500 | 32200 | 70.77% | 2.4 | 25200 | R-410A
215375280 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R802V1255A24UHN | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375282 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R802V1255A24UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375312 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R951V0705A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375313 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R951V0705A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375314 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R951V0855A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
215375332 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R962V0705A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
207455425 | 3.71 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LH40/61W9 | SL297UH080NV60C* | 44500 | 20 | 12 | 9.2 | 43500 | 37200 | 85.52% | 1.82 | 44500 | R-410A
207455460 | 3.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LH42/62W9 | SLP99UH110XV60C* | 46000 | 20 | 12.5 | 9.4 | 42000 | 35800 | 85.24% | 1.9 | 41000 | R-410A
212977574 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**2417AL* | 58S(B,C)*B045M14**12 | 23400 | 17 | 10 | 9 | 27000 | 26200 | 97.04% | 2.2 | 19400 | R-410A
213821243 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *92MSN0401712A* | 23400 | 16 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
213821284 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)36B34+TDR | *96MSN0401712A* | 23200 | 16 | 9.5 | 8.5 | 26200 | 20400 | 77.86% | 2.86 | 19200 | R-410A
213821332 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30B34+TDR | *96VTN1002120B* | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
213770998 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *96CTN0601714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.94 | 20800 | R-410A
215735530 | 3.58 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YE35*48+TXV-BLEED | TM9Y100C16MP11 | 43000 | 16 | 10.5 | 8.3 | 42500 | 33400 | 78.59% | 1.96 | 32000 | R-454B
213163591 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | H,FG82936+AEFE3A* |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
215939883 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0802120A* | 34400 | 20 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.96 | 30000 | R-454B
216770064 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TAM5D06AC41 |  | 52000 | 16 | 11.2 | 8.7 | 50500 | 38000 | 75.25% | 2.17 | 33600 | R-454B
213312841 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V36H175P139+CBPE4B* |  | 24000 | 18 | 10.5 | 8.85 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
212479884 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 58S(B,C)*A070E21**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22400 | 91.06% | 1.9 | 18100 | R-410A
216767014 | 2.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*D010AS3 | S8V2D120M5PCB | 34600 | 17.1 | 12.5 | 9 | 32400 | 24000 | 74.07% | 2.23 | 21200 | R-454B
214501065 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VS960603BUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
215643927 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CV360**C+TXV | Y81E080B12SMPS1 | 21800 | 18 | 11 | 8.9 | 21200 | 17500 | 82.55% | 1.9 | 17100 | R-454B
216683193 | 2.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CSPH*3612AL* | 59TP7A120V24**22 | 35600 | 15.5 | 9.8 | 8.5 | 38500 | 34600 | 89.87% | 1.78 | 29200 | R-410A
211178350 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VS800604BUA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
212479982 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P159 | 58TP*A070V17**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212480027 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 59SC2D080E17**16 | 24000 | 17 | 10 | 8.5 | 25200 | 23400 | 92.86% | 1.96 | 18400 | R-410A
212480048 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 59SC5B040E14**10 | 24200 | 15.2 | 10 | 8.5 | 25000 | 22000 | 88% | 1.82 | 18400 | R-410A
211178357 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VC960803BNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
211178375 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | G*VM970803BNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
216733294 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X25M17A* | *80CTL0701716B* | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216764146 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B006AS3 | S9V2B060U4PSC | 23800 | 18 | 12.7 | 9 | 21800 | 17400 | 79.82% | 2 | 15500 | R-454B
216764176 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8X1A040M3PSC | 23000 | 17.5 | 12 | 8.7 | 21800 | 17200 | 78.9% | 2 | 15300 | R-454B
216764211 | 1.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9V2B060D3PSC | 22400 | 17.1 | 12 | 9 | 21200 | 17000 | 80.19% | 2 | 15100 | R-454B
216764213 | 1.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB006AS3 | S9V2B080D4PSC | 22400 | 17.1 | 12 | 9 | 21400 | 17100 | 79.91% | 2 | 15200 | R-454B
216733696 | 1.83 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M14A* | *80CTL0701412B* | 22000 | 16.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
215942643 | 3 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN1002122A* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
216796574 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8X2C100M5PTC | 31200 | 15.2 | 11.7 | 8.5 | 31400 | 22400 | 71.34% | 3 | 21800 | R-454B
216796577 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X2C100M5PTC | 31800 | 15.5 | 11.7 | 8.5 | 31600 | 22600 | 71.52% | 3.03 | 22000 | R-454B
215375348 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R801V0755A21UHS | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 50500 | 93.52% | 1.75 | 49500 | R-410A
215375349 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R801V1005A21DZ | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
212608498 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*TT3931 |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
214775804 | 4.42 | No | No | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,DE48960 | WPV100T5BA | 53000 | 15.2 | 9.5 | 8.4 | 56000 | 40500 | 72.32% | 1.78 | 37000 | R-410A
216796490 | 2.58 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8V2C100M5PDB | 31000 | 15.2 | 12 | 8.1 | 31000 | 22200 | 71.61% | 2.93 | 21600 | R-454B
216794522 | 3.54 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S8V2D120M5PCB | 42500 | 20.4 | 11.7 | 9.5 | 46500 | 42500 | 91.4% | 2.72 | 51000 | R-454B
216794547 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2C080U5VSB+LRP | 42000 | 20 | 12 | 9.5 | 46500 | 42000 | 90.32% | 2.75 | 50000 | R-454B
216796414 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | L8V1C100U5VSB | 31400 | 15.2 | 12 | 8.5 | 31000 | 21800 | 70.32% | 2.92 | 21400 | R-454B
212989187 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *95MSU0601716A* | 23800 | 17.5 | 10 | 8.5 | 26200 | 23800 | 90.84% | 1.98 | 19100 | R-410A
212977610 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CAP**3017AL* | 58S(B,C)*B045M14**12 | 23600 | 17 | 10 | 8.5 | 26000 | 24000 | 92.31% | 2 | 19100 | R-410A
214392119 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R801V0503A14DZ | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392120 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R801V0503A14DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392152 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R801V0504A17UHN | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392236 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R801V0754A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392269 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R801V1004A17UH | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
214392285 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0503A14DZ | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392472 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R921V0703A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214501057 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VS800604BUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214501062 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4B* | G*VC801005C*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214501080 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4B* | G*VC800804C*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214501082 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4B* | G*VS800805CUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214392504 | 1.68 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R951V0403A17UHU | 20200 | 17.7 | 9 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392539 | 1.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R951V0603A17UHU | 21400 | 18 | 10 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392588 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R962V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392301 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0503A14UHN | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392338 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R802V0504A17UHN | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392353 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R802V0504A17UHS | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392656 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | U802VA075317Z | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
215375078 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0704A17UHU | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
215375086 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R802V0504A17UHN | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
215375087 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R802V0504A17UHS | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
215375088 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R802V0754A17DZ | 21600 | 17 | 10 | 8.1 | 22600 | 18900 | 83.63% | 2.1 | 16800 | R-410A
216687166 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF95SV304017M4 | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
216687168 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF92SV306017M4 | 22800 | 21 | 13 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
216687183 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80SV407517UH | 22800 | 21 | 13 | 10 | 22800 | 18400 | 80.7% | 1.8 | 21200 | R-454B
216687185 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80SV407017UH | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
212976741 | 2.52 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | CAP**4224AL* | GG96VTAB60100C** | 30200 | 15.2 | 9 | 8.1 | 34200 | 27400 | 80.12% | 1.8 | 23600 | R-410A
215375096 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R951V0403A17M4S | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
215375098 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R951V0603A17M4S | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 17000 | R-410A
216763592 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S8X1B080M4PSC | 32600 | 17.1 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
216763628 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S9V2B040U3PSC | 33000 | 17.1 | 12 | 9 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216763642 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD04AS3 | S9V2B060D3PSC | 32400 | 17 | 11.7 | 8.2 | 33400 | 24600 | 73.65% | 1.9 | 21600 | R-454B
215941003 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN0802120B* | 44500 | 21 | 11 | 9.5 | 48500 | 36600 | 75.46% | 2 | 39500 | R-454B
215941033 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1202422A* | 44500 | 21 | 11 | 9.5 | 48000 | 36400 | 75.83% | 2 | 39000 | R-454B
215941083 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0802120A* | 45000 | 21 | 11 | 9.5 | 48500 | 37000 | 76.29% | 2 | 40000 | R-454B
215941103 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN0802120B* | 45500 | 21 | 11 | 9.5 | 48500 | 37000 | 76.29% | 2 | 40000 | R-454B
213821353 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0701412A* | 29600 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
213147359 | 2.53 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | V,C36H175P139+AEFE4B* |  | 30400 | 15.2 | 8.5 | 8.4 | 33800 | 26400 | 78.11% | 1.84 | 22800 | R-410A
215375081 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0754A17UHS | 21600 | 17 | 10 | 8.1 | 22600 | 18900 | 83.63% | 2.1 | 16800 | R-410A
216794364 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2A040M3PDB | 32400 | 20 | 11.7 | 9 | 32400 | 31600 | 97.53% | 2.75 | 39000 | R-454B
214392200 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R801V0704A17UHU | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392359 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R802V0754A17DZ | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
215941133 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN1202422A* | 45500 | 21.5 | 11.5 | 9.5 | 48500 | 36600 | 75.46% | 2 | 39500 | R-454B
215941153 | 3.67 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU0401712B* | 44000 | 20 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
206136342 | 2.72 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X42AAL+WALLCON | *95CSU1002122A* | 32600 | 17 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31600 | R-410A
211387841 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33600 | 23600 | 70.24% | 2.02 | 26600 | R-410A
216794348 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | *UHMB080CCV3+LRP | 32800 | 20.4 | 12 | 9.5 | 32400 | 31600 | 97.53% | 2.9 | 39000 | R-454B
216794389 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2D120M5PCB | 33000 | 20.9 | 12.5 | 9 | 31800 | 31000 | 97.48% | 2.86 | 38000 | R-454B
216794280 | 1.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B040D3PSC+LRP | 18600 | 19.2 | 11 | 9 | 23000 | 21800 | 94.78% | 2.71 | 26600 | R-454B
216794491 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S8V2B080M4PCB | 42000 | 19.2 | 11.7 | 9 | 47000 | 42500 | 90.43% | 2.79 | 50500 | R-454B
216794539 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2C080U5PSC+LRP | 42000 | 20 | 12 | 9.5 | 46500 | 42000 | 90.32% | 2.79 | 50000 | R-454B
212293021 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TMLV120C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
216754783 | 2.65 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH30AAK | EA*5X37M21A* | *80CSU0601716A* | 31800 | 15.2 | 9.5 | 9 | 34400 | 30200 | 87.79% | 1.8 | 21400 | R-454B
215375101 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R962V0403A17M4S | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
215375074 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0503A14UH | 21600 | 18 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
211388100 | 2.65 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC30CXXN1+TXV | TP9C060B12MP13 | 31800 | 16.5 | 9 | 8.1 | 33000 | 23200 | 70.3% | 1.96 | 26000 | R-410A
211388114 | 2.65 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC30CXXN1+TXV | LP9C060B12MP13 | 31800 | 16.5 | 9 | 8.1 | 33000 | 23200 | 70.3% | 1.96 | 26000 | R-410A
211388643 | 2.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TM9E100C16MP12 | 33000 | 17.5 | 10 | 8.5 | 33000 | 23200 | 70.3% | 2.04 | 26200 | R-410A
214331344 | 3.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,A,DG50960 | WPV080T4BA | 46000 | 17 | 10 | 8.5 | 48000 | 34600 | 72.08% | 1.8 | 32000 | R-410A
214331346 | 3.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,A,DG50960 | WUV070T4BA | 46000 | 17 | 10 | 8.5 | 48000 | 34600 | 72.08% | 1.8 | 32000 | R-410A
214392460 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R921V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392577 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R962V0403A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392416 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R802V1004A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
216794582 | 3.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2D120D5PSC+LRP | 40500 | 20 | 11.7 | 9.5 | 46000 | 41500 | 90.22% | 2.69 | 49500 | R-454B
216794584 | 3.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2D120D5PSC+LRP | 40500 | 20 | 11.7 | 9 | 45500 | 41500 | 91.21% | 2.63 | 49500 | R-454B
214392434 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R802V1004A17UHS | 21000 | 18.9 | 9.8 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392439 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R921V0403A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392450 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R921V0403A17M4S | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392459 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R921V0603A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392491 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R951V0403A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
216797094 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2C100M5PDB | 30400 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.87 | 37600 | R-454B
216797126 | 2.55 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2C100U5PSC+LRP | 30600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.88 | 37400 | R-454B
214392578 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R962V0403A17M4S | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392128 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R801V0503A14DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392146 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R801V0503A14UH | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392178 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R801V0504A17UHS | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392263 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R801V1004A17UH | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
211178371 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | G*VC960403BNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
214392295 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R802V0503A14UHN | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
211388702 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DXXN1+TXV | TM9E080C16MP12 | 34000 | 18 | 10 | 8.1 | 33600 | 23800 | 70.83% | 2.08 | 25200 | R-410A
215933640 | 2.78 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0601714B* | 33400 | 19 | 10.5 | 9 | 34200 | 26200 | 76.61% | 1.96 | 30000 | R-454B
215939613 | 2.7 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0401712B* | 32400 | 19.5 | 11 | 9.5 | 35000 | 26800 | 76.57% | 2 | 30800 | R-454B
216763662 | 2.77 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3 | S8X1A040M3PSC | 33200 | 17.1 | 11.7 | 8.7 | 33600 | 24600 | 73.21% | 2 | 21800 | R-454B
216763710 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 | S9V2C100U5PSC | 34000 | 17.1 | 12 | 9 | 32200 | 23800 | 73.91% | 2.2 | 21200 | R-454B
216763712 | 2.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C009AS3 | S9V2C100U4VSB | 34000 | 17.1 | 12 | 9 | 32200 | 23800 | 73.91% | 2.2 | 21200 | R-454B
216763842 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9V2B060D3VSB | 31400 | 16 | 11.5 | 8.7 | 31600 | 23600 | 74.68% | 2.1 | 20800 | R-454B
216763879 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 | S9V2B040U3PSC | 33000 | 17.1 | 12 | 9 | 32600 | 24000 | 73.62% | 2.1 | 21200 | R-454B
216017399 | 2.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | FE*TT3*37+TXV-BLEED |  | 34000 | 19 | 11.7 | 9 | 29800 | 24800 | 83.22% | 2 | 24800 | R-454B
214392144 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R801V0503A14UH | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392296 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0503A14UHN | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392311 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R802V0503A14UHS | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392328 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0504A17UHN | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392344 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0504A17UHS | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392380 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R802V0754A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392429 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V1004A17UHS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392525 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R951V0603A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392541 | 1.72 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R951V0603A17UHU | 20600 | 17.8 | 9.7 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392584 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R962V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392716 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | U98MV0703A17UPS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392625 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | U802VA050317M | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
216797065 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | *UHMB080CCV3+LRP | 29600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.68 | 37800 | R-454B
215939713 | 2.73 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CTN1002122A* | 32800 | 20 | 11.5 | 9.5 | 34800 | 26600 | 76.44% | 2 | 30600 | R-454B
215939733 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0401712B* | 33400 | 20.5 | 11.7 | 9.5 | 34400 | 26200 | 76.16% | 2.04 | 30200 | R-454B
215940033 | 2.8 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU0401712B* | 33600 | 19.5 | 11.7 | 9 | 34600 | 26600 | 76.88% | 1.92 | 30400 | R-454B
211388859 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TM9E080B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 23400 | 70.06% | 2.02 | 26400 | R-410A
213307183 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM8V100C16MP12 | 31400 | 17.4 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.62 | 25200 | R-410A
213307165 | 2.62 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE(D,N,U)+DM36A34+TDR |  | 31400 | 18.3 | 10.3 | 8.4 | 33000 | 26200 | 79.39% | 2.65 | 24400 | R-410A
214392160 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R801V0504A17UHN | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392210 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R801V0704A17UHU | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392226 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R801V0754A17DZ | 21000 | 18.9 | 9.8 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392544 | 1.68 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R951V0603A17UHU | 20200 | 17.7 | 9 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392562 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R951V0703A17M4S | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392712 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | U98MV0703A17UPS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392279 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R802V0503A14DZ | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392312 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0503A14UHS | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
215375095 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R921V0703A17M4S | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
207455060 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36S9 | EL296UH110XV48C* | 33600 | 22 | 13 | 8.7 | 32800 | 26400 | 80.49% | 1.82 | 29600 | R-410A
213307333 | 2.62 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE(D,N,U)+DM36A36+TDR |  | 31400 | 18.3 | 10.3 | 8.4 | 33000 | 26200 | 79.39% | 2.65 | 24400 | R-410A
212479906 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 58SP*A045V17**16 | 23400 | 17 | 10 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
214392360 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0754A17DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392363 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V0754A17DZ | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392411 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V1004A17UHN | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392412 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R802V1004A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392413 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V1004A17UHN | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
213821387 | 2.45 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)42B34+TDR | *80MS(N,L)0902116A* | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213821470 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36C34+TDR | *92MSN0802120A* | 29000 | 15.4 | 8.8 | 8.5 | 33400 | 23800 | 71.26% | 2.79 | 23200 | R-410A
213781018 | 2.63 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *95CSU0601716B* | 31600 | 16.5 | 10.5 | 8.1 | 33000 | 24600 | 74.55% | 1.86 | 31400 | R-410A
213781288 | 2.68 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X48L21A*+WALLCON | *80CTL0701716B* | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.96 | 31400 | R-410A
213781488 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X60L24A*+WALLCON | *80CTL1352422B* | 32800 | 17.5 | 11.5 | 8.1 | 31800 | 24600 | 77.36% | 1.98 | 30800 | R-410A
213781538 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X61L21A*+WALLCON | *80CTL0451712B* | 33000 | 17 | 11 | 8.1 | 32400 | 25200 | 77.78% | 1.94 | 31600 | R-410A
216797104 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B060D3VSB+LRP | 30200 | 18 | 9.8 | 8.5 | 33800 | 33800 | 100% | 2.76 | 38500 | R-454B
216797106 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B060U3VSB+LRP | 30400 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.69 | 38000 | R-454B
216797149 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S8V2C100M5PCB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.83 | 51000 | R-454B
213781638 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X61L21A*+WALLCON | *96CTN0801714B* | 33000 | 17 | 11 | 8.1 | 32000 | 25000 | 78.12% | 1.96 | 31400 | R-410A
215931547 | 4.67 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V60*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0902120B* | 56000 | 18.5 | 11.5 | 8.5 | 60500 | 45500 | 75.21% | 2.06 | 47000 | R-454B
214392427 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V1004A17UHS | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392445 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R921V0403A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392480 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R921V0703A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392512 | 1.68 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R951V0403A17UHU | 20200 | 17.7 | 9 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
216764230 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S9V2B060U3VSB | 32200 | 17 | 11.7 | 8.7 | 32200 | 24000 | 74.53% | 2.1 | 21200 | R-454B
216755383 | 2.58 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH30AAK | EA*5X37M21A* | *80VSL1102122B* | 31000 | 15.2 | 9.5 | 9 | 34200 | 30200 | 88.3% | 1.8 | 21200 | R-454B
216794380 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2C080M5PDB | 32600 | 20 | 12 | 9.5 | 31800 | 31600 | 99.37% | 2.91 | 39000 | R-454B
216797112 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B080D4VSB+LRP | 30400 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.72 | 38500 | R-454B
216797125 | 2.5 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2C100U5PSC+LRP | 30000 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.82 | 37000 | R-454B
215375080 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0754A17UHN | 21600 | 17 | 10 | 8.1 | 22600 | 18900 | 83.63% | 2.1 | 16800 | R-410A
213160924 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | V,G36H***P449+AEFE3A* |  | 17800 | 17 | 11 | 9 | 17100 | 19400 | 113.5% | 2.4 | 11500 | R-410A
213821466 | 2.35 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30B34+TDR | *92MSN0802120A* | 28200 | 15.2 | 8.7 | 8.3 | 33200 | 24000 | 72.29% | 2.76 | 23200 | R-410A
216687211 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF96TV508521M4 | 45500 | 19 | 11.7 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
216687163 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF95SV307017M4 | 22800 | 20 | 12 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
216764260 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8X1B060M4PSC | 32600 | 17.1 | 11.7 | 8.2 | 33400 | 24400 | 73.05% | 1.9 | 21600 | R-454B
216764277 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD06AS3 | S9V2B080D4VSB | 33000 | 17.1 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2 | 21400 | R-454B
214392528 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R951V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
213738337 | 2.43 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | PL36H175P159 | *80MS(N,L)0701412A* | 29200 | 15.2 | 8.5 | 8.1 | 32400 | 26800 | 82.72% | 1.82 | 22400 | R-410A
216764363 | 2.73 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | L8V1A040U3VSB | 32800 | 17.1 | 11.7 | 8.7 | 32600 | 24200 | 74.23% | 2.1 | 21400 | R-454B
216794416 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B060U4VSB+LRP | 32200 | 19.2 | 12 | 9 | 32600 | 31000 | 95.09% | 2.77 | 37800 | R-454B
216794448 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2C100U5VSB+LRP | 32200 | 20 | 12 | 9 | 32600 | 30800 | 94.48% | 2.77 | 37600 | R-454B
216794505 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S8V2C080M5PDB | 42000 | 20 | 11.7 | 9.5 | 47000 | 42500 | 90.43% | 2.77 | 50500 | R-454B
216794532 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2B060U4PSC+LRP | 41500 | 19.2 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.76 | 51000 | R-454B
212480217 | 2.48 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | PL36H210P299 | 58SU*A080E21**20 | 29800 | 15.2 | 9 | 8.1 | 32200 | 26800 | 83.23% | 1.78 | 22200 | R-410A
211391026 | 2.83 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DXXN1+TXV | TPLC060A12MP13 | 34000 | 17.5 | 9.5 | 8.1 | 34000 | 24200 | 71.18% | 2.06 | 25600 | R-410A
211391160 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB30CXXN1+TXV | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 23400 | 70.06% | 2.02 | 26000 | R-410A
211391428 | 2.8 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DBCN1 | TM8E100C16MP11 | 33600 | 17.5 | 10 | 8.1 | 33000 | 23200 | 70.3% | 2.04 | 24800 | R-410A
211391548 | 2.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TM8E100C16MP11 | 33000 | 18 | 10 | 8.5 | 33000 | 23200 | 70.3% | 2.04 | 26000 | R-410A
211391762 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DBCN1 | TM8E100B12MP11 | 34000 | 18 | 10 | 8.1 | 33800 | 23800 | 70.41% | 2.06 | 25400 | R-410A
213885800 | 1.82 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | AE(D,N,U)+CM36A34+TDR |  | 21800 | 17.1 | 11.2 | 8.1 | 20400 | 24800 | 121.6% | 2.72 | 20000 | R-410A
216797127 | 3.75 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | *DHMC100CCV4+LRP | 45000 | 17.5 | 10 | 8.1 | 45500 | 45500 | 100% | 2.58 | 50500 | R-454B
214092080 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TMLE080B12MP11 | 31600 | 17.9 | 9.3 | 8.1 | 34000 | 28000 | 82.35% | 2.62 | 25800 | R-410A
214092731 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
214328313 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG33936 | WPV060T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
216797128 | 3.75 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | *DHMC100CCV4+LRP | 45000 | 18 | 10 | 8.1 | 45000 | 45000 | 100% | 2.54 | 51000 | R-454B
216797143 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S8V2B080M4PDB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.7 | 52000 | R-454B
211391847 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DBCN1 | TM8E100B12MP11 | 34000 | 18 | 10 | 8.1 | 33800 | 23800 | 70.41% | 2.06 | 25400 | R-410A
211392165 | 2.78 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DBCN1 | TM8E080B12MP11 | 33400 | 17.5 | 9.5 | 8.1 | 33200 | 23400 | 70.48% | 2.02 | 25000 | R-410A
216766845 | 1.8 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCA001AS3 | S8V2A040M3PDB | 21600 | 15.2 | 11.2 | 10 | 21200 | 16100 | 75.94% | 1.89 | 22000 | R-454B
213612032 | 1.83 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R962V0403A17M4S | 22000 | 15.4 | 11.8 | 8.1 | 22800 | 16400 | 71.93% | 2.83 | 15900 | R-410A
211392367 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TMLE080B12MP11 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 23800 | 70% | 2.02 | 26800 | R-410A
211392533 | 2.77 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DXXN1+TXV | TMLE060A12MP11 | 33200 | 17 | 9.5 | 8.1 | 33200 | 23400 | 70.48% | 2 | 25000 | R-410A
211390120 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC30CXXN1+TXV | TPLC080C16MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 22800 | 70.37% | 2 | 25600 | R-410A
211390172 | 2.83 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DXXN1+TXV | TM8V080C16MP12 | 34000 | 17.5 | 10 | 8.5 | 33800 | 23800 | 70.41% | 2.08 | 25400 | R-410A
211390981 | 2.67 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB30CXXN1+TXV | TPLC060A12MP13 | 32000 | 17 | 9.5 | 8.1 | 32800 | 23000 | 70.12% | 1.98 | 25600 | R-410A
214091949 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TL9E060B12UH11 | 31400 | 17.9 | 9.3 | 8.1 | 34000 | 27800 | 81.76% | 2.58 | 25600 | R-410A
214091951 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL9E060B12UH11 | 32600 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.6 | 25600 | R-410A
215375330 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R962V0705A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
214328312 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG34936 | WPV050T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
211178360 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VS800805CUA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
211178361 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VC800804C*A* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
216797081 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2B060M4PDB | 29800 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.63 | 37600 | R-454B
214328324 | 3.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,A,DG49960 | WPV080T4BA | 46000 | 17 | 10 | 8.5 | 48000 | 34600 | 72.08% | 1.8 | 32000 | R-410A
216794248 | 1.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | L8V1B080U4VSB+LRP | 19800 | 21 | 11.7 | 10 | 22400 | 21800 | 97.32% | 2.94 | 26800 | R-454B
216794589 | 3.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2D120D5VSB+LRP | 40500 | 20 | 11.7 | 9.5 | 46000 | 41500 | 90.22% | 2.69 | 49500 | R-454B
216794600 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2D120U5PSC+LRP | 41500 | 20.2 | 11.7 | 9 | 45500 | 41500 | 91.21% | 2.75 | 49500 | R-454B
216797130 | 3.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | *UHMC100CCV4+LRP | 45000 | 18 | 10 | 8.5 | 45500 | 45500 | 100% | 2.78 | 51500 | R-454B
216797157 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S9V2B060U4PSC+LRP | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.7 | 52000 | R-454B
213612052 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R802V0503A14UH | 32800 | 15.4 | 10 | 8.1 | 33800 | 26800 | 79.29% | 2.8 | 25000 | R-410A
213885801 | 1.85 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | AE(D,N,U)+CM36B34+TDR |  | 22200 | 17.3 | 11.4 | 8.4 | 20600 | 25000 | 121.4% | 2.8 | 20200 | R-410A
214092712 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
215941653 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN1002122A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.9 | 43500 | R-454B
214328319 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG33936 | WUV060T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
216764379 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB006AS3 | S9V2B040D3PSC | 31400 | 16 | 11.5 | 8.7 | 31400 | 23600 | 75.16% | 2.1 | 20800 | R-454B
214331210 | 3.08 | No | No | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | *G34936 | WPV070T3AA | 37000 | 16 | 9.5 | 8.25 | 34800 | 32400 | 93.1% | 1.76 | 24600 | R-410A
216733946 | 1.85 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *80CTL0451712B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
216734229 | 1.85 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X30M17A* | *96CTN0801714B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.85 | 17600 | R-454B
215936927 | 3 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *80CTL0902120B* | 36000 | 22.5 | 12.5 | 8.5 | 37600 | 28200 | 75% | 2.06 | 32200 | R-454B
215931997 | 2.57 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X30M14A*+WALLCON | *96CTN0401410B* | 30800 | 17 | 10 | 9 | 34400 | 26600 | 77.33% | 1.9 | 30400 | R-454B
214392647 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | U802VA075317Z | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392594 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R962V0603A17M4S | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392680 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | U97MV0703A17DHS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214391628 | 1.39 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ18AJ2N | CP31A34+TDR | R951V0603A17UHU | 16700 | 15.5 | 11.8 | 8.3 | 17200 | 12500 | 72.67% | 2.75 | 12100 | R-410A
214328321 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG33936 | WUV070T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
214092078 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
214091974 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.3 | 32800 | 29000 | 88.41% | 2.71 | 26000 | R-410A
214092026 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.66 | 26000 | R-410A
214092083 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 28600 | 86.67% | 2.65 | 25800 | R-410A
214092103 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TMLV120C20MP12 | 32000 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214092108 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.69 | 26600 | R-410A
214092135 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
216794378 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2C080M5PCB | 32600 | 20 | 12 | 9.5 | 31800 | 31600 | 99.37% | 2.91 | 39000 | R-454B
216794259 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S8V2B060M4PCB | 19500 | 21 | 11.2 | 10 | 22000 | 21800 | 99.09% | 2.93 | 27000 | R-454B
216794296 | 1.57 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B040U3VSB+LRP | 18800 | 19.6 | 11 | 9 | 22200 | 21000 | 94.59% | 2.56 | 25600 | R-454B
216687172 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF98MV510021UP | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
216687222 | 4.5 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF80TV510021UH | 54000 | 17 | 10 | 10 | 54000 | 48500 | 89.81% | 2 | 51000 | R-454B
211259764 | 1.52 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96VTN0401712A* | 18200 | 15.5 | 10.5 | 8.5 | 18300 | 17600 | 96.17% | 2.12 | 12300 | R-410A
211259998 | 1.51 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *80ES(N,L)0701412A* | 18100 | 16.5 | 11 | 8.5 | 18000 | 17700 | 98.33% | 2.14 | 12200 | R-410A
213612042 | 2.28 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R802V0754A17UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20800 | 73.24% | 2.62 | 20000 | R-410A
211260014 | 1.59 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *80ESU0601716A | 19100 | 16.5 | 11 | 9 | 19000 | 17400 | 91.58% | 2.14 | 12700 | R-410A
211260057 | 1.55 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | OMV112K14A | 18600 | 15.5 | 10.5 | 8.5 | 18700 | 17500 | 93.58% | 2.12 | 12600 | R-410A
216453750 | 2.78 | No | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)37A44+TDR | R962V0403A17M4 | 33400 | 17 | 9.8 | 8.5 | 34200 | 24400 | 71.35% | 2.76 | 23800 | R-410A
211260175 | 1.49 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L14A* | *95ESN0261410A* | 17900 | 15.5 | 10.5 | 8.5 | 19000 | 18900 | 99.47% | 2.26 | 12600 | R-410A
211260275 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *96VSN0401410A* | 17400 | 16 | 10.5 | 8.5 | 18300 | 19200 | 104.9% | 2.3 | 12300 | R-410A
211261061 | 1.53 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *92ESN0401712A* | 18400 | 15.5 | 10.5 | 8.5 | 18300 | 17500 | 95.63% | 2.12 | 12400 | R-410A
211261827 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *80VTL0701716A* | 17500 | 16.5 | 10.5 | 8.5 | 17900 | 18600 | 103.9% | 2.24 | 12200 | R-410A
211260625 | 1.47 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *80ES(N,L)0701412A* | 17600 | 16 | 10.5 | 8.5 | 18400 | 19100 | 103.8% | 2.3 | 12400 | R-410A
216794402 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B040U3VSB+LRP | 32000 | 19.2 | 11.7 | 9 | 32800 | 31000 | 94.51% | 2.77 | 37800 | R-454B
216797059 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | *DHMB080CCV3+LRP | 29600 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.68 | 38500 | R-454B
216797075 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2A040M3PCB | 29600 | 18 | 9.8 | 8.5 | 33800 | 33800 | 100% | 2.68 | 38000 | R-454B
216797109 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B080D4PSC+LRP | 29800 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.68 | 38500 | R-454B
214091945 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL8E080C16UH11 | 32600 | 17.5 | 10 | 8.1 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
214091947 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TL8E100C20UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.68 | 25400 | R-410A
214091978 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.2 | 33000 | 29000 | 87.88% | 2.72 | 26000 | R-410A
214092048 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
211756130 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | YPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
213286671 | 1.43 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CP1801A+TXV+TD |  | 17100 | 15.2 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
216453754 | 2.78 | No | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)37A44+TDR | R962V0703A17M4 | 33400 | 17 | 9.8 | 8.5 | 34200 | 24400 | 71.35% | 2.76 | 23800 | R-410A
213739581 | 1.46 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FG80936 | *96MSN0401410A* | 17500 | 16 | 10.5 | 8.5 | 16700 | 18500 | 110.8% | 2.26 | 11300 | R-410A
213612036 | 2.28 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R802V0503A14DZ | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 21000 | 73.94% | 2.63 | 20200 | R-410A
212986329 | 1.47 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *96MSN0401410A* | 17600 | 16 | 10.5 | 8.5 | 18300 | 18800 | 102.7% | 2.26 | 12300 | R-410A
212989271 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *95MSU0601716A* | 17800 | 16.5 | 10.5 | 8.1 | 17800 | 17900 | 100.6% | 2.16 | 12100 | R-410A
216797062 | 2.55 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | *DHMC100CCV4+LRP | 30600 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.72 | 38500 | R-454B
216797089 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2C080M5PDB | 29600 | 18 | 9.8 | 8.5 | 32600 | 32600 | 100% | 2.85 | 37600 | R-454B
215931697 | 4.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V60*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0902120B* | 57000 | 19 | 11.5 | 8.5 | 60500 | 46500 | 76.86% | 2.04 | 47500 | R-454B
215931847 | 4.67 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V60*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU0802120B* | 56000 | 17.5 | 11 | 8.1 | 61000 | 46000 | 75.41% | 1.95 | 47500 | R-454B
213781688 | 2.77 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X61L24A*+WALLCON | *97CMN1002122B* | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31000 | R-410A
213782088 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X48AAL+WALLCON | *80CTL0902120B* | 32600 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31400 | R-410A
215932297 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CMN0602120B* | 32600 | 19 | 11 | 9.5 | 35200 | 27200 | 77.27% | 2 | 31000 | R-454B
216764428 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*C009AS3 | S9V2C100U5PSC | 43000 | 16.5 | 11.7 | 9 | 44000 | 32400 | 73.64% | 2.1 | 29400 | R-454B
213781985 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 59MN7C100C21**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
214328315 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG33936 | WPV070T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
214328317 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG33936 | WUV050T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
207455126 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*23/37Z9 | SL280UH080NV60C* | 34000 | 21 | 13.5 | 8.8 | 33800 | 27000 | 79.88% | 1.82 | 31800 | R-410A
213885820 | 3.5 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH848GKA2* | AE(D,N,U)+CM48A34+TDR |  | 42000 | 17.8 | 10.2 | 8.1 | 45500 | 39500 | 86.81% | 2.74 | 35600 | R-410A
216764445 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | L9X1C100U5VSA | 43500 | 16.5 | 11.2 | 8.7 | 45000 | 33000 | 73.33% | 2.1 | 30200 | R-454B
216764446 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | S9V2D120U5VSB | 43500 | 17.1 | 12 | 9 | 43500 | 32000 | 73.56% | 2.2 | 29000 | R-454B
216764447 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5PX*D010AS3 | S9V2D120U5PSC | 43500 | 17.1 | 12 | 9 | 43500 | 32000 | 73.56% | 2.2 | 29000 | R-454B
216764496 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | S8X1D120M5PSC | 51500 | 16.5 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
216764514 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*DD10AS3 | S8X1D120M5PSC | 51000 | 16 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.1 | 34000 | R-454B
214092183 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y82E100C20LMPS1 | 32600 | 18.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092203 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | YP9C120D20MP13 | 32200 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
214092210 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | YPLC080C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
211206977 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | LPLC120C20MP13 | 43500 | 19 | 12 | 9 | 44500 | 36200 | 81.35% | 2.14 | 41500 | R-410A
211207004 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | LPLC080C16MP13 | 43500 | 19 | 12 | 9 | 44500 | 36200 | 81.35% | 2.14 | 41500 | R-410A
214092217 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | YPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
216797129 | 3.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | *UHMC100CCV4+LRP | 45000 | 18 | 10 | 8.5 | 45500 | 45500 | 100% | 2.82 | 51500 | R-454B
209880043 | 3.71 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF96TV508521M4S*A | 44500 | 18 | 11.7 | 8.5 | 43000 | 45000 | 104.7% | 2 | 44500 | R-410A
216797167 | 3.75 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S9V2C100D5PSC+LRP | 45000 | 17.5 | 10 | 8.1 | 45000 | 45000 | 100% | 2.61 | 51000 | R-454B
216487853 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | H,PG53*36+TXV | 986TD66100C21*** | 34400 | 18 | 10.5 | 9 | 32600 | 24400 | 74.85% | 1.9 | 28800 | R-454B
216794496 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S8V2B080M4PDB | 42000 | 19.2 | 11.7 | 9 | 47000 | 42500 | 90.43% | 2.79 | 50500 | R-454B
215289570 | 1.38 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG32924 | *92MSN0401712A* | 16500 | 15.2 | 10 | 8.5 | 16500 | 18400 | 111.5% | 2.24 | 11200 | R-410A
216797158 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2B060U4PSC+LRP | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
213369415 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG7J936 | 59TP6C100V21**20 | 23000 | 17 | 10 | 8.5 | 24600 | 24200 | 98.37% | 2.04 | 18100 | R-410A
213369434 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG7J936 | 59TP6C100V21**20 | 35200 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
216797051 | 1.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | D(A,C,E)30A4J+TDR | *UHMB080CCV3+LRP | 20600 | 18 | 11 | 8.5 | 24200 | 24200 | 100% | 3.02 | 28600 | R-454B
215912479 | 3.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60B3K+TDR | Y81E130D20SMPS1 | 42000 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215912379 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E080B12MP12 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18700 | 83.48% | 2 | 18600 | R-454B
215912426 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Y91E060B12SMPS1 | 21600 | 17 | 11.7 | 8.1 | 22400 | 18600 | 83.04% | 2 | 18500 | R-454B
213927888 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B3G+TXV+TDR | TM9Y080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
215912443 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y120C20MP11 | 31000 | 18 | 11.7 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
215289620 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG33936 | *92MSN0601412A* | 17400 | 16 | 11 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215289621 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG33936 | *92MSN0601412A* | 17400 | 16 | 11 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215289639 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG8J936 | *92MSN0601412A* | 17500 | 16 | 11 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215289653 | 1.41 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG31930 | *92MSN0601714A* | 16900 | 16 | 10 | 8.5 | 16900 | 19000 | 112.4% | 2.34 | 11400 | R-410A
215289654 | 1.41 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE31924 | *92MSN0601714A* | 16900 | 16 | 10 | 8.5 | 16900 | 19000 | 112.4% | 2.34 | 11400 | R-410A
215289655 | 1.41 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE31930 | *92MSN0601714A* | 16900 | 16 | 10 | 8.5 | 16900 | 19000 | 112.4% | 2.34 | 11400 | R-410A
215289672 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE34936 | *92MSN0601714A* | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215289687 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG9J936 | *92MSN0601714A* | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
213773748 | 2 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L21A*+WALLCON | *97CMN0601714B* | 24000 | 16.5 | 10.5 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
213779148 | 2.63 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L21A*+WALLCON | *96CTN0601714B* | 31600 | 16.5 | 10.5 | 8.1 | 33200 | 24600 | 74.1% | 1.86 | 31400 | R-410A
213779198 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L24A*+WALLCON | *80CTL1352422B* | 31800 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.88 | 31000 | R-410A
212603375 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36F4 |  | 33000 | 17 | 10 | 8.1 | 31800 | 27000 | 84.91% | 2.73 | 24600 | R-410A
214777869 | 1.5 | Yes | Yes | DAY & NIGHT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DLCURAH18ABK | PL36H***P039+TD |  | 18000 | 16 | 11.7 | 9.05 | 17200 | 14600 | 84.88% | 2.1 | 13600 | R-410A
211206873 | 2.75 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B3621 | XAMC36DE2N1+CC | TP9C080C16MP13 | 33000 | 18 | 12 | 8.5 | 34200 | 29200 | 85.38% | 1.96 | 34400 | R-410A
215375097 | 1.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R951V0403A17UHU | 21400 | 17 | 10 | 8.1 | 22400 | 19100 | 85.27% | 2 | 17100 | R-410A
216494162 | 3.58 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)4824G1K*+TXV | 987MC60060C21*** | 43000 | 20 | 10 | 9.5 | 46500 | 36800 | 79.14% | 1.88 | 39000 | R-454B
214777870 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | DLCURAH24ABK | PL36H***P039+TD |  | 23800 | 16 | 10.5 | 9 | 23200 | 19600 | 84.48% | 1.86 | 20000 | R-410A
211178352 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | G*VC800604B*A* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
216733076 | 1.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X24M17A* | *96VTN0601716B* | 22000 | 16 | 10.5 | 8.5 | 21000 | 19100 | 90.95% | 1.96 | 18000 | R-454B
216681547 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*3612AL* | 59TP7A080V21**20 | 24200 | 16.5 | 10 | 9 | 25600 | 22000 | 85.94% | 1.75 | 18800 | R-410A
214595165 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36F4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212480140 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 59TP6B040V14**10 | 22800 | 16 | 9.5 | 8.5 | 24000 | 23400 | 97.5% | 1.96 | 17900 | R-410A
212480149 | 2.07 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P299 | 59TP6B080V17**16 | 24800 | 17 | 10.5 | 8.5 | 24000 | 20600 | 85.83% | 1.76 | 17700 | R-410A
216797139 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S8V2B060M4PDB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.69 | 52000 | R-454B
216797146 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S8V2C080M5PCB | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.81 | 52500 | R-454B
216797164 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2C080U5PSC+LRP | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.79 | 51500 | R-454B
216764924 | 1.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5TXCB004AS3 | S8X2B080M4PSC | 22600 | 17.5 | 12 | 8.7 | 21600 | 17000 | 78.7% | 1.9 | 15100 | R-454B
213612034 | 1.83 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R962V0703A17M4S | 22000 | 15.4 | 11.8 | 8.1 | 22800 | 16200 | 71.05% | 2.81 | 15800 | R-410A
216763943 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*CD09AS3 | S9V2C100D5PSC | 43000 | 17.1 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.1 | 29200 | R-454B
216764027 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | L8V1C100U5VSB | 43500 | 17.1 | 12.5 | 9 | 44000 | 32000 | 72.73% | 2.2 | 29200 | R-454B
216681785 | 2.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L24A* | *97VTN1002120A* | 35400 | 16 | 10 | 8.5 | 38500 | 34600 | 89.87% | 1.76 | 29400 | R-410A
216683208 | 2.98 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EHD4X42AAL | *97VTN1202422A* | 35800 | 15.5 | 9.8 | 8.5 | 38500 | 34400 | 89.35% | 1.82 | 29200 | R-410A
213885802 | 1.82 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | AE(D,N,U)+CM36A34+TDR |  | 21800 | 17.1 | 11.2 | 8.1 | 20400 | 24800 | 121.6% | 2.72 | 20000 | R-410A
214092145 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.2 | 32800 | 29400 | 89.63% | 2.71 | 26200 | R-410A
214092148 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E080C16LMPS1 | 32400 | 18 | 10 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092149 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y81E080C16LMPS1 | 32600 | 18 | 10 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092165 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y81E100C20LMPS1 | 32600 | 17.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214395062 | 1.46 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *96MSN0601716A* | 17500 | 15.5 | 10.5 | 8.5 | 18500 | 19000 | 102.7% | 2.28 | 12400 | R-410A
213612038 | 2.28 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R802V0503A14UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20800 | 73.24% | 2.63 | 20000 | R-410A
213612040 | 2.28 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R802V0754A17DZ | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 21000 | 73.94% | 2.62 | 20200 | R-410A
215413729 | 1.4 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | SM3919 |  | 16800 | 17 | 11 | 8.75 | 17000 | 19400 | 114.1% | 2.34 | 11500 | R-410A
216794429 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2C080U5PSC+LRP | 32000 | 19.9 | 12 | 9 | 32200 | 30200 | 93.79% | 2.77 | 36600 | R-454B
216797083 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2B080M4PCB | 29600 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.63 | 37600 | R-454B
212348392 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | LEW30B4 |  | 23000 | 16 | 10 | 8.5 | 26000 | 23400 | 90% | 2.77 | 19000 | R-410A
212348393 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | LEW30C4 |  | 23000 | 16 | 10 | 8.8 | 26000 | 23400 | 90% | 2.77 | 19000 | R-410A
211260759 | 1.52 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *95ESU0401712A* | 18200 | 16.5 | 11 | 8.5 | 18000 | 17600 | 97.78% | 2.12 | 12200 | R-410A
211467457 | 3.54 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YH2F48TB21 | D(A,C,E)48B44+TDR | TM8V080C16MP12 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
216599679 | 1.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | 5PX*B006AS3 | S9V2B080U4PSC+LRP | 22000 | 18.1 | 11.5 | 8.5 | 23000 | 18700 | 81.3% | 2.2 | 22800 | R-454B
216763893 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | L8V1C100U5VSB | 33800 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.2 | 21400 | R-454B
216764545 | 1.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*B004AS3 | S8X2A040M3PTC | 23000 | 17.1 | 12.5 | 9 | 21800 | 17200 | 78.9% | 2 | 15300 | R-454B
212479865 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 58S(B,C)*A070E17**16 | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212479949 | 2.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P149 | 58SU*A060E17**16 | 25000 | 17 | 10.5 | 8.5 | 25000 | 21400 | 85.6% | 1.82 | 18300 | R-410A
213781105 | 2.65 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4224AL*+UI | 58TN*B135C24**22 | 31800 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.88 | 31000 | R-410A
213781135 | 2.65 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4224AL*+UI | 59TN6C100C21**22 | 31800 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.88 | 31200 | R-410A
213780655 | 2.62 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3617AL*+UI | 58TN*B070C17**16 | 31400 | 16.5 | 10.5 | 8.1 | 33400 | 24400 | 73.05% | 1.82 | 31200 | R-410A
212479850 | 2.03 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 58S(B,C)*A045E14**12 | 24400 | 16 | 10.5 | 8.1 | 25000 | 22000 | 88% | 1.84 | 18300 | R-410A
212479891 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 58SP*A045V14**12 | 24000 | 16 | 10 | 8.5 | 24800 | 22600 | 91.13% | 1.9 | 18200 | R-410A
212479893 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P299 | 58SP*A045V17**16 | 23400 | 17 | 10 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
213785015 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**2417AL*+UI | 58TN*B090C17**16 | 23000 | 19.5 | 12.5 | 10 | 27000 | 20200 | 74.81% | 2.3 | 25200 | R-410A
213785063 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3017AL*+UI | 59TN6C060C17**14 | 23000 | 19.5 | 12.5 | 10 | 26800 | 20000 | 74.63% | 2.34 | 25200 | R-410A
213785065 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3017AL*+UI | 59TN6C080C17**14 | 23200 | 20 | 12.5 | 10 | 26800 | 20000 | 74.63% | 2.36 | 25000 | R-410A
213785079 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3617AL*+UI | 59TN6C040C14**10 | 22800 | 18 | 11.5 | 10 | 27000 | 20400 | 75.56% | 2.3 | 25400 | R-410A
212348395 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | LEW30E4 |  | 23600 | 16 | 10 | 9 | 26200 | 23400 | 89.31% | 2.93 | 19200 | R-410A
215289704 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *92MSN0801716A* | 17400 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
210693381 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VS800604BUA* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693384 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VS800805CUA* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693331 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC960803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216687194 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF97MV508521DH | 34200 | 21 | 12 | 10 | 34200 | 29400 | 85.96% | 2 | 30000 | R-454B
216764563 | 1.9 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5TXCB004AS3 | S8X1B040M2PTC | 22800 | 17.1 | 12.5 | 8.7 | 21600 | 17100 | 79.17% | 1.9 | 15200 | R-454B
213779348 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X43L21A*+WALLCON | *96CTN0801714B* | 32800 | 17 | 11 | 8.5 | 32800 | 25200 | 76.83% | 1.96 | 31800 | R-410A
213779498 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L24A*+WALLCON | *80CTL1102120B* | 32400 | 17.5 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213782138 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X48AAL+WALLCON | *97CMN0801714B* | 32400 | 16.5 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31800 | R-410A
213782288 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X60AAL+WALLCON | *97CMN0601714B* | 32800 | 16 | 11 | 8.1 | 32400 | 25200 | 77.78% | 1.96 | 31600 | R-410A
213780268 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X48AAL+WALLCON | *96CTN0801714B* | 32600 | 16.5 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.94 | 31600 | R-410A
214331212 | 3.08 | No | No | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | *G34936 | WUV070T3AA | 37000 | 16 | 9.5 | 8.25 | 34800 | 32400 | 93.1% | 1.76 | 24600 | R-410A
212348394 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | LEW30D4 |  | 23600 | 16 | 10 | 9 | 26200 | 23400 | 89.31% | 2.93 | 19200 | R-410A
212480075 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 59SC5B080E17**16 | 24800 | 15.2 | 10 | 8.5 | 25200 | 21600 | 85.71% | 1.8 | 18400 | R-410A
212480084 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59SP6A040V17**12 | 23200 | 16 | 10 | 8.5 | 24200 | 23200 | 95.87% | 1.94 | 18000 | R-410A
212480093 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59SP6A080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
216755684 | 2.6 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ30AA3 | CAA**4321AM* | 58SU*B080M21**20 | 31200 | 15.5 | 9.5 | 9 | 34200 | 30000 | 87.72% | 1.8 | 21200 | R-454B
213612046 | 2.28 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R962V0403A17M4S | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20800 | 73.24% | 2.63 | 20000 | R-410A
211392649 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAUB36DXXN1+TXV | TM8E060A12MP11 | 34000 | 18 | 10 | 8.1 | 33800 | 23800 | 70.41% | 2.06 | 25400 | R-410A
211392815 | 2.67 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB30CXXN1+TXV | TMLE040A12MP11 | 32000 | 17.5 | 9.5 | 8.1 | 31800 | 23000 | 72.33% | 1.98 | 25600 | R-410A
212480001 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149 | 58TP*A090V17**16 | 23800 | 17 | 10.5 | 8.1 | 24400 | 23000 | 94.26% | 1.94 | 18000 | R-410A
212480099 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P149 | 59SP6A080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
213782035 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 59TN6C120C24**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
212498517 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CE2505C+TXV |  | 23600 | 17 | 10 | 9 | 25600 | 25200 | 98.44% | 2.14 | 18600 | R-410A
215289720 | 1.48 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG36936 | *92MSN0801716A* | 17700 | 16 | 11 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215289753 | 1.41 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE32936 | *96MSN0261410A* | 16900 | 20 | 10 | 8.1 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215289786 | 1.4 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG31924 | *96MSN0401410A* | 16800 | 16 | 10 | 8.5 | 16900 | 19100 | 113% | 2.34 | 11400 | R-410A
215289787 | 1.4 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG31930 | *96MSN0401410A* | 16800 | 16 | 10 | 8.5 | 16900 | 19100 | 113% | 2.34 | 11400 | R-410A
215289803 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE33936 | *96MSN0401410A* | 17400 | 16 | 10.5 | 8.5 | 16900 | 19100 | 113% | 2.34 | 11400 | R-410A
215289821 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE8J936 | *96MSN0401410A* | 17400 | 16 | 10.5 | 8.5 | 16900 | 19100 | 113% | 2.34 | 11400 | R-410A
215289837 | 1.38 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE31930 | *96MSN0401712A* | 16600 | 15.2 | 9.5 | 8.5 | 16700 | 19000 | 113.8% | 2.32 | 11300 | R-410A
215289889 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE32936 | *96MSN0601412A* | 17400 | 16 | 10.5 | 8.5 | 17000 | 19400 | 114.1% | 2.38 | 11500 | R-410A
211393518 | 2.67 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB30CXXN1+TXV | TL8E060A12UH11 | 32000 | 17.5 | 9.5 | 8.1 | 32600 | 23000 | 70.55% | 1.98 | 25800 | R-410A
211390008 | 2.83 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DBCN1 | TM8V080C16MP12 | 34000 | 17 | 9.5 | 8.1 | 34000 | 24600 | 72.35% | 2.08 | 25600 | R-410A
213612030 | 1.83 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R802V0503A14UH | 22000 | 15.4 | 11.8 | 8.1 | 22800 | 16200 | 71.05% | 2.81 | 15800 | R-410A
213612031 | 1.83 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R802V0754A17UH | 22000 | 15.5 | 11.8 | 8.2 | 22800 | 16200 | 71.05% | 2.83 | 15800 | R-410A
215289923 | 1.41 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG31930 | *96MSN0601716A* | 16900 | 15.2 | 10 | 8.5 | 16900 | 18600 | 110.1% | 2.28 | 11400 | R-410A
215289937 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE33936 | *96MSN0601716A* | 17100 | 16 | 10.5 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
215289955 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE8J936 | *96MSN0601716A* | 17100 | 16 | 10.5 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
215289970 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE31930 | *96MSN0801716A* | 17200 | 16 | 10 | 8.5 | 17000 | 19000 | 111.8% | 2.32 | 11500 | R-410A
215290003 | 1.47 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG9J936 | *96MSN0801716A* | 17600 | 16 | 11 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11500 | R-410A
215290005 | 1.47 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG80936 | *96MSN0801716A* | 17600 | 16 | 11 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11500 | R-410A
215290021 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE32930 | *96VTN0401410A* | 17100 | 16 | 10 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290039 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE7J936 | *96VTN0401410A* | 17200 | 16 | 10 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
211388874 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DXXN1+TXV | TM9E080B12MP12 | 34000 | 17.5 | 10 | 8.1 | 33800 | 24000 | 71.01% | 2.06 | 25400 | R-410A
211388956 | 2.78 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DBCN1 | TM9E060B12MP12 | 33400 | 17 | 9.5 | 8.1 | 33400 | 23800 | 71.26% | 2 | 25200 | R-410A
211389274 | 2.83 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DXXN1+TXV | TM8Y120C20MP11 | 34000 | 17 | 9.5 | 8.1 | 33800 | 24200 | 71.6% | 2.08 | 25400 | R-410A
211388154 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DBCN1 | TM9V060B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33000 | 23400 | 70.91% | 1.98 | 25000 | R-410A
211388303 | 2.82 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DXXN1+TXV | TM9V060B12MP12 | 33800 | 17 | 9.5 | 8.5 | 33400 | 23800 | 71.26% | 2.04 | 25400 | R-410A
211388338 | 2.82 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DBCN1 | TM9V060B12MP12 | 33800 | 17 | 9.5 | 8.5 | 33400 | 23800 | 71.26% | 2.04 | 25400 | R-410A
211388470 | 2.7 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DBCN1 | TM9V040A10MP12 | 32400 | 16.5 | 9.5 | 8.1 | 32600 | 23000 | 70.55% | 1.96 | 24800 | R-410A
211387935 | 2.8 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DBCN1 | TP9C080B12MP13 | 33600 | 17.5 | 10 | 8.5 | 33400 | 23400 | 70.06% | 2.04 | 25000 | R-410A
214331345 | 3.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,A,DG52960 | WPV080T4BA | 46000 | 17 | 10 | 8.5 | 48000 | 34600 | 72.08% | 1.8 | 32000 | R-410A
216794242 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | L8V1A060U3VSB+LRP | 19500 | 21 | 11.2 | 10 | 22200 | 21800 | 98.2% | 2.93 | 27000 | R-454B
216794362 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S8V2A040M3PCB | 32400 | 20 | 11.7 | 9 | 32400 | 31600 | 97.53% | 2.75 | 39000 | R-454B
216794394 | 2.53 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B040D3PSC+LRP | 30400 | 17.5 | 11 | 9 | 31800 | 30000 | 94.34% | 2.77 | 36600 | R-454B
213781285 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4821AL*+UI | 58TN*B070C17**16 | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.96 | 31400 | R-410A
213781335 | 2.67 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4821AL*+UI | 59MN7C060C17**14 | 32000 | 16.5 | 10.5 | 8.1 | 32800 | 25200 | 76.83% | 1.94 | 31600 | R-410A
213781455 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4824AL*+UI | 59TN6C120C24**22 | 32400 | 17 | 11 | 8.5 | 32400 | 24800 | 76.54% | 1.98 | 31200 | R-410A
213781555 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6121AL*+UI | 58TN*B090C17**16 | 33200 | 17.5 | 11.5 | 8.1 | 32000 | 24800 | 77.5% | 1.98 | 31200 | R-410A
214839588 | 1.88 | No | Yes | GE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS22H24MA4-**A | L(E,G)M36D4 |  | 22600 | 18.5 | 12.2 | 8.5 | 23000 | 16100 | 70% | 2.32 | 14900 | R-410A
215289569 | 1.38 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *92MSN0401712A* | 16500 | 15.2 | 10 | 8.5 | 16500 | 18400 | 111.5% | 2.24 | 11200 | R-410A
215290053 | 1.38 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG31930 | *96VTN0401410B* | 16600 | 16 | 9.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290071 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG34936 | *96VTN0401410B* | 17200 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290087 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE8J936 | *96VTN0401410B* | 17100 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290088 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG9J936 | *96VTN0401410B* | 17200 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290122 | 1.41 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE30924 | *96VTN0401712A* | 16900 | 15.2 | 10 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
215290138 | 1.41 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG31924 | *96VTN0401712B* | 16900 | 15.2 | 10 | 8.5 | 17000 | 18800 | 110.6% | 2.3 | 11500 | R-410A
215290140 | 1.41 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG31930 | *96VTN0401712B* | 16900 | 15.2 | 10 | 8.5 | 17000 | 18800 | 110.6% | 2.3 | 11500 | R-410A
215290154 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE33936 | *96VTN0401712B* | 17100 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
213885815 | 2.63 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | AE(D,N,U)+CM36A34+TDR |  | 31600 | 18.5 | 11.9 | 8.3 | 31200 | 38000 | 121.8% | 2.87 | 30800 | R-410A
215289572 | 1.38 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE32930 | *92MSN0401712A* | 16500 | 15.2 | 10 | 8.5 | 16500 | 18400 | 111.5% | 2.24 | 11200 | R-410A
215289586 | 1.36 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG30924 | *92MSN0401712A* | 16300 | 15.2 | 9.5 | 8.5 | 16700 | 19000 | 113.8% | 2.32 | 11300 | R-410A
215289604 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG24936 | *92MSN0601412A* | 17500 | 16 | 11 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215289671 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE34936 | *92MSN0601714A* | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215289689 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE9J936 | *92MSN0601714A* | 17500 | 16 | 10.5 | 8.5 | 16900 | 19000 | 112.4% | 2.34 | 11400 | R-410A
215289719 | 1.48 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG35936 | *92MSN0801716A* | 17700 | 16 | 11 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215289737 | 1.38 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE22936 | *96MSN0261410A* | 16600 | 19 | 10 | 8.1 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215289756 | 1.43 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG33936 | *96MSN0261410A* | 17100 | 20 | 10 | 8.1 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
216794424 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B080U4PSC+LRP | 32000 | 19.4 | 12 | 9 | 32800 | 30800 | 93.9% | 2.76 | 37400 | R-454B
216794265 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S8V2B060M4PDB | 19500 | 21 | 11.2 | 10 | 22000 | 21800 | 99.09% | 2.93 | 27000 | R-454B
216794427 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B080U4VSB+LRP | 32000 | 19.4 | 12 | 9 | 32800 | 30800 | 93.9% | 2.76 | 37400 | R-454B
216797086 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2B080M4PDB | 30200 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.68 | 38000 | R-454B
216797101 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B060D3PSC+LRP | 29600 | 18 | 9.8 | 8.5 | 33800 | 33800 | 100% | 2.71 | 38500 | R-454B
216797103 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B060D3VSB+LRP | 29600 | 18 | 9.8 | 8.5 | 33800 | 33800 | 100% | 2.71 | 38500 | R-454B
216794244 | 1.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | L8V1A060U3VSB+LRP | 19800 | 21.2 | 11.2 | 10 | 22200 | 21800 | 98.2% | 2.95 | 27000 | R-454B
216794278 | 1.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | S8V2B080M4PDB | 20000 | 21.8 | 11.7 | 9.5 | 22600 | 22000 | 97.35% | 2.89 | 27200 | R-454B
212479911 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 58SP*A045V17**16 | 23200 | 17 | 10 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212479913 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L159 | 58SP*A045V17**16 | 23400 | 17 | 10 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212479995 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 58TP*A090V17**16 | 23200 | 17 | 10 | 8.1 | 24400 | 23000 | 94.26% | 1.94 | 18000 | R-410A
212480029 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 59SC2D080E17**16 | 24000 | 17 | 10.5 | 8.1 | 24600 | 22400 | 91.06% | 1.88 | 18100 | R-410A
212480044 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 59SC2D080E17**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22400 | 91.06% | 1.88 | 18100 | R-410A
213781645 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6121AL*+UI | 59TN6C100C21**22 | 33200 | 17.5 | 11.7 | 8.5 | 32000 | 24800 | 77.5% | 1.98 | 31200 | R-410A
216686107 | 4.54 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FHRAVM6021S*YECA |  | 54500 | 17.5 | 10.5 | 8.1 | 54500 | 53000 | 97.25% | 2 | 51000 | R-454B
215290155 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE33936 | *96VTN0401712B* | 17100 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290187 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE31924 | *96VTN0601412A* | 17500 | 16 | 10 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
215290188 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE31930 | *96VTN0601412A* | 17500 | 16 | 10 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
215290189 | 1.48 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32930 | *96VTN0601412A* | 17700 | 16 | 10 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
215290190 | 1.48 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *96VTN0601412A* | 17700 | 16 | 10 | 8.5 | 17200 | 18600 | 108.1% | 2.28 | 11500 | R-410A
215290220 | 1.41 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE22936 | *96VTN0601412B* | 16900 | 16 | 10 | 8.5 | 16900 | 19400 | 114.8% | 2.38 | 11400 | R-410A
215290254 | 1.44 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE7J924 | *96VTN0601412B* | 17300 | 16 | 10.5 | 8.5 | 16900 | 19400 | 114.8% | 2.38 | 11400 | R-410A
215290257 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG8J936 | *96VTN0601412B* | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
210607415 | 2.85 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+MBVC1601**-1A*+TX |  | 34200 | 19 | 12 | 8.2 | 34200 | 24400 | 71.35% | 1.85 | 21600 | R-410A
214731215 | 2.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG9J936 | 926TC60080V21*** | 35600 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.9 | 28400 | R-410A
213885822 | 3.58 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH848GKA2* | AE(D,N,U)+CM60A34+TDR |  | 43000 | 18 | 10.4 | 8.3 | 46000 | 39000 | 84.78% | 2.75 | 35600 | R-410A
216619281 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | C60A***L199 | 59MN7C080C21**20 | 44500 | 21 | 12 | 9 | 44500 | 36000 | 80.9% | 2.26 | 42500 | R-410A
211206915 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | TM9V100C20MP12 | 43500 | 19 | 11.7 | 9 | 44500 | 36400 | 81.8% | 2.14 | 41500 | R-410A
211206880 | 2.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B3621 | XAMB36DE2N1+CC | TM9V080B12MP12 | 32200 | 18 | 11.7 | 8.5 | 34000 | 29400 | 86.47% | 1.92 | 34600 | R-410A
214091976 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.68 | 26000 | R-410A
211391533 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DBCN1 | TMLE100C16MP11 | 34000 | 17.5 | 10 | 8.1 | 33600 | 23800 | 70.83% | 2.08 | 25200 | R-410A
216794255 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S8V2A040M3PDB | 19500 | 21.2 | 11.2 | 10 | 22400 | 21600 | 96.43% | 2.79 | 26600 | R-454B
216794289 | 1.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | S9V2B040D3VSB+LRP | 19000 | 19.4 | 11.7 | 9 | 23200 | 21800 | 93.97% | 2.74 | 26400 | R-454B
216794330 | 1.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | S9V2B080U4PSC+LRP | 20000 | 21 | 11.7 | 10 | 22400 | 21600 | 96.43% | 2.95 | 26600 | R-454B
216797049 | 1.58 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | D(A,C,E)30A4J+TDR | *DHMB080CCV3+LRP | 18900 | 18 | 9.8 | 8.5 | 23200 | 23200 | 100% | 2.9 | 27800 | R-454B
216797088 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2C080M5PCB | 30400 | 18 | 9.8 | 8.5 | 32600 | 32600 | 100% | 2.88 | 37400 | R-454B
216797124 | 2.55 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2C100U4VSB+LRP | 30600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.88 | 37400 | R-454B
213885823 | 3.63 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH848GKA2* | AE(D,N,U)+CM60B34+TDR |  | 43500 | 18 | 10.4 | 8.4 | 46000 | 39500 | 85.87% | 2.79 | 35800 | R-410A
216797117 | 2.5 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2C080U5PSC+LRP | 30000 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.82 | 37400 | R-454B
214092180 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y82E100C16LMPS1 | 32400 | 18 | 9.5 | 8.5 | 33400 | 28000 | 83.83% | 2.7 | 25600 | R-410A
214092182 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y82E100C20LMPS1 | 32400 | 18.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092196 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | YP9C100C16MP13 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
214092198 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | YP9C100C20MP13 | 31600 | 17.5 | 9.3 | 8.1 | 33800 | 28200 | 83.43% | 2.69 | 25800 | R-410A
214092701 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL9E080C16UH11 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.64 | 25800 | R-410A
214092703 | 2.78 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.2 | 33400 | 29000 | 86.83% | 2.72 | 26200 | R-410A
214092726 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V100C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214092728 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V120C20MP12 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214092769 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V120D20MP12 | 32200 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
214092778 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y100C20MP11 | 32400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.59 | 25600 | R-410A
214092787 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLE080B12MP11 | 32600 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.61 | 25800 | R-410A
214092051 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
215472302 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X48A1 | D(A,C,E)48C34+TDR | S9V2C080U5PSC+RP | 44000 | 18 | 11 | 8.2 | 44000 | 37000 | 84.09% | 2.2 | 42500 | R-410A
214092092 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.68 | 26000 | R-410A
214092094 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.2 | 33000 | 29000 | 87.88% | 2.72 | 26000 | R-410A
214092142 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E040A12SMPS1 | 33200 | 18 | 10 | 8.3 | 32800 | 30000 | 91.46% | 2.76 | 26600 | R-410A
214092144 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.3 | 32800 | 29800 | 90.85% | 2.73 | 26400 | R-410A
214092158 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E100B12SMPS1 | 32400 | 18.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214092201 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | YP9C120D20MP13 | 31200 | 16.8 | 9.3 | 8.5 | 32200 | 28000 | 86.96% | 2.79 | 25200 | R-410A
211178381 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | G*VM970804CNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
214064202 | 1.98 | Yes | Yes | CONCORD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | H,A,DG9J936 | 97G2DF070BE16 | 23800 | 18 | 12 | 8.5 | 22400 | 16300 | 72.77% | 2.16 | 16000 | R-410A
213752640 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M14**12 | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.89 | 19100 | R-410A
213752709 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B090M21**20 | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.91 | 19100 | R-410A
213752809 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2E060M17**14 | 23800 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213752842 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2E100M21**20 | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.88 | 19100 | R-410A
213752860 | 1.92 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC6A040M14**10 | 23000 | 16.5 | 9.9 | 8.5 | 25400 | 20200 | 79.53% | 2.94 | 18800 | R-410A
213752875 | 1.88 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC6A060M14**12 | 22600 | 16.9 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.95 | 18700 | R-410A
213753028 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59TP6C080V17**16 | 23400 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.88 | 19100 | R-410A
211178380 | 1.38 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | G*VC960804CNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
212498431 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CP2403A+TXV+TD |  | 23000 | 16 | 10 | 8.5 | 24800 | 22600 | 91.13% | 1.84 | 18200 | R-410A
211391803 | 2.73 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC30CXXN1+TXV | TMLE100B12MP11 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 23400 | 70.06% | 2.04 | 26200 | R-410A
211391876 | 2.83 | Yes | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DBCN1 | TMLE100B12MP11 | 34000 | 18 | 10 | 8.1 | 33800 | 23800 | 70.41% | 2.06 | 25400 | R-410A
211388332 | 2.82 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DXXN1+TXV | LP9C060B12MP13 | 33800 | 17 | 9.5 | 8.5 | 33400 | 23800 | 71.26% | 2.04 | 25400 | R-410A
212479908 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P159 | 58SP*A045V17**16 | 23400 | 17 | 10 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212479915 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 58SP*A045V17**16 | 23000 | 17 | 9.5 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212480017 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 59SC2D060E14**12 | 23000 | 17 | 9.5 | 8.5 | 24000 | 23200 | 96.67% | 1.96 | 17800 | R-410A
212480108 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 59SP6A080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212480165 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P159 | 59TP6B080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
211387750 | 2.77 | No | No | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DXXN1+TXV | TP9C080B12MP13 | 33200 | 16.5 | 9.5 | 8.1 | 33400 | 23600 | 70.66% | 2 | 25200 | R-410A
215290371 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE33936 | *96VTN0801716A* | 17400 | 16 | 10.5 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290373 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG34936 | *96VTN0801716A* | 17400 | 16 | 10.5 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290388 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG9J936 | *96VTN0801716A* | 17400 | 16 | 10.5 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290406 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG32936 | *96VTN0801716B* | 17400 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215290407 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE32930 | *96VTN0801716B* | 17400 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
212348376 | 1.45 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)W244+TDR |  | 17400 | 15.2 | 10.5 | 8.5 | 18400 | 18300 | 99.46% | 2.57 | 12400 | R-410A
212348378 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | LEW30B4 |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
216794606 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2D120U5VSB+LRP | 41500 | 20.2 | 11.7 | 9 | 45500 | 41500 | 91.21% | 2.75 | 49500 | R-454B
213770177 | 2 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DE9J936 | A96DF1E045B12 | 24000 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
212479800 | 1.46 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A24VBA+TXV | 58S(B,C)*A070E14**12 | 17500 | 16 | 10.5 | 8.5 | 16800 | 18700 | 111.3% | 2.3 | 11400 | R-410A
212479839 | 1.47 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A36VCA+TXV | 59SU5A040E17**12 | 17600 | 16 | 11 | 8.5 | 16900 | 18400 | 108.9% | 2.26 | 11400 | R-410A
214092698 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.6 | 25600 | R-410A
214092750 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.71 | 26200 | R-410A
214061528 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | A24VBA+TXV | A97DF2E045B12 | 23400 | 17 | 12 | 8.35 | 22400 | 16900 | 75.45% | 2.18 | 16100 | R-410A
214061529 | 1.98 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | A36VDA+TXV | A97DF2E045B12 | 23800 | 18 | 12 | 8.5 | 22400 | 16900 | 75.45% | 2.22 | 16100 | R-410A
214092817 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29000 | 86.31% | 2.61 | 26200 | R-410A
214092850 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E100B12LMPS1 | 31600 | 18.4 | 9.3 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
214064201 | 2 | Yes | Yes | CONCORD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | H,A,DG9J936 | 97G2DF045BE12 | 24000 | 18 | 12 | 8.5 | 22400 | 16300 | 72.77% | 2.16 | 16000 | R-410A
214263954 | 2 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J936 | A96DF2E045B12 | 24000 | 18 | 12 | 8.5 | 22400 | 16300 | 72.77% | 2.16 | 16000 | R-410A
213782235 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*6012AL*+UI | 58TN*B090C17**16 | 33000 | 16.5 | 11 | 8.1 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213274529 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM8E120C16MP11 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213274559 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TMLE080C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.14 | 30400 | R-410A
212480160 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149 | 59TP6B080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212480258 | 2.6 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | PL36H210P299 | 59SC2D100E21**20 | 31200 | 15.2 | 9 | 8.5 | 32000 | 25600 | 80% | 1.86 | 22200 | R-410A
212480342 | 2.43 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | PL36H210P749 | 59TP6B080V21**20 | 29200 | 15.2 | 8.5 | 8.1 | 32000 | 27000 | 84.38% | 1.78 | 22200 | R-410A
214092696 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL8E100C20UH11 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.68 | 25400 | R-410A
214092735 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y080C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
214092771 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9Y060B12MP11 | 32600 | 17.5 | 9.5 | 8.1 | 33800 | 29200 | 86.39% | 2.61 | 26400 | R-410A
213286674 | 1.45 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CP2403A+TXV+TD |  | 17400 | 15.2 | 10.5 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
213286706 | 2.45 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | CE2903C+TXV |  | 29400 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
215375079 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0754A17DZ | 21600 | 17 | 10 | 8.1 | 22600 | 18900 | 83.63% | 2.1 | 16800 | R-410A
211206890 | 2.68 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B3621 | XAMB36DE2N1+CC | LP9C080B12MP13 | 32200 | 18 | 11.7 | 8.5 | 34000 | 29400 | 86.47% | 1.92 | 34600 | R-410A
216797162 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2B080U4VSB+LRP | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
214101698 | 1.97 | Yes | Yes | CONCORD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | H,A,DD06936 | 97G2DF045BE12 | 23600 | 17 | 12 | 8.35 | 22400 | 16300 | 72.77% | 2.12 | 16000 | R-410A
215932547 | 2.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0902120B* | 34000 | 20.5 | 12 | 9.5 | 34000 | 25800 | 75.88% | 2.06 | 29800 | R-454B
214394751 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R962V0705A21M4S | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214336692 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R951V1005A21M4S | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215933617 | 2.8 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU0802120B* | 33600 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
215933787 | 2.85 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0901716B* | 34200 | 19.5 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.94 | 30000 | R-454B
213753091 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M14**12 | 29600 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
210693334 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC961005CNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213885803 | 1.85 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | AE(D,N,U)+CM36B34+TDR |  | 22200 | 17.3 | 11.4 | 8.4 | 20600 | 25000 | 121.4% | 2.8 | 20200 | R-410A
214092801 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLV120C20MP12 | 32000 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214092812 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TP9C120D20MP13 | 32000 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
214092846 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | Y81E080C20LMPS1 | 32600 | 18 | 10 | 8.5 | 33400 | 28400 | 85.03% | 2.71 | 25800 | R-410A
214092860 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E100C16SMPS1 | 32400 | 18 | 9.5 | 8.5 | 33400 | 28400 | 85.03% | 2.7 | 25800 | R-410A
214092862 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E100C20LMPS1 | 31600 | 17.5 | 9.3 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
214092871 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E120C16SMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
214092887 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y82E100C16LMPS1 | 32400 | 18 | 9.5 | 8.5 | 33400 | 28000 | 83.83% | 2.7 | 25600 | R-410A
213782335 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*6012AL*+UI | 59TN6C080C17**14 | 32800 | 16.5 | 11 | 8.1 | 32200 | 25000 | 77.64% | 1.98 | 31400 | R-410A
213286684 | 1.45 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CE1801A+TXV |  | 17400 | 17 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
216796427 | 2.52 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8V2A040M3PCB | 30200 | 15.5 | 12 | 8.1 | 30000 | 21600 | 72% | 2.86 | 21000 | R-454B
216796511 | 2.52 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X1A040M3PSC | 30200 | 15.5 | 11.7 | 8.1 | 30400 | 21800 | 71.71% | 2.89 | 21200 | R-454B
216796538 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X1C100M5PTC | 31800 | 15.5 | 11.7 | 8.5 | 31600 | 22600 | 71.52% | 3.03 | 22000 | R-454B
216796563 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X2C080M5PSC | 31800 | 15.5 | 12 | 8.5 | 31400 | 22400 | 71.34% | 3.03 | 21800 | R-454B
216796581 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X2D120M5PSC | 31800 | 16 | 11.7 | 8.5 | 31400 | 22000 | 70.06% | 2.94 | 21600 | R-454B
216796654 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S9V2C080U5PSC | 31200 | 15.2 | 12 | 8.5 | 31000 | 22200 | 71.61% | 2.97 | 21600 | R-454B
216796643 | 2.6 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2B080U4VSA | 31200 | 15.5 | 11.7 | 8.5 | 32000 | 22400 | 70% | 3 | 22000 | R-454B
214263953 | 2 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J(1,2)36+TXV | A96DF2E045B12 | 24000 | 18 | 12 | 8.5 | 22400 | 16300 | 72.77% | 2.16 | 16000 | R-410A
213274511 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | CP9C100C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
210609975 | 2.83 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | AMVE48DP1400A* |  | 34000 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213278587 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D24+JMET12BS2N1+TDR |  | 32000 | 17.5 | 8.6 | 8.1 | 36000 | 26000 | 72.22% | 2.8 | 25200 | R-410A
213274534 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM8V100C20MP12 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.09 | 31000 | R-410A
215218907 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AD-33(P,U)*****9 | Y91E080B12SMPS1 | 33200 | 17 | 10 | 8.5 | 30400 | 22000 | 72.37% | 1.8 | 24200 | R-410A
214092810 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
214092878 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E120C20SMPS1 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214092885 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | Y82E080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.2 | 32800 | 29800 | 90.85% | 2.8 | 26400 | R-410A
214092867 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | Y81E100C20SMPS1 | 32600 | 17.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092917 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | YPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
216796507 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8V2D120M5PDB | 31400 | 15.5 | 11.7 | 8.5 | 31200 | 22200 | 71.15% | 2.96 | 21600 | R-454B
216796526 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X1C080M5PSC | 31800 | 16 | 11.7 | 8.1 | 31400 | 22000 | 70.06% | 2.93 | 21600 | R-454B
216796710 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2D120U5VSB | 32200 | 16 | 11.7 | 8.5 | 31600 | 22200 | 70.25% | 2.97 | 21800 | R-454B
216796742 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X1C100U5PSB | 31800 | 15.2 | 11.7 | 8.1 | 31400 | 22400 | 71.34% | 3.01 | 21800 | R-454B
216796775 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X2C080U5PSB | 31600 | 15.5 | 12 | 8.5 | 31200 | 22400 | 71.79% | 2.98 | 21800 | R-454B
215375162 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R921V0603A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 31600 | 92.4% | 1.9 | 29800 | R-410A
214336701 | 4.29 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R97MV1155A24DHS | 51500 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214336683 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802VA100521Z | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336685 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802VA125524Z | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214336718 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R801V1005A21UHU | 45500 | 16 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.18 | 32400 | R-410A
216796536 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8X1C100M5PTC | 31200 | 15.2 | 11.7 | 8.5 | 31400 | 22400 | 71.34% | 3 | 21800 | R-454B
216796572 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X2C100M5PSC | 31800 | 15.5 | 11.7 | 8.5 | 31600 | 22600 | 71.52% | 3.03 | 22000 | R-454B
216796622 | 2.6 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2B060U4PSB | 31200 | 15.5 | 11.7 | 8.5 | 32000 | 22400 | 70% | 2.96 | 22000 | R-454B
216794291 | 1.57 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B040U3PSC+LRP | 18800 | 19.6 | 11 | 9 | 22200 | 21000 | 94.59% | 2.56 | 25600 | R-454B
215565282 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
215565273 | 2.53 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4J+TDR | TM8E120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
213278571 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+JMET12CS2N1+TDR |  | 29800 | 16.9 | 9 | 8.5 | 32600 | 27800 | 85.28% | 2.8 | 25200 | R-410A
214092896 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | YP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.63 | 25600 | R-410A
214092910 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | YPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29000 | 86.31% | 2.61 | 26200 | R-410A
213612088 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R802V0755A21DZ | 44000 | 15.4 | 10 | 8.1 | 45500 | 36400 | 80% | 3.02 | 33800 | R-410A
207455035 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36U9 | EL296UH090XV36C* | 34000 | 22 | 13 | 8.8 | 34000 | 27200 | 80% | 1.82 | 32000 | R-410A
213614464 | 1.98 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YZT48B21 | D(A,C,E)60B44+TDR | TM9Y100C16MP11 | 23800 | 16 | 12.4 | 8.4 | 47500 | 34200 | 72% | 3.03 | 33200 | R-410A
215565327 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)61A3J+TDR | CP9C100C16MP13 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215565277 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | CP9C100C16MP13 | 40500 | 17 | 11.5 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
215413728 | 1.36 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | SM2925 |  | 16300 | 17 | 10.5 | 8.55 | 16900 | 19300 | 114.2% | 2.28 | 11500 | R-410A
214061530 | 1.93 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | A24VBA+TXV | A97DF2E070B16 | 23200 | 17 | 12 | 8.35 | 22400 | 16900 | 75.45% | 2.18 | 16100 | R-410A
214263892 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J(1,2)36+TXV | A80DS2V090B16 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.16 | 15800 | R-410A
216796547 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X1D120M5PTC | 31800 | 16 | 11.7 | 8.5 | 31400 | 22000 | 70.06% | 2.94 | 21600 | R-454B
216796613 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2B060D3VSB | 31600 | 15.5 | 12 | 8.1 | 32200 | 22600 | 70.19% | 2.85 | 22200 | R-454B
214264021 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J936 | EFV12BCA | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
216796665 | 2.65 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2C100D4VSB | 31800 | 15.5 | 12 | 8.1 | 32000 | 22400 | 70% | 2.84 | 22000 | R-454B
216796679 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2C100U4VSB | 31800 | 15.5 | 12 | 8.5 | 31400 | 22400 | 71.34% | 3.03 | 21800 | R-454B
216797056 | 1.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | D(A,C,E)30A4J+TDR | S9V2B060U4PSC+LRP | 20400 | 18 | 11 | 8.5 | 24400 | 24400 | 100% | 3.04 | 28600 | R-454B
215565332 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)61A3J+TDR | TP9C120D20MP13 | 41500 | 18 | 11.5 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216796688 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2C100U5PSC | 31800 | 15.5 | 12 | 8.5 | 31400 | 22400 | 71.34% | 3.03 | 21800 | R-454B
216796482 | 2.58 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8V2C100M5PCB | 31000 | 15.2 | 12 | 8.1 | 31000 | 22200 | 71.61% | 2.93 | 21600 | R-454B
216796498 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8V2D120M5PCB | 31400 | 15.5 | 11.7 | 8.5 | 31200 | 22200 | 71.15% | 2.96 | 21600 | R-454B
216796549 | 2.52 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X2A040M3PSC | 30200 | 15.5 | 11.7 | 8.1 | 30400 | 21800 | 71.71% | 2.89 | 21200 | R-454B
213279263 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM9E100C20MP12 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.11 | 31000 | R-410A
216796528 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8X1C080M5PTC | 31200 | 15.2 | 12 | 8.5 | 31200 | 22200 | 71.15% | 3 | 21600 | R-454B
216796589 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2B040D3PSC | 31400 | 15.5 | 12 | 8.1 | 32000 | 22800 | 71.25% | 2.87 | 22200 | R-454B
216796671 | 2.65 | No | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2C100D5VSB | 31800 | 15.5 | 12 | 8.1 | 32000 | 22400 | 70% | 2.84 | 22000 | R-454B
216796712 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X1B040D3PSB | 31400 | 15.5 | 11.7 | 8.1 | 32200 | 22600 | 70.19% | 2.85 | 22200 | R-454B
216796734 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X1C080U5PSB | 31600 | 15.5 | 12 | 8.5 | 31200 | 22400 | 71.79% | 2.98 | 21800 | R-454B
215565271 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | Z9ES060A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
215565305 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM9V060B12MP12 | 22400 | 17 | 12 | 9 | 23000 | 18000 | 78.26% | 2 | 18400 | R-454B
215565321 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z8ET080B12LMPS1 | 22200 | 18 | 12 | 9 | 22800 | 18500 | 81.14% | 2 | 18600 | R-454B
216794283 | 1.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | S9V2B040D3PSC+LRP | 19000 | 19.4 | 11.7 | 9 | 23200 | 21800 | 93.97% | 2.74 | 26400 | R-454B
215565287 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
215419907 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)25B4J+TDR | Z9ES040A10SMPS1 | 21200 | 18 | 11.7 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18400 | R-454B
215565264 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TP9C060B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
213279241 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM8E080C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.14 | 30400 | R-410A
215565312 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TMLE100B12MP11 | 22400 | 17 | 12 | 9 | 23000 | 18000 | 78.26% | 2 | 18400 | R-454B
215565253 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | CP9C080B12MP13 | 22600 | 17 | 12 | 9 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
213279238 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TL9E080C16UH11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.11 | 30600 | R-410A
213279268 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM9V100C20MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.14 | 30600 | R-410A
213782165 | 2.7 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 59TN6C060C17**14 | 32400 | 16 | 10.5 | 8.1 | 33000 | 25200 | 76.36% | 1.94 | 31800 | R-410A
211206901 | 2.72 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B3621 | XAMB36DE2N1+CC | LPLC080B12MP13 | 32600 | 18 | 11.7 | 8.5 | 34400 | 29600 | 86.05% | 1.94 | 34600 | R-410A
216796509 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8V2D120M5PDB | 32200 | 16 | 11.7 | 8.5 | 31400 | 22400 | 71.34% | 2.99 | 21800 | R-454B
216796591 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2B040D3VSB | 31400 | 15.5 | 11.7 | 8.1 | 32000 | 22800 | 71.25% | 2.87 | 22200 | R-454B
216796659 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S9V2C080U5VSB | 31200 | 15.2 | 11.7 | 8.5 | 31000 | 22200 | 71.61% | 2.97 | 21600 | R-454B
214336719 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60C44+TDR | R802V0755A21UHN | 45500 | 15.2 | 10 | 8.1 | 45500 | 33800 | 74.29% | 3.18 | 32400 | R-410A
213279284 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TMLV100C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
216796686 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S9V2C100U5PSC | 31200 | 15.2 | 12 | 8.5 | 31200 | 22200 | 71.15% | 3 | 21600 | R-454B
213774638 | 2 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EHD4X48AAL+WALLCON | *97CMN0601714B* | 24000 | 15.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20600 | R-410A
216687195 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF97MV307017DH | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
214802925 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60B44+TDR | R801V1005A21UHN | 45000 | 15.6 | 10.1 | 8.2 | 45500 | 33800 | 74.29% | 3.06 | 36400 | R-410A
215565256 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TL9E060B12UH11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
214802922 | 3.67 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R801V1005A21UHN | 44000 | 15.4 | 10 | 8.1 | 45500 | 33600 | 73.85% | 3.01 | 36000 | R-410A
214802738 | 1.87 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A44+TDR | R801V1004A17UHS | 22400 | 16.4 | 11.8 | 8.2 | 23000 | 16300 | 70.87% | 3.01 | 17000 | R-410A
213274555 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM9Y100C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213274557 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM9Y120D20MP11 | 43000 | 16 | 11 | 8.2 | 44000 | 31400 | 71.36% | 3.11 | 30600 | R-410A
215565274 | 2.53 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4J+TDR | TMLE120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
215565258 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TM8E060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
215565261 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TM9Y080B12MP11 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18600 | R-454B
213274514 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | CPLC080C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213274550 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM9V100C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213279244 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM8E100C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213279245 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM8E100C20MP11 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.11 | 31000 | R-410A
214394786 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U97MV1155A24DHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
212348377 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | LEW30A4 |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
213279276 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TMLE080C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.14 | 30400 | R-410A
213279279 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TMLE100C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
216794476 | 3.54 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | L8V1C100U5VSB+LRP | 42500 | 20.4 | 11.7 | 9.5 | 47000 | 42500 | 90.43% | 2.74 | 50500 | R-454B
213273413 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D26+TDR | Z8ES100C20SMPS1 | 32000 | 16 | 8.6 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
215565260 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TM9V060B12MP12 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215399921 | 2.57 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR |  | 30800 | 15.2 | 10 | 8.1 | 31000 | 31600 | 101.9% | 2.52 | 27000 | R-454B
214521918 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ES080C16SMPS1 | 31800 | 17.9 | 9.9 | 8.4 | 33200 | 27400 | 82.53% | 2.68 | 25200 | R-410A
215565275 | 2.53 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4J+TDR | Z8ES080B12SMPS1 | 30400 | 18 | 11.2 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
215565308 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM9Y080B12MP11 | 22200 | 17 | 11.7 | 9 | 23000 | 18500 | 80.43% | 2 | 18700 | R-454B
215565310 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TMLE060A12MP11 | 20600 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
213753093 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 58S(B,C)*B070M14**12 | 29600 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.72 | 23400 | R-410A
214101699 | 2 | Yes | Yes | CONCORD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | H,A,DD15936 | 97G2DF045BE12 | 24000 | 18 | 12 | 8.5 | 22400 | 16300 | 72.77% | 2.16 | 16000 | R-410A
214802750 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0504A17UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.63 | 21000 | R-410A
214802755 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)30B34+TDR | R801V0754A17DZ | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.62 | 21000 | R-410A
214802732 | 1.9 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24C34+TDR | R801V1004A17UHN | 22800 | 16 | 12 | 8.4 | 23000 | 16300 | 70.87% | 3.07 | 17000 | R-410A
214802741 | 1.87 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)30A34+TDR | R801V1004A17UHS | 22400 | 16.4 | 11.8 | 8.1 | 22800 | 16200 | 71.05% | 2.95 | 16900 | R-410A
214802932 | 3.75 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)60C34+TDR | R801V1005A21UHS | 45000 | 15.6 | 10.1 | 8.1 | 45500 | 33600 | 73.85% | 2.99 | 36000 | R-410A
212623983 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM9Y080B12MP11 | 29800 | 17.4 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212623680 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TL9E060B12UH11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623733 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9E060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623832 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | CP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623850 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM9V060B12MP12 | 29800 | 16.9 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
211206908 | 4.33 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B6021 | XAMC60HE4N1+CC | TP9C100C20MP13 | 52000 | 18 | 11 | 8.5 | 55000 | 42000 | 76.36% | 2.16 | 47000 | R-410A
213278583 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A46+JMET12BS2N1+TDR |  | 34000 | 18 | 8.9 | 8.1 | 36000 | 26000 | 72.22% | 2.8 | 25200 | R-410A
213274572 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TP9C100C20MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.14 | 30600 | R-410A
213274574 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TPLC080C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
212623867 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM9V060B12MP12 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623883 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TP9C060B12MP13 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623897 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623917 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E080B12MP11 | 31600 | 17.9 | 9.3 | 8.4 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212623931 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TL8E060A12UH11 | 31600 | 18 | 9.5 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212623965 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E080B12MP11 | 32800 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212623980 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM9Y080B12MP11 | 29800 | 17.4 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
216054516 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | CP9C060B12MP13 | 22600 | 17 | 12 | 9 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054686 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL8E100C20UH11 | 31000 | 17 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216054695 | 2.53 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216054541 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E080B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054542 | 1.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8E080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216054574 | 1.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E060B12MP12 | 22000 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
216054575 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E060B12MP12 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18600 | R-454B
214391675 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R921V0603A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.9 | 16000 | R-410A
213612055 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R802V0754A17UH | 32800 | 15.4 | 11.7 | 8.1 | 33800 | 26000 | 76.92% | 2.76 | 24600 | R-410A
214802769 | 2.73 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R801V0754A17UH | 32800 | 15.4 | 11.7 | 8.1 | 33800 | 24600 | 72.78% | 2.76 | 26000 | R-410A
214802771 | 2.77 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R801V1004A17UHS | 33200 | 15.4 | 11.7 | 8.1 | 34200 | 24800 | 72.51% | 2.77 | 26200 | R-410A
216054591 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9V080B12MP12 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
216054593 | 1.66 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y040A10MP11 | 19900 | 16 | 10 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216054608 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TMLE040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054624 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TP9C060B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
213286672 | 1.43 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CP2301A+TXV+TD |  | 17100 | 15.2 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
216054690 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216054658 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES026A08SMPS1 | 20600 | 17.5 | 11.2 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
216054659 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | Z9ES026A08SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17300 | 75.22% | 2 | 17700 | R-454B
216054533 | 1.65 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E040A12MP11 | 19800 | 16 | 11.2 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054565 | 1.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E040A10MP12 | 19500 | 16 | 10 | 9 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
216054566 | 1.72 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM9E040A10MP12 | 20600 | 16.5 | 9.8 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
216054583 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9V040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 17500 | 76.09% | 2 | 17800 | R-454B
216054649 | 1.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ET060A12LMPS1 | 19500 | 18 | 11.2 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
216054665 | 1.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES060A10SMPS1 | 19600 | 17 | 11.2 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216054666 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES060A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
216054668 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z9ES060A10SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216054727 | 2.53 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216054741 | 2.55 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
214608728 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 24800 | 72.94% | 2.12 | 25000 | R-410A
212628083 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | CP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628085 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628101 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628117 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627934 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8Y080C16MP11 | 29800 | 17.8 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
215399919 | 1.88 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.69 | 18700 | R-454B
216035143 | 1.87 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3J+TDR |  | 22400 | 15.2 | 11 | 8.5 | 22600 | 21200 | 93.81% | 2.65 | 18600 | R-454B
216054536 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216054545 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM8E100B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054563 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E026A08MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
213752153 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58S(B,C)*B045M14**12 | 22800 | 16.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213752335 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*B090V21**20 | 23600 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
216054595 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216054670 | 1.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES060B12SMPS1 | 22000 | 17 | 11.7 | 8.5 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
213752544 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SP6A080V21**20 | 23800 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213752578 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C060V14**12 | 23200 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
213752678 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M21**16 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213752694 | 1.87 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B090M21**16 | 22400 | 17.2 | 10 | 8.4 | 25200 | 19900 | 78.97% | 2.94 | 18600 | R-410A
212627936 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8Y080C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627953 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8Y080C16MP11 | 33400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627983 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628068 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212628069 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212626930 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TMLE060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212627000 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9V080C16MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212627048 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | CP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
214328316 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG34936 | WPV070T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
214521921 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ES080C20LMPS1 | 31800 | 17.9 | 9.9 | 8.4 | 33200 | 28200 | 84.94% | 2.69 | 25600 | R-410A
214521955 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES120C20SMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
214521964 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ET100C16LMPS1 | 32200 | 18 | 9.4 | 8.5 | 33200 | 27800 | 83.73% | 2.7 | 25400 | R-410A
216794233 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | *DHMB080CCV3+LRP | 19500 | 20.9 | 11.2 | 10 | 23000 | 22000 | 95.65% | 2.91 | 27000 | R-454B
215565281 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | TM9V120D20MP12 | 41000 | 18 | 11.5 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
212627064 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627148 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8Y100C20MP11 | 32600 | 18 | 9 | 8.4 | 33800 | 30000 | 88.76% | 2.83 | 26800 | R-410A
212627151 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | CP9C100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27200 | 80.47% | 2.47 | 25200 | R-410A
212627251 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627348 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9V060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627350 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9V060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627433 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8E080B12MP11 | 30600 | 17.7 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627466 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TMLE080B12MP11 | 29800 | 17.4 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
213752712 | 1.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B110M21**20 | 22800 | 17.3 | 10.2 | 8.4 | 25600 | 20000 | 78.12% | 2.98 | 18800 | R-410A
213752748 | 1.9 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*B070V17**16 | 22800 | 17.5 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213752753 | 1.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58TP*B090V17**16 | 22200 | 17.3 | 9.7 | 8.4 | 25200 | 19900 | 78.97% | 2.94 | 18600 | R-410A
213752812 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2E060M17**14 | 23600 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213752905 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SP6A040V14**10 | 23200 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.83 | 19000 | R-410A
213752923 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SP6A040V17**12 | 23200 | 16 | 9 | 8.5 | 25800 | 20200 | 78.29% | 2.83 | 19000 | R-410A
212627468 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TMLE080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627483 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLE080B12MP11 | 33200 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627517 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CP9C080B12MP13 | 31800 | 17 | 9 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212627567 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8E080C16MP11 | 32600 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212627585 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8E100C16MP11 | 32600 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212627652 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9Y080C16MP11 | 33000 | 18.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627668 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212627684 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8Y100C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627716 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | CPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627749 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8V080C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627767 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627784 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8V100C16MP12 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627786 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8Y080C16MP11 | 31600 | 18.4 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627816 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TPLC080C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627817 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627835 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TPLC080C16MP13 | 33400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627916 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | CP9C100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627917 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627918 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624024 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TMLE080B12MP11 | 33000 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624041 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TMLE080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624057 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CPLC060A12MP13 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624059 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CPLC060A12MP13 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624072 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM8E080C16MP11 | 31400 | 18 | 9.9 | 8.4 | 34000 | 28400 | 83.53% | 2.75 | 26000 | R-410A
212624158 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TP9C080B12MP13 | 31800 | 17 | 9 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624223 | 2.63 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TMLE040A12MP11 | 31600 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624293 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212624392 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9Y080C16MP11 | 30600 | 18.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624424 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8E120C16MP11 | 32000 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624440 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TMLE120C16MP11 | 32400 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212624474 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624524 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | CPLC100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624607 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM8V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624675 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLV100C16MP12 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624724 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TPLC100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624725 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624727 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624776 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TL8E080C16UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624824 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624826 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TL9E080C16UH11 | 30000 | 17 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624875 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | CP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624894 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CP9C100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624911 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8Y080C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624958 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM8Y080C16MP11 | 31000 | 18.2 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624978 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625060 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9V100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625078 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM9V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625160 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TL9E100C20UH11 | 32400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
216035493 | 1.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | AE*S+CM24D2J+TDR |  | 22000 | 19 | 12 | 9 | 23200 | 20000 | 86.21% | 2.84 | 17900 | R-454B
215565257 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TM8E040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215565262 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TMLE040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215565296 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TL9E060B12UH11 | 22400 | 17 | 12 | 9 | 23000 | 18000 | 78.26% | 2 | 18400 | R-454B
215565298 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM8E060A12MP11 | 20600 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18300 | R-454B
215565303 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM9E060B12MP12 | 22200 | 17 | 11.7 | 9 | 23000 | 18300 | 79.57% | 2 | 18700 | R-454B
213613582 | 1.5 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24G4 |  | 18000 | 15.2 | 9.5 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214521935 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES100C16SMPS1 | 31200 | 17.8 | 9.3 | 8.3 | 33000 | 28200 | 85.45% | 2.66 | 25600 | R-410A
214864388 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE*L+CM48E34+TDR |  | 31200 | 18.3 | 10.3 | 8.4 | 32800 | 23200 | 70.73% | 2.1 | 24600 | R-410A
213278569 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+JMET12CS2N1+TDR |  | 29800 | 16.9 | 9 | 8.5 | 32600 | 27800 | 85.28% | 2.8 | 25200 | R-410A
214864381 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE*S+CM36A34+TDR |  | 31400 | 18.3 | 10.3 | 8.4 | 33000 | 23200 | 70.3% | 2.1 | 24600 | R-410A
212625162 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TL9E100C20UH11 | 32400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625195 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8Y100C20MP11 | 32600 | 18 | 9 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625209 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8Y120C20MP11 | 32200 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625226 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625276 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TL8E100C20UH11 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625359 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | CP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625394 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625409 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM9V100C20MP12 | 32800 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625426 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9V100C20MP12 | 33400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625443 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625526 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9V120D20MP12 | 29400 | 16.3 | 9 | 8.4 | 32000 | 28000 | 87.5% | 2.77 | 25200 | R-410A
212625561 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | CPLC120C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625611 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM9V120D20MP12 | 31400 | 16.9 | 9.3 | 8.4 | 32200 | 28000 | 86.96% | 2.77 | 25200 | R-410A
212625629 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM9V120D20MP12 | 31800 | 17 | 9.4 | 8.5 | 32200 | 28200 | 87.58% | 2.8 | 25400 | R-410A
212625693 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CPLC120C20MP13 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625696 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | CPLC120C20MP13 | 32000 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625746 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TMLV120C20MP12 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625762 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
213752366 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2E060M14**12 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.9 | 20200 | R-410A
213752418 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2E100M21**20 | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
212625795 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TPLC120C20MP13 | 32800 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625812 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9Y120D20MP11 | 32000 | 16.5 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625813 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9Y120D20MP11 | 29800 | 15.9 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625827 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9V120D20MP12 | 29800 | 16.4 | 9 | 8.5 | 32400 | 27800 | 85.8% | 2.79 | 25200 | R-410A
212625928 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V040A10MP12 | 32600 | 17 | 9 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625929 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
213752482 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC6A080M21**20 | 23800 | 16 | 9.5 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213752534 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SP6A080V17**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
212626046 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8Y060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626048 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8Y060A12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626078 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8Y080B12MP11 | 30600 | 17.6 | 9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626080 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8Y080B12MP11 | 31000 | 17.7 | 9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
213752583 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6C060V14**12 | 23600 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
213752617 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6C100V21**20 | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
212626264 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626364 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9E100C16MP12 | 31600 | 17.9 | 9.8 | 8.4 | 33600 | 27200 | 80.95% | 2.64 | 25200 | R-410A
212626531 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.2 | 33800 | 29200 | 86.39% | 2.65 | 26400 | R-410A
212626532 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.2 | 33800 | 29200 | 86.39% | 2.65 | 26400 | R-410A
213163587 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | H,FG80936+AEFE4B* |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
214625022 | 2.35 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)30A34+TDR |  | 28200 | 15.2 | 10.3 | 9.5 | 22600 | 27000 | 119.5% | 1.85 | 22600 | R-410A
213753268 | 2.43 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)36B34+TDR | 58TP*B070V14**12 | 29200 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.7 | 23400 | R-410A
212626696 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.68 | 26000 | R-410A
212626813 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TM8Y100C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 33800 | 27200 | 80.47% | 2.61 | 25200 | R-410A
209880042 | 3.67 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1848MJAZCA | FCCA6021SZEA | FF98MV510021UPS*A | 44000 | 19 | 10 | 8.1 | 43500 | 45500 | 104.6% | 1.9 | 45000 | R-410A
215565309 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TMLE040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
212623982 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9Y080B12MP11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
216054701 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y080C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216035483 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | AE*L+CM48C3J+TDR |  | 43000 | 18 | 11.7 | 8.5 | 45500 | 39000 | 85.71% | 2.87 | 35200 | R-454B
215565293 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | CP9C080B12MP13 | 22200 | 17 | 12 | 9 | 23000 | 18300 | 79.57% | 2 | 18600 | R-454B
212626849 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9E080B12MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626898 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8E060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
213753384 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 59SC2E080M21**20 | 29400 | 15.5 | 8.9 | 8.5 | 33400 | 23800 | 71.26% | 2.79 | 23200 | R-410A
213781175 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4321AL*+UI | 58TN*B090C17**16 | 33000 | 17 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
213273374 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Z8ES080C20SMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213278590 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D26+JMET12BS2N1+TDR |  | 32000 | 17.5 | 8.6 | 8.1 | 36000 | 26000 | 72.22% | 2.8 | 25200 | R-410A
213274512 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | CP9C100C20MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.14 | 30600 | R-410A
213274544 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM9E080C20MP12 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.11 | 31000 | R-410A
211206951 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | TM8V120C20MP12 | 43500 | 19 | 12 | 9 | 44500 | 36200 | 81.35% | 2.14 | 41500 | R-410A
213612029 | 1.83 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R802V0503A14DZ | 22000 | 15.4 | 11.7 | 8.1 | 22800 | 16200 | 71.05% | 2.8 | 15800 | R-410A
216687162 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF92SV307017M4 | 22800 | 20 | 12 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
216687189 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF80TV405017UH | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
213753368 | 2.42 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 59SC2E080M17**16 | 29000 | 15.5 | 8.9 | 8.1 | 33200 | 24000 | 72.29% | 2.79 | 23200 | R-410A
213612059 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R962V0703A17M4S | 32800 | 15.4 | 10 | 8.1 | 33800 | 26400 | 78.11% | 2.79 | 24800 | R-410A
213274571 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TP9C100C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213279272 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM9Y100C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213279274 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM9Y120D20MP11 | 43000 | 16 | 11 | 8.2 | 44000 | 31400 | 71.36% | 3.11 | 30600 | R-410A
216770038 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9V2C100U5PSC | 43000 | 16 | 12 | 8.7 | 44000 | 32400 | 73.64% | 2.2 | 29400 | R-454B
213273376 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D24+TDR | Z8ES080C20SMPS1 | 32000 | 16.5 | 8.6 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
216687178 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF97MV307017DH | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
214328325 | 3.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,A,DG49960 | WUV070T4BA | 46000 | 17 | 10 | 8.5 | 48000 | 34600 | 72.08% | 1.8 | 32000 | R-410A
214802751 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)30B34+TDR | R801V0504A17UHU | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.63 | 21000 | R-410A
214802936 | 3.79 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D44+TDR | R801V1005A21UHU | 45500 | 15.5 | 10.2 | 8.4 | 46000 | 34000 | 73.91% | 3.12 | 36400 | R-410A
215375218 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R801V0755A21UHS | 44000 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375236 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R801V1005A21UHU | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375261 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R802V0755A21UHS | 45500 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375293 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R802V1505A24UHS | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375300 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R921V0855A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
215375311 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R951V0705A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
215375077 | 1.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0504A17UHU | 21400 | 17 | 10 | 8.1 | 22400 | 19000 | 84.82% | 2 | 17000 | R-410A
216794338 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | *DHMB060CCV3+LRP | 32600 | 19.2 | 11.7 | 9 | 33800 | 32400 | 95.86% | 2.73 | 39500 | R-454B
216794231 | 1.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | *DHMB060CCV3+LRP | 19800 | 20.9 | 11.2 | 10 | 23200 | 22200 | 95.69% | 2.93 | 27200 | R-454B
216794240 | 1.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | L8V1A040U3VSB+LRP | 19800 | 21.2 | 11.2 | 10 | 22400 | 22000 | 98.21% | 2.95 | 27200 | R-454B
213274575 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TPLC100C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213279254 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM8Y080C16MP11 | 43000 | 16 | 11.5 | 8.2 | 44500 | 31600 | 71.01% | 3.11 | 30800 | R-410A
213782185 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 59TN6C100C21**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31400 | R-410A
215399922 | 2.53 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR |  | 30400 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.54 | 27000 | R-454B
212626674 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E060A10MP12 | 32400 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626788 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626822 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM8E100B12MP11 | 31600 | 17.9 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
216794397 | 2.53 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B040D3VSB+LRP | 30400 | 17.5 | 11 | 9 | 31800 | 30000 | 94.34% | 2.77 | 36600 | R-454B
216797064 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | *UHMB060CCV3+LRP | 30200 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.73 | 38000 | R-454B
216797105 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B060U3VSB+LRP | 29800 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.63 | 37600 | R-454B
216797114 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B080U4PSC+LRP | 30200 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.72 | 37600 | R-454B
215375316 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R951V0855A21M4S | 45500 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25800 | R-410A
216797148 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S8V2C080M5PDB | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.84 | 51500 | R-454B
213274515 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | CPLC100C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213274533 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM8V100C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213274564 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TMLE120C16MP11 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
215565302 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM8Y080B12MP11 | 22200 | 17 | 12 | 9 | 23000 | 18300 | 79.57% | 2 | 18600 | R-454B
215565283 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
213273368 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Z8ES080C20LMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
215565250 | 2.53 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4J+TDR |  | 30400 | 15.2 | 10 | 8.1 | 31000 | 31600 | 101.9% | 2.54 | 27000 | R-454B
214521990 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z9ES100C20SMPS1 | 31800 | 17.5 | 9.4 | 8.4 | 33200 | 27400 | 82.53% | 2.65 | 25200 | R-410A
216797155 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S8V2D120M5PDB | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.83 | 50500 | R-454B
216797166 | 3.75 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2C100D4VSB+LRP | 45000 | 18 | 10 | 8.1 | 45000 | 45000 | 100% | 2.59 | 51000 | R-454B
216770106 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TAM5D05AC31 |  | 33400 | 17.1 | 12 | 8.7 | 33000 | 24200 | 73.33% | 2.16 | 21400 | R-454B
214328314 | 1.83 | Yes | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | H,A,DG34936 | WPV060T3AA | 22000 | 17 | 10 | 8.5 | 23400 | 17100 | 73.08% | 1.8 | 14000 | R-410A
216770056 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD008AS3 | S9V2D120U5PSC | 43000 | 16.5 | 12 | 9 | 44500 | 32400 | 72.81% | 2.23 | 29600 | R-454B
216794481 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S8V2B060M4PCB | 42000 | 19.2 | 11.7 | 9.5 | 46500 | 42500 | 91.4% | 2.81 | 51000 | R-454B
215849883 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8V080B12MP12 | 22400 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
215849892 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM8Y060A12MP11 | 20800 | 17.5 | 10.5 | 9 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
215849901 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | TM8Y080B12MP11 | 22200 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
215850026 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | TM9Y060B12MP11 | 22400 | 17 | 11.7 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18600 | R-454B
215565280 | 3.38 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | TM8V100C16MP12 | 40500 | 17 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
214625027 | 2.33 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)42D24+TDR |  | 28000 | 15.2 | 10.3 | 9.5 | 22800 | 27000 | 118.4% | 1.85 | 22600 | R-410A
213753814 | 2.88 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC6A140M24**22 | 34600 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
214625020 | 1.29 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ18AB3 | D(A,C,E)24A24+TDR |  | 15500 | 15.2 | 11 | 9.3 | 14700 | 15000 | 102% | 2.2 | 14700 | R-410A
214521922 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES080C20LMPS1 | 32200 | 18 | 9.9 | 8.5 | 33200 | 28200 | 84.94% | 2.71 | 25600 | R-410A
214521931 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100B12SMPS1 | 32200 | 18.5 | 9.4 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
214521954 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ES120C20SMPS1 | 31800 | 17.5 | 9.4 | 8.4 | 33800 | 27800 | 82.25% | 2.64 | 25600 | R-410A
214521963 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ET100C16LMPS1 | 31800 | 17.9 | 9.4 | 8.4 | 33200 | 27800 | 83.73% | 2.68 | 25400 | R-410A
212624004 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9Y080B12MP11 | 31000 | 17.8 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624020 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624061 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | CPLC060A12MP13 | 32400 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
214802923 | 3.71 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48D34+TDR | R801V1005A21UHN | 44500 | 15.5 | 10 | 8.2 | 45500 | 33600 | 73.85% | 3.03 | 36000 | R-410A
213612054 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R802V0754A17DZ | 32800 | 15.4 | 10 | 8.1 | 33800 | 26400 | 78.11% | 2.78 | 24800 | R-410A
213781475 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**6024AL*+UI | 58TN*B110C21**20 | 32800 | 17.5 | 11.5 | 8.1 | 31800 | 24600 | 77.36% | 1.98 | 30800 | R-410A
216973037 | 4.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | PL60H210P17*+TXV | 59TN6C100C21**22 | 55500 | 18 | 11 | 8.5 | 58500 | 46000 | 78.63% | 2.02 | 47000 | R-454B
213274528 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM8E100C20MP11 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.11 | 31000 | R-410A
213274562 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TMLE100C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213274567 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TMLV100C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213274521 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TL9E080C16UH11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.11 | 30600 | R-410A
212624086 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8V060A12MP12 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624088 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8V060A12MP12 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624113 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TMLV060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624120 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TPLC060A12MP13 | 32400 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624177 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624218 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8E040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624261 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TMLE080C16MP11 | 31800 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624402 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM9Y080C16MP11 | 33000 | 18.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216770072 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD008AS3 | S8X1D120M5PTC | 51500 | 16 | 11 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34400 | R-454B
215375359 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R802V1005A21DZ | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
215375082 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V1004A17UH | 21600 | 17 | 10 | 8.1 | 22600 | 18800 | 83.19% | 2.1 | 16800 | R-410A
215375091 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R802V1004A17UHN | 21600 | 17 | 10 | 8.1 | 22600 | 18900 | 83.63% | 2.1 | 16800 | R-410A
213279280 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TMLE100C20MP11 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.11 | 31000 | R-410A
213274518 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TL8E080C16UH11 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
212627093 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TP9C080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627143 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TL9E080C16UH11 | 32200 | 17.5 | 9.4 | 8.5 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
212627154 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM9V100C16MP12 | 29200 | 16.7 | 9.4 | 8.5 | 33800 | 27200 | 80.47% | 2.67 | 25200 | R-410A
212627170 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | CP9C100C20MP13 | 31600 | 17.5 | 9.3 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
216796753 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X2B040D3PSB | 31400 | 15.5 | 11.7 | 8.1 | 32200 | 22600 | 70.19% | 2.85 | 22200 | R-454B
212627245 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627247 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627252 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TL9E060B12UH11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627288 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9E060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627313 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CP9C060B12MP13 | 29400 | 16.7 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627320 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | CP9C060B12MP13 | 33000 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627361 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TP9C060B12MP13 | 29800 | 16.9 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212625323 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
213279228 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | CP9C100C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
211708439 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM8E120C16MP11 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
211708440 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM8E120C20MP11 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31200 | 70.11% | 3.07 | 30600 | R-410A
214521914 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES080C16LMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
214521928 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100B12LMPS1 | 32200 | 18.5 | 9.4 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
213279281 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TMLE120C16MP11 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213278588 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D24+JMVT12BC2N1+TDR |  | 32000 | 17.5 | 8.6 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
214625028 | 2.88 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)36A34+TDR |  | 34600 | 15.2 | 10 | 8.6 | 27400 | 31600 | 115.3% | 1.85 | 27400 | R-410A
212625364 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | CP9C100C20MP13 | 30800 | 17.3 | 9.2 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625391 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625464 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TP9C100C20MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625509 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | CPLC100C20MP13 | 28600 | 15.6 | 8.4 | 8.1 | 32000 | 27600 | 86.25% | 2.44 | 25000 | R-410A
212625600 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TPLC100C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625664 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625691 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625707 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8V100C20MP12 | 32400 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625709 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8V100C20MP12 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625723 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8V120C20MP12 | 30000 | 16 | 8.6 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625748 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLV120C20MP12 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625768 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625784 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625841 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CP9C120D20MP13 | 32400 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625848 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | CP9C120D20MP13 | 30200 | 16.5 | 9.1 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625859 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9V120D20MP12 | 32600 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625868 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9V120D20MP12 | 30200 | 16.5 | 9.1 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212625925 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9V040A10MP12 | 30000 | 16.6 | 9.1 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212626034 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212626052 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TL9E100C20UH11 | 31000 | 17 | 9.8 | 8.1 | 33400 | 28800 | 86.23% | 2.71 | 26000 | R-410A
212626066 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8Y080B12MP11 | 32200 | 18 | 9.9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626077 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8Y080B12MP11 | 32600 | 18 | 10 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626241 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8E100C16MP11 | 31800 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626286 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.1 | 33600 | 28600 | 85.12% | 2.67 | 26000 | R-410A
212626341 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626402 | 2.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9E100C16MP12 | 33600 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626416 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM8Y120C20MP11 | 31200 | 17.9 | 9.3 | 8.4 | 33600 | 30000 | 89.29% | 2.83 | 26800 | R-410A
212626425 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 33600 | 28200 | 83.93% | 2.46 | 25800 | R-410A
212626600 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.68 | 25800 | R-410A
212626661 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9E060A10MP12 | 30600 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626668 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9E060A10MP12 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.4 | 25400 | R-410A
212626686 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.2 | 33800 | 28200 | 83.43% | 2.68 | 25800 | R-410A
212626700 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.71 | 26000 | R-410A
212626868 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
212626909 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626943 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TMLE060A12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626961 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TMLE100B12MP11 | 30400 | 17.5 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626984 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
212626995 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TL8E080C16UH11 | 31800 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212627027 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM9V100C16MP12 | 31800 | 17.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
212627036 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | CP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627043 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627063 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9V080C16MP12 | 30400 | 17 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627086 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TP9C080C16MP13 | 30400 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212624571 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8V080C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624664 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TMLV100C16MP12 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624671 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TMLV100C16MP12 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624673 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TMLV100C16MP12 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624689 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TPLC080C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624723 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624730 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624755 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TL9E080C16UH11 | 29200 | 16.7 | 8.9 | 8.5 | 34000 | 27800 | 81.76% | 2.65 | 25600 | R-410A
212624780 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TL8E080C16UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624855 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.4 | 34000 | 30200 | 88.82% | 2.83 | 27000 | R-410A
212624864 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM9V100C16MP12 | 29800 | 16.9 | 9.5 | 8.5 | 34000 | 27000 | 79.41% | 2.66 | 25200 | R-410A
212624896 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | CP9C100C16MP13 | 32600 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624973 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM8Y100C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624996 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8Y100C16MP11 | 33000 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625016 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8Y100C16MP11 | 33200 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625114 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625155 | 2.67 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TL9E100C20UH11 | 32000 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625205 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625216 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212624503 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | CPLC100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624537 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624153 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9V080B12MP12 | 32800 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624178 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624180 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM9Y100C20MP11 | 32400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624196 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9Y100C16MP11 | 31600 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624314 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLE100C16MP11 | 32200 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624346 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B34+TDR | TM8V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212624387 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627997 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9V100C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627999 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9V100C16MP12 | 33400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628113 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9V100C20MP12 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
214625035 | 1.72 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ24AB3 | D(A,C,E)24A24+TDR |  | 20600 | 15.2 | 10 | 9.3 | 21000 | 20000 | 95.24% | 1.95 | 21000 | R-410A
212627486 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.72 | 26000 | R-410A
212627495 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212627520 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212627522 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9V080B12MP12 | 31800 | 17 | 9 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212627531 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212627536 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627547 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9Y100C20MP11 | 32800 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627572 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8E040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212627597 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212627645 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624428 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM8E120C16MP11 | 32400 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624439 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLE120C16MP11 | 32400 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212624462 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM8Y100C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212624478 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | CPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624489 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624028 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TMLE080B12MP11 | 30200 | 17.5 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624110 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLV060A12MP12 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212628090 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CP9C100C20MP13 | 33000 | 17.5 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627663 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9Y080C16MP11 | 30600 | 18.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627681 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8Y080C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627695 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627915 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | CP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627922 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | CP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212627931 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8Y080C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627949 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y080C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627954 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8Y100C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
211708472 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TM9E100C20MP12 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
214056957 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE(D,N,U)+DM36A36+TDR |  | 31400 | 18.3 | 10.3 | 8.4 | 33000 | 26200 | 79.39% | 2.65 | 24400 | R-410A
212624000 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9Y080B12MP11 | 33200 | 18 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
211708473 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TM9E100C20MP12 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
211708506 | 3.83 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TMLE100C20MP11 | 46000 | 16 | 11.9 | 8.2 | 44500 | 31600 | 71.01% | 3.08 | 30800 | R-410A
211708508 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D34+TDR | TMLE120C16MP11 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
211708525 | 3.79 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)48D36+TDR | TP9C100C20MP13 | 45500 | 16 | 11.9 | 8.2 | 44000 | 31200 | 70.91% | 3.13 | 30400 | R-410A
212624014 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TMLE080B12MP11 | 30200 | 17.5 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627965 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8Y100C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627974 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8Y100C16MP11 | 33200 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627981 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627990 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627711 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | CPLC080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627756 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8V080C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627790 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TMLV100C16MP12 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627795 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212625085 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9V100C16MP12 | 33400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625137 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625167 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212625187 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8Y100C20MP11 | 32200 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625320 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212625334 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625421 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9V100C20MP12 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625554 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | CPLC120C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625603 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TPLC120C20MP13 | 31600 | 16.5 | 8.9 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212625618 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | CP9C120D20MP13 | 31200 | 16.8 | 9.3 | 8.1 | 32200 | 28000 | 86.96% | 2.51 | 25200 | R-410A
212625621 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9V120D20MP12 | 31200 | 16.8 | 9.3 | 8.5 | 32200 | 28000 | 86.96% | 2.79 | 25200 | R-410A
212625705 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625752 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLV120C20MP12 | 32600 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625753 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLV120C20MP12 | 32000 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625771 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TPLC100C20MP13 | 32600 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625772 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC100C20MP13 | 32000 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
213753816 | 2.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC6A140M24**22 | 35000 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
214625045 | 2.82 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)48C24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 27600 | 31600 | 114.5% | 1.85 | 27400 | R-410A
215850276 | 2.62 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 31400 | 18 | 10.5 | 8.5 | 31600 | 25600 | 81.01% | 2 | 28000 | R-454B
215850117 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C080B12MP13 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
215850187 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24C3K+TDR | Z9ES026A08SMPS1 | 20800 | 17.5 | 11 | 8.5 | 23000 | 17300 | 75.22% | 2 | 17700 | R-454B
215850194 | 1.68 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z9ES060A10SMPS1 | 20200 | 17.5 | 11.2 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18000 | R-454B
212625788 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TPLC120C20MP13 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625805 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9Y120D20MP11 | 31600 | 16.5 | 9.3 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625839 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | CP9C120D20MP13 | 32600 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625919 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625920 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9V040A10MP12 | 32000 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625936 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM8Y080B12MP11 | 30000 | 17.4 | 9.5 | 8.3 | 33200 | 27400 | 82.53% | 2.6 | 25200 | R-410A
212625937 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A36+TDR | TM8Y080B12MP11 | 32000 | 17.9 | 9.9 | 8.3 | 33200 | 27400 | 82.53% | 2.62 | 25200 | R-410A
212625952 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9E100C20MP12 | 32400 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212626055 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8Y080B12MP11 | 32400 | 18 | 9.9 | 8.4 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
212626071 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8Y080B12MP11 | 32200 | 18 | 9.9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626239 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212626339 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626357 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A36+TDR | TL9E080C16UH11 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.62 | 25600 | R-410A
212626371 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TM9V080C16MP12 | 29400 | 16.7 | 9.4 | 8.4 | 33600 | 27600 | 82.14% | 2.64 | 25400 | R-410A
212626421 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 33600 | 28200 | 83.93% | 2.46 | 25800 | R-410A
212626423 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM9V100C20MP12 | 30000 | 17 | 9 | 8.5 | 33600 | 28200 | 83.93% | 2.7 | 25800 | R-410A
212626640 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9V080B12MP12 | 31400 | 17 | 9.5 | 8.3 | 33800 | 29200 | 86.39% | 2.67 | 26400 | R-410A
212626741 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM9Y100C16MP11 | 32000 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626789 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
212626840 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9E080B12MP12 | 33000 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626841 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9E080B12MP12 | 32600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626858 | 2.68 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8E100C16MP11 | 32200 | 18 | 10 | 8.4 | 33800 | 28600 | 84.62% | 2.72 | 26000 | R-410A
212626922 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8E100B12MP11 | 33200 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626939 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TMLE060A12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626972 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TMLE100B12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212627023 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM8Y080C16MP11 | 31800 | 18.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
212627042 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627055 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9V080C16MP12 | 32200 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627059 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627072 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM9V080C16MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627074 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9V080C16MP12 | 31200 | 17.3 | 9.7 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627108 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30200 | 89.35% | 2.82 | 27000 | R-410A
212627123 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM9Y080C16MP11 | 32200 | 18.5 | 9.4 | 8.5 | 33800 | 28200 | 83.43% | 2.67 | 25800 | R-410A
212627124 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TL9E100C20UH11 | 31000 | 17 | 9.8 | 8.4 | 33800 | 28800 | 85.21% | 2.79 | 26200 | R-410A
212627156 | 2.63 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TL9E100C20UH11 | 31600 | 17 | 9.9 | 8.5 | 33800 | 28800 | 85.21% | 2.81 | 26200 | R-410A
212627174 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9V100C20MP12 | 31600 | 17.5 | 9.3 | 8.5 | 33800 | 28200 | 83.43% | 2.7 | 25800 | R-410A
212627257 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TL9E060B12UH11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627258 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TL9E060B12UH11 | 33000 | 18 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627376 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627426 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8E080B12MP11 | 32400 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212628124 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628129 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627765 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627770 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627781 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8V100C16MP12 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627797 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TMLV100C16MP12 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627806 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLV100C16MP12 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627813 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627441 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9Y080B12MP11 | 29400 | 17.2 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627493 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.75 | 26000 | R-410A
212627557 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212627574 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TMLE040A12MP11 | 32000 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212627575 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212627592 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.77 | 26200 | R-410A
212627608 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212627624 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627708 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627709 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | CPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627726 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627727 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627757 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627826 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627844 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TPLC100C16MP13 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627861 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TL9E080C16UH11 | 30000 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.65 | 25600 | R-410A
212627879 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL8E080C16UH11 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627906 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.4 | 34000 | 30200 | 88.82% | 2.83 | 27000 | R-410A
212627940 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627947 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8Y080C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627972 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8Y100C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627988 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9V100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628038 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8Y120C20MP11 | 32600 | 18 | 9 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628072 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9V100C20MP12 | 30000 | 17 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.69 | 25800 | R-410A
212627891 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TL9E080C16UH11 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627928 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CP9C100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624502 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | CPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624616 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624617 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624649 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLV100C16MP12 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624652 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLV100C16MP12 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624668 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TMLV100C16MP12 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212628074 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212628079 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627670 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212627713 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CPLC080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627715 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CPLC080C16MP13 | 33400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627720 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | CPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627731 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | CPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627747 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624685 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624732 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624834 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TL9E080C16UH11 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624849 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TL9E080C16UH11 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624852 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TL9E080C16UH11 | 33400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624903 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8Y080C16MP11 | 29200 | 17.7 | 9.4 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624950 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM8Y080C16MP11 | 32600 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624983 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625000 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625003 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8Y100C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625051 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625069 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM9V100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625083 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9V100C16MP12 | 31000 | 17.3 | 9.7 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624067 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | CPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624083 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8V060A12MP12 | 31600 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624098 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM8V060A12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624131 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | CP9C080B12MP13 | 31400 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624147 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9V080B12MP12 | 32200 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624201 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624214 | 2.63 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8E040A12MP11 | 31600 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624217 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8E040A12MP11 | 32400 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624234 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLE040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212624249 | 2.65 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM8E080C16MP11 | 31800 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212624267 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE080C16MP11 | 32600 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212627363 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627370 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TP9C060B12MP13 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627377 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627445 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9Y080B12MP11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627463 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627470 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627472 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TMLE080B12MP11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627481 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLE080B12MP11 | 32600 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627131 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.4 | 33800 | 27200 | 80.47% | 2.64 | 25200 | R-410A
212627232 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212627249 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TL9E060B12UH11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627281 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9E060B12MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627283 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9E060B12MP12 | 30400 | 17 | 9.1 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627333 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | CP9C060B12MP13 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627349 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM9V060B12MP12 | 30400 | 17 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627383 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8E080B12MP11 | 32200 | 18 | 9.4 | 8.4 | 34000 | 28000 | 82.35% | 2.6 | 25800 | R-410A
212627417 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8E080B12MP11 | 32000 | 18 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627448 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9Y080B12MP11 | 33000 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627602 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.76 | 26000 | R-410A
212627649 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9Y080C16MP11 | 30600 | 18.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627650 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627667 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8E120C16MP11 | 32400 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212627717 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CPLC100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627718 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | CPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627733 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CPLC100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627750 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8V080C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627751 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627984 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627985 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9V100C16MP12 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214521907 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES040A12SMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
214521941 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES100C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
214521943 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100C20SMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
212626900 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8E060A12MP11 | 32800 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626913 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8E100B12MP11 | 33000 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626916 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8E100B12MP11 | 33000 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212626931 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TMLE060A12MP11 | 30000 | 17.4 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626999 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM8V100C16MP12 | 31800 | 17.5 | 9.9 | 8.3 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212627015 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A36+TDR | TM9Y080C16MP11 | 31800 | 18.5 | 9.4 | 8.4 | 33800 | 27800 | 82.25% | 2.64 | 25600 | R-410A
212627049 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | CP9C080C16MP13 | 30800 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627065 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9V080C16MP12 | 32600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627084 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TP9C080C16MP13 | 33000 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
214802737 | 1.83 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R801V1004A17UHS | 22000 | 16.3 | 11.8 | 8.1 | 22800 | 16200 | 71.05% | 2.96 | 16900 | R-410A
214521933 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ES100C16LMPS1 | 31800 | 17.9 | 9.4 | 8.4 | 33200 | 28200 | 84.94% | 2.68 | 25600 | R-410A
214521950 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES120C20LMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.64 | 25600 | R-410A
214521984 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z9ES080C20SMPS1 | 31800 | 17.5 | 9.4 | 8.4 | 33200 | 27400 | 82.53% | 2.65 | 25200 | R-410A
212627097 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TP9C080C16MP13 | 31200 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627099 | 2.67 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TL9E100C20UH11 | 32000 | 17 | 10 | 8.3 | 33800 | 28800 | 85.21% | 2.77 | 26200 | R-410A
212627116 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B26+TDR | TL8E080C16UH11 | 30200 | 17 | 9 | 8.4 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627147 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8Y100C20MP11 | 32600 | 18 | 9 | 8.4 | 33800 | 30000 | 88.76% | 2.83 | 26800 | R-410A
212627149 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8Y120C20MP11 | 32600 | 18 | 9 | 8.4 | 33800 | 30000 | 88.76% | 2.83 | 26800 | R-410A
212627231 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212627248 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TL9E060B12UH11 | 30200 | 17.5 | 9.1 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627250 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL9E060B12UH11 | 32400 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212624281 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9E080C16MP12 | 31800 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.49 | 26200 | R-410A
212624316 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE100C16MP11 | 32600 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624383 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM9Y080C16MP11 | 29200 | 17.7 | 8.9 | 8.5 | 34000 | 27800 | 81.76% | 2.66 | 25600 | R-410A
212624384 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624400 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624448 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | CPLC100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27200 | 80.47% | 2.48 | 25200 | R-410A
212624449 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM8V080C16MP12 | 29800 | 16.9 | 9.5 | 8.5 | 34000 | 27000 | 79.41% | 2.67 | 25200 | R-410A
213273410 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Z8ES100C20SMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
212627840 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627845 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627863 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627888 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TL9E080C16UH11 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627704 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | CPLC080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627706 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
214320269 | 2.67 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | C(A,C,E)37C24+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
214392641 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | U802VA075317M | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
213753694 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B110M21**20 | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
213753710 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 58S(B,C)*B155M24**20 | 35400 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213753728 | 2.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58TP*B090V17**16 | 34400 | 16.5 | 9.9 | 8.1 | 38500 | 31800 | 82.6% | 2.67 | 29200 | R-410A
213753760 | 2.85 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC2E080M17**16 | 34200 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.74 | 29000 | R-410A
213753844 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SP6A120V24**22 | 35200 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
213753878 | 2.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59TP6C100V21**22 | 35200 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213274546 | 3.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM9E100C20MP12 | 43500 | 16 | 11 | 8.3 | 45000 | 31600 | 70.22% | 3.11 | 31000 | R-410A
213279231 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | CPLC080C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213278565 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+JMET12CS2N1+TDR |  | 31600 | 17.5 | 9.3 | 8.5 | 32600 | 28000 | 85.89% | 2.79 | 25400 | R-410A
212506622 | 2.92 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M36E4 |  | 35000 | 18 | 9 | 8.1 | 35400 | 26000 | 73.45% | 2.82 | 25400 | R-410A
214320267 | 1.92 | Yes | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | D(A,C,E)25B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215565323 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z9ES040A10SMPS1 | 20800 | 17.5 | 11.7 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18400 | R-454B
213753875 | 2.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59TP6C100V21**22 | 34800 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
212627986 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM9V100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628003 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TP9C100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628016 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628018 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TP9C100C16MP13 | 32600 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628052 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TL8E100C20UH11 | 33000 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628084 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628102 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
214625031 | 2.82 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)48C24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 27600 | 31600 | 114.5% | 1.85 | 27400 | R-410A
214625034 | 1.29 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ18AB3 | D(A,C,E)24A24+TDR |  | 15500 | 15.2 | 11 | 9.3 | 14700 | 15000 | 102% | 2.2 | 14700 | R-410A
214521917 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES080C16SMPS1 | 31200 | 17.8 | 9.8 | 8.3 | 33000 | 27600 | 83.64% | 2.68 | 25200 | R-410A
214521932 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES100C16LMPS1 | 31200 | 17.8 | 9.3 | 8.3 | 33000 | 28200 | 85.45% | 2.66 | 25600 | R-410A
214521966 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | Z8ET100C20LMPS1 | 31800 | 18.5 | 9.4 | 8.4 | 33200 | 27400 | 82.53% | 2.68 | 25200 | R-410A
214521967 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ET100C20LMPS1 | 32200 | 18.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
214521968 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ET120C20LMPS1 | 31200 | 18.3 | 9.3 | 8.3 | 33000 | 27800 | 84.24% | 2.66 | 25400 | R-410A
215565311 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TMLE080B12MP11 | 22400 | 17 | 12 | 9 | 23000 | 18000 | 78.26% | 2 | 18400 | R-454B
216055585 | 1.7 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z8ES040A12SMPS1 | 20400 | 17.5 | 11.2 | 9.5 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216055635 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z9ES060A10SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
216055421 | 1.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TL8E060A12UH11 | 20000 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
216055451 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055469 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8Y080B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216055471 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8Y080B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216055502 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9E080B12MP12 | 22600 | 17 | 11.7 | 8.5 | 22600 | 18700 | 82.74% | 2 | 18800 | R-454B
213753607 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30B34+TDR | 59TP6C100V21**20 | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
213753625 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 59TP6C100V21**22 | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
213753650 | 2.88 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B070M14**12 | 34600 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.63 | 29400 | R-410A
213753750 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SC2E060M14**12 | 35000 | 15.5 | 9.5 | 8.1 | 38500 | 32400 | 84.16% | 2.51 | 29600 | R-410A
213753789 | 2.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC6A080M17**16 | 34400 | 16 | 9.9 | 8.1 | 38500 | 31800 | 82.6% | 2.68 | 29200 | R-410A
214320270 | 3.92 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | C(A,C,D,E)48C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
216797097 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B040U3PSC+LRP | 29600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.68 | 37800 | R-454B
212627284 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212627331 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | CP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
213753768 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC2E100M21**20 | 35000 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
214320272 | 3.92 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | D(A,C,E)61C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
216055459 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8V080B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055527 | 1.75 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.1 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216055528 | 1.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9Y040A10MP11 | 21200 | 17 | 10.5 | 8.1 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216055544 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
215850196 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR | Z9ES060A10SMPS1 | 20800 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18100 | R-454B
213927953 | 2.43 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)42B44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213927960 | 2.4 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)37A44+TDR |  | 28800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
214625047 | 2.82 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)42D24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 27600 | 31600 | 114.5% | 1.85 | 27400 | R-410A
214320268 | 2.67 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
213279249 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM8V080C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
216055536 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9Y080B12MP11 | 21000 | 17 | 11.2 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18600 | R-454B
216055554 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE080B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
214802898 | 3.67 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | D(A,C,E)48B44+TDR | R801V0755A21UH | 44000 | 15.4 | 10 | 8.1 | 45500 | 34000 | 74.73% | 3.03 | 36600 | R-410A
214320276 | 4.21 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | C(A,C,D,E)60C44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
213927961 | 2.43 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)43A44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213927968 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)31C44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
212627554 | 2.78 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9Y100C20MP11 | 33400 | 15.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627579 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212627622 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8V100C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627647 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM9Y080C16MP11 | 29600 | 17.8 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216797091 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S8V2C100M5PCB | 29800 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.83 | 37800 | R-454B
213274527 | 3.54 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM8E100C16MP11 | 42500 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.13 | 30600 | R-410A
213273375 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A46+TDR | Z8ES080C20SMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
214320266 | 1.92 | Yes | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | C(A,C,D,E)24B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
214625059 | 2.82 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)48C24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 27600 | 31600 | 114.5% | 1.85 | 27400 | R-410A
213279267 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM9V100C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213207092 | 2.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A090E21**16 | 34600 | 16 | 9.8 | 8.1 | 39000 | 31200 | 80% | 2.74 | 29000 | R-410A
216797107 | 2.48 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B060U4PSC+LRP | 29800 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.67 | 37600 | R-454B
213278567 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+JMET12CS2N1+TDR |  | 31600 | 17.5 | 9.3 | 8.5 | 32600 | 28000 | 85.89% | 2.79 | 25400 | R-410A
212506617 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36E4 |  | 32400 | 17 | 10 | 8.5 | 32000 | 28000 | 87.5% | 2.88 | 25200 | R-410A
213286707 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | CE3005A+TXV |  | 29800 | 15.2 | 8.5 | 8.2 | 33200 | 27000 | 81.33% | 1.78 | 22600 | R-410A
214625041 | 2.33 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)42D24+TDR |  | 28000 | 15.2 | 10.3 | 9.5 | 22800 | 27000 | 118.4% | 1.85 | 22600 | R-410A
214625042 | 2.88 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)36A34+TDR |  | 34600 | 15.2 | 10 | 8.6 | 27400 | 31600 | 115.3% | 1.85 | 27400 | R-410A
214625056 | 2.88 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)36A34+TDR |  | 34600 | 15.2 | 10 | 8.6 | 27400 | 31600 | 115.3% | 1.85 | 27400 | R-410A
212626823 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8E100B12MP11 | 32400 | 18 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212626908 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8E100B12MP11 | 30000 | 17.4 | 9.5 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
214625050 | 2.35 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)30A34+TDR |  | 28200 | 15.2 | 10.3 | 9.5 | 22600 | 27000 | 119.5% | 1.85 | 22600 | R-410A
214625052 | 2.33 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)30B34+TDR |  | 28000 | 15.4 | 10.3 | 9 | 32400 | 27000 | 83.33% | 1.85 | 22400 | R-410A
216055892 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055899 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y120C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055917 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V080C16MP12 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055965 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLV120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
213753872 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59TP6C100V21**20 | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.61 | 29400 | R-410A
214320271 | 3.92 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | C(A,C,D,E)48D44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
213927965 | 2.48 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)43D34+TDR |  | 29800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213613386 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24I4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213613387 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24J4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213752633 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58S(B,C)*B045M14**12 | 23400 | 17 | 10 | 8.5 | 27000 | 20400 | 75.56% | 2.88 | 19400 | R-410A
213752650 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*B070M17**12 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.86 | 19000 | R-410A
213752666 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M17**16 | 23000 | 17.5 | 10.3 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213752751 | 1.88 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*B070V17**16 | 22600 | 17.4 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
213752768 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58TP*B090V21**20 | 23600 | 17 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.92 | 19100 | R-410A
213752832 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC2E080M21**20 | 23200 | 17.4 | 10.3 | 8.5 | 25600 | 20200 | 78.91% | 3 | 18900 | R-410A
213752835 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2E100M21**20 | 23400 | 17.5 | 10.5 | 8.5 | 26400 | 20200 | 76.52% | 2.88 | 19100 | R-410A
213752850 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC6A026M14**10 | 23200 | 16.5 | 10 | 8.5 | 27000 | 20600 | 76.3% | 2.86 | 19500 | R-410A
214320265 | 1.92 | Yes | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | D(A,C,E)24D34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215565328 | 3.46 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)61A3J+TDR | TL8E080C16UH11 | 41500 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
214625051 | 2.38 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)36A34+TDR |  | 28600 | 15.2 | 10.4 | 9.5 | 22600 | 27000 | 119.5% | 1.85 | 22600 | R-410A
216797084 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S8V2B080M4PCB | 30200 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.68 | 38000 | R-454B
214320263 | 1.92 | Yes | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | D(A,C,E)24A44+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
213612056 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ36AJ2N | D(A,C,E)36A34+TDR | R802V1004A17UH | 33000 | 15.4 | 11.7 | 8.1 | 34000 | 26400 | 77.65% | 2.78 | 24800 | R-410A
215289838 | 1.43 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32930 | *96MSN0401712A* | 17200 | 15.2 | 10 | 8.5 | 17100 | 18800 | 109.9% | 2.3 | 11500 | R-410A
213752676 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B070M21**16 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213752877 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC6A060M14**12 | 22600 | 16.8 | 9.8 | 8.4 | 25200 | 20000 | 79.37% | 2.92 | 18700 | R-410A
213752910 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SP6A040V14**10 | 23200 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.83 | 19000 | R-410A
215565255 | 1.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4J+TDR | TL8E060A12UH11 | 21000 | 17.5 | 11.2 | 9 | 22800 | 17900 | 78.51% | 2 | 18300 | R-454B
212480358 | 2.5 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | C36A***L159 | 59TP6B100V21**22 | 30000 | 15.2 | 9 | 8.1 | 32400 | 26800 | 82.72% | 1.8 | 22400 | R-410A
213279250 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TM8V100C16MP12 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
213279289 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TP9C100C20MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31400 | 71.36% | 3.14 | 30600 | R-410A
216794566 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2C100U4VSB+LRP | 42000 | 20 | 12 | 9.5 | 46500 | 42000 | 90.32% | 2.79 | 50000 | R-454B
213273407 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D26+TDR | Z8ES100C20LMPS1 | 32000 | 16 | 8.6 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213752369 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2E060M14**12 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.9 | 20200 | R-410A
213752394 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC2E080M17**16 | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.87 | 19800 | R-410A
213752405 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2E080M21**20 | 23400 | 16.5 | 9 | 8.1 | 24600 | 22200 | 90.24% | 2.88 | 19800 | R-410A
215940233 | 2.85 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0802120A* | 34200 | 19.5 | 11.7 | 9 | 34200 | 26000 | 76.02% | 1.96 | 30000 | R-454B
215565307 | 1.85 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM9Y060B12MP11 | 22200 | 17 | 11.7 | 9 | 23000 | 18400 | 80% | 2 | 18800 | R-454B
216776750 | 1.85 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | CM24C3K+TDR |  | 22200 | 15.2 | 11 | 8.1 | 22800 | 21200 | 92.98% | 2.76 | 18700 | R-454B
213927969 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)31E34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
216055884 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055907 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055909 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9E100C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055918 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9V080C16MP12 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055941 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055560 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE100B12MP11 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055561 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE100B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216055878 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8V080C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055895 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C20MP11 | 40000 | 17.5 | 11.2 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
214625037 | 2.38 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)36A34+TDR |  | 28600 | 15.2 | 10.4 | 9.5 | 22600 | 27000 | 119.5% | 1.85 | 22600 | R-410A
216055891 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y080C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055893 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216055900 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y120C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055923 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055925 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V120D20MP12 | 40000 | 17.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
213780125 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | CSPH*4212AL*+UI | 59TN6C120C24**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
215565284 | 3.42 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)49B3J+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216055980 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055994 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080C20SMPS1 | 40000 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216056045 | 3.42 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES100C16SMPS1 | 41000 | 17.5 | 10.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
216055894 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216056050 | 3.5 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES100C16SMPS1 | 42000 | 18 | 10.5 | 8.5 | 46500 | 34200 | 73.55% | 2 | 33800 | R-454B
216056059 | 3.5 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES100C20SMPS1 | 42000 | 17.5 | 11.5 | 8.1 | 46500 | 34000 | 73.12% | 2 | 33400 | R-454B
216055859 | 3.42 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E080C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055868 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8E120C16MP11 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34200 | 76% | 2 | 33600 | R-454B
216055916 | 3.29 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080C16MP12 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055968 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C080C16MP13 | 40500 | 17 | 10.5 | 8.5 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
215565294 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | CPLC080B12MP13 | 22400 | 17 | 12 | 9 | 23000 | 17700 | 76.96% | 2 | 18200 | R-454B
213753044 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59TP6C100V21**20 | 23200 | 17.5 | 10 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
214595151 | 2 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M364+TDR |  | 24000 | 15.2 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214595166 | 2 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36L4 |  | 24000 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
216055896 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055928 | 3.29 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080C16MP11 | 39500 | 16.5 | 10.5 | 8.1 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055929 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055930 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055577 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TPLC080B12MP13 | 21600 | 17 | 11.7 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055578 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TPLC080B12MP13 | 21200 | 17 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216055962 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLV100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
213752867 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC6A040M17**12 | 23000 | 16 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19200 | R-410A
213752902 | 1.88 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC6A080M21**20 | 22600 | 17.4 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 2.97 | 18700 | R-410A
213752918 | 1.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SP6A040V17**12 | 23000 | 16 | 9.5 | 8.5 | 25800 | 20200 | 78.29% | 2.83 | 19000 | R-410A
213752950 | 1.9 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SP6A080V17**16 | 22800 | 16.7 | 10 | 8.4 | 25600 | 19900 | 77.73% | 2.94 | 18700 | R-410A
214625023 | 2.38 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)36A34+TDR |  | 28600 | 15.2 | 10.4 | 9.5 | 22600 | 27000 | 119.5% | 1.85 | 22600 | R-410A
214595161 | 1.95 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36B4 |  | 23400 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214625055 | 2.33 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)42D24+TDR |  | 28000 | 15.2 | 10.3 | 9.5 | 22800 | 27000 | 118.4% | 1.85 | 22600 | R-410A
216055848 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
216055932 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216055998 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215565290 | 1.87 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR |  | 22400 | 15.2 | 11 | 8.5 | 23000 | 21400 | 93.04% | 2.83 | 18800 | R-454B
216055910 | 3.42 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E100C20MP12 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055947 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216055964 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLV120C20MP12 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055977 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055978 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055979 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC080C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055943 | 3.42 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216055973 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C20MP13 | 40000 | 17.5 | 10.5 | 8.1 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055975 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216055982 | 3.29 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216056000 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C20SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216056007 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES120C16SMPS1 | 41000 | 18 | 11.7 | 8.5 | 43000 | 33000 | 76.74% | 2 | 31600 | R-454B
216055995 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216055612 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ET060A12LMPS1 | 21000 | 19 | 11.7 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
213752926 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SP6A060V14**12 | 23200 | 16.5 | 10 | 8.5 | 26400 | 20400 | 77.27% | 2.86 | 19300 | R-410A
213752942 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SP6A060V17**14 | 23400 | 16.5 | 10 | 8.5 | 25800 | 20000 | 77.52% | 2.85 | 18900 | R-410A
213752993 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6C040V17**12 | 23000 | 16.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.84 | 19100 | R-410A
213753041 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6C080V21**20 | 23800 | 17 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
216055967 | 3.29 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216055992 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216057053 | 1.83 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR |  | 22000 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.67 | 18600 | R-454B
216056001 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z8ES100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
213752964 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SP6A080V21**20 | 23800 | 17 | 10 | 8.5 | 26000 | 20200 | 77.69% | 2.92 | 19000 | R-410A
213753057 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59TP6C100V21**22 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.94 | 19100 | R-410A
215848363 | 1.87 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24C3K+TDR |  | 22400 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.7 | 18700 | R-454B
214625021 | 1.72 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ24AB3 | D(A,C,E)24A24+TDR |  | 20600 | 15.2 | 10 | 9.3 | 21000 | 20000 | 95.24% | 1.95 | 21000 | R-410A
212627913 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628024 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212628029 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TL8E100C20UH11 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
212628047 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TL8E100C20UH11 | 29600 | 16.9 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628099 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628106 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212628122 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627895 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627897 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TL9E080C16UH11 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627379 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TP9C060B12MP13 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627404 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TL8E060A12UH11 | 32000 | 18 | 9 | 8.1 | 33400 | 29000 | 86.83% | 2.46 | 26200 | R-410A
212627420 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8E080B12MP11 | 29800 | 17.4 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627427 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM8E080B12MP11 | 30200 | 17.5 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627461 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9Y080B12MP11 | 31000 | 17.8 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627477 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TMLE080B12MP11 | 30200 | 17.5 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
214331698 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214331709 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M100C5A | 31200 | 18.5 | 11.9 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
213927967 | 2.43 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)31B44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
212627556 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8E100C16MP11 | 31400 | 18 | 9.9 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212627570 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8E040A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 29000 | 86.83% | 2.48 | 26200 | R-410A
212627588 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TMLE080C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212627604 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.76 | 26000 | R-410A
212627606 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212627672 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE120C16MP11 | 33200 | 18 | 10 | 8.1 | 33000 | 29200 | 88.48% | 2.5 | 26200 | R-410A
212627736 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CPLC100C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627738 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CPLC100C16MP13 | 33400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213613392 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36D4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213613393 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36E4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214802736 | 1.85 | Yes | Yes | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)36D24+TDR | R801V1004A17UHN | 22200 | 16.3 | 11.8 | 8.5 | 23200 | 16400 | 70.69% | 3.15 | 17100 | R-410A
214392711 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | U98MV0703A17UPS | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
212627740 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8V080C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627815 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627829 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TPLC080C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627838 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627854 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC100C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627052 | 2.8 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | CP9C080C16MP13 | 33600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627068 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM9V080C16MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
212627070 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
216055966 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TMLV120C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216055850 | 3.33 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL9E080C16UH11 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216055857 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8E080C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216687212 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF98MV510021UP | 45500 | 19 | 11.7 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
213927950 | 2.4 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)36B44+TDR |  | 28800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
212627077 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TP9C080C16MP13 | 29400 | 16.7 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
212627138 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A26+TDR | TMLV100C16MP12 | 29200 | 16.7 | 9.4 | 8.1 | 33800 | 27200 | 80.47% | 2.48 | 25200 | R-410A
212627161 | 2.63 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TL8E100C20UH11 | 31600 | 17.5 | 9.8 | 8.5 | 33800 | 27400 | 81.07% | 2.69 | 25400 | R-410A
212627177 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TP9C100C20MP13 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
212627179 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TP9C100C20MP13 | 32200 | 17.5 | 9.4 | 8.1 | 33800 | 28200 | 83.43% | 2.46 | 25800 | R-410A
212627243 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TL9E060B12UH11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627254 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TL9E060B12UH11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212627329 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | CP9C060B12MP13 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
215941253 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1002122A* | 45000 | 20.5 | 11 | 9 | 48500 | 36600 | 75.46% | 1.82 | 39500 | R-454B
215375385 | 1.88 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C46+TDR |  | 22600 | 15.2 | 12 | 9 | 19400 | 19400 | 100% | 2.73 | 24200 | R-410A
215399917 | 1.8 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR |  | 21600 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.63 | 18600 | R-454B
216056068 | 3.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z9ES120D20SMPS1 | 43000 | 17.5 | 11.5 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
215940993 | 3.63 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CTN1002122A* | 43500 | 21 | 10.5 | 9.5 | 48000 | 36400 | 75.83% | 2 | 39500 | R-454B
215375384 | 1.88 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C44+TDR |  | 22600 | 15.2 | 12 | 9 | 19400 | 19400 | 100% | 2.73 | 24200 | R-410A
215375386 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M060B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 19500 | 82.63% | 2.17 | 22200 | R-410A
214331711 | 2.52 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M100C5B | 30200 | 18.5 | 11 | 8.8 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
214331845 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331863 | 2.68 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M080C4B | 32200 | 17.5 | 11 | 8.9 | 34200 | 26600 | 77.78% | 2.5 | 25000 | R-410A
215057517 | 2.68 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M48A4 |  | 32200 | 19 | 12 | 9.5 | 33200 | 24000 | 72.29% | 1.9 | 28000 | R-410A
214595299 | 1.83 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24C46+TDR |  | 22000 | 15.2 | 11.9 | 8.8 | 24000 | 19100 | 79.58% | 1.94 | 19400 | R-410A
213752392 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC2E080M17**16 | 23600 | 16.5 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.87 | 19800 | R-410A
212624019 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE080B12MP11 | 31000 | 17.8 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212624119 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TPLC060A12MP13 | 32000 | 17.5 | 9 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624121 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TPLC060A12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 33400 | 28800 | 86.23% | 2.49 | 26000 | R-410A
212624137 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624144 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42C24+TDR | TM9V080B12MP12 | 31400 | 17 | 9.5 | 8.5 | 34000 | 29400 | 86.47% | 2.73 | 26600 | R-410A
212624160 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.45 | 26600 | R-410A
212624169 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM9Y100C20MP11 | 32000 | 15.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212624194 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
212624312 | 2.65 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLE100C16MP11 | 31800 | 18 | 10 | 8.1 | 33000 | 29000 | 87.88% | 2.49 | 26000 | R-410A
212624339 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B34+TDR | TM8V080C16MP12 | 32200 | 17.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212624405 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9Y080C16MP11 | 32800 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624430 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8E120C16MP11 | 32800 | 18 | 10 | 8.5 | 34000 | 28800 | 84.71% | 2.79 | 26200 | R-410A
212624446 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.4 | 34000 | 29200 | 85.88% | 2.79 | 26400 | R-410A
212624453 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TPLC100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27200 | 80.47% | 2.48 | 25200 | R-410A
212624487 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | CPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624494 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CPLC080C16MP13 | 33200 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213927957 | 3.38 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)60C44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213927973 | 3.38 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)61A44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
215565324 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z9ES060A10SMPS1 | 20800 | 17.5 | 11.7 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
214331699 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M080B3B | 22400 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214331706 | 2.72 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080C4B | 32600 | 17.5 | 11 | 9 | 34200 | 26600 | 77.78% | 2.51 | 25000 | R-410A
214331860 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M080C4B | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 26400 | 78.11% | 2.41 | 24800 | R-410A
215399918 | 1.87 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR |  | 22400 | 15.2 | 11 | 8.5 | 22600 | 21200 | 93.81% | 2.65 | 18600 | R-454B
215375389 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M100C5B | 29800 | 18.5 | 11 | 8.7 | 34000 | 25400 | 74.71% | 2.43 | 27400 | R-410A
213613375 | 2 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M36L4 |  | 24000 | 15.5 | 9 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213927955 | 3.42 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)48D44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
212624539 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | CPLC100C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624555 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | CPLC100C16MP13 | 33400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624569 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM8V080C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624573 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM8V080C16MP12 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624628 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM8V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624687 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TPLC080C16MP13 | 30200 | 17 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212348379 | 1.42 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | LEW30C4 |  | 17000 | 15.2 | 10.5 | 8.5 | 18000 | 18300 | 101.7% | 2.56 | 12000 | R-410A
214331690 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M060B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331692 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M060B3B | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.34 | 24800 | R-410A
214331701 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M080B3B | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331851 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M080B3B | 22400 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
216055997 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C16SMPS1 | 40000 | 16.5 | 11.7 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
214331836 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M060B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214331837 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M060B3B | 22600 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214331839 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M060B3B | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
213206908 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 59SC2D080E21**20 | 29600 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.49 | 23200 | R-410A
213927970 | 3.42 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)43D44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213205854 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*A070E17**16 | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 22800 | 87.02% | 2.92 | 20600 | R-410A
213205890 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58S(B,C)*A090E21**20 | 23800 | 16 | 9.5 | 8.5 | 25800 | 22800 | 88.37% | 2.86 | 20400 | R-410A
213205924 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58TP*A070V17**16 | 23800 | 16.5 | 9 | 8.1 | 25200 | 22600 | 89.68% | 2.85 | 20200 | R-410A
216797121 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2C100D5PSC+LRP | 30200 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.67 | 37800 | R-454B
213752756 | 1.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 58TP*B090V17**16 | 22200 | 17.2 | 9 | 8.4 | 25200 | 19900 | 78.97% | 2.94 | 18600 | R-410A
213885816 | 2.68 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | AE(D,N,U)+CM36B34+TDR |  | 32200 | 18.5 | 12 | 8.5 | 31400 | 38500 | 122.6% | 2.95 | 31000 | R-410A
213927949 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)30D44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
214331686 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M060B3B | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214331702 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3B | 31000 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.31 | 24800 | R-410A
214331704 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M080C4B | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 26400 | 78.11% | 2.41 | 24800 | R-410A
214331705 | 2.62 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M080C4B | 31400 | 17.5 | 10.8 | 8.7 | 34000 | 26400 | 77.65% | 2.44 | 24800 | R-410A
214331854 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3B | 31000 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.31 | 24800 | R-410A
212627332 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | CP9C060B12MP13 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212627415 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9V080B12MP12 | 32200 | 17 | 9.5 | 8.4 | 34000 | 29400 | 86.47% | 2.74 | 26600 | R-410A
214331855 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M080C4A | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 26400 | 78.11% | 2.41 | 24800 | R-410A
214331870 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M100C5B | 29800 | 18.5 | 11 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
212627432 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8E080B12MP11 | 32800 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.63 | 25800 | R-410A
212627465 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TMLE080B12MP11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.41 | 25800 | R-410A
212627498 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9Y100C16MP11 | 32400 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.75 | 26000 | R-410A
214063991 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M060B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214064025 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M100C5B | 29800 | 18.5 | 11 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214094116 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | DM36A34+TDR | BGH96M060B3A | 22200 | 18.3 | 11.8 | 8.4 | 23600 | 23000 | 97.46% | 2.3 | 19900 | R-410A
212624712 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TPLC100C16MP13 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212624721 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TPLC100C16MP13 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
214595296 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30C36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 17400 | 73.11% | 1.9 | 19400 | R-410A
214595314 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30C36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 28400 | 119.3% | 1.9 | 19400 | R-410A
213753697 | 2.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*B110M24**20 | 35000 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213753799 | 2.82 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59SC6A100M21**20 | 33800 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.74 | 29000 | R-410A
214331852 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331869 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5A | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214331685 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M060B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214595298 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 20000 | 84.03% | 2 | 19400 | R-410A
214595305 | 1.87 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30C46+TDR |  | 22400 | 15.2 | 12 | 8.9 | 24000 | 22600 | 94.17% | 2 | 19400 | R-410A
212627549 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9Y100C20MP11 | 33000 | 15.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.38 | 25600 | R-410A
212627584 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 34000 | 28400 | 83.53% | 2.77 | 26000 | R-410A
212627682 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A36+TDR | TM8Y080C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627683 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8Y100C16MP11 | 32200 | 18.5 | 9.9 | 8.4 | 34000 | 27400 | 80.59% | 2.65 | 25400 | R-410A
212627700 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | CPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627702 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CPLC080C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627782 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TM8V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627783 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8V100C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214595316 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 38500 | 161.8% | 1.88 | 19400 | R-410A
212841194 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | AFM234+TDR |  | 23800 | 19.5 | 12.5 | 9 | 23800 | 26600 | 111.8% | 2.61 | 22000 | R-410A
212628118 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TP9C100C20MP13 | 29600 | 16.9 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212627752 | 2.7 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8V080C16MP12 | 32400 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627768 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM8V100C16MP12 | 30600 | 17.2 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627769 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212627800 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TMLV100C16MP12 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627849 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627851 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
213753156 | 2.45 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 58S(B,C)*B090M21**16 | 29400 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.63 | 23400 | R-410A
213752372 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2E060M14**12 | 23600 | 16 | 9.5 | 8.5 | 25400 | 22600 | 88.98% | 2.9 | 20200 | R-410A
213752386 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2E060M17**14 | 23800 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213753263 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 58TP*B070V14**12 | 29600 | 15.2 | 9 | 8.1 | 34000 | 23800 | 70% | 2.7 | 23400 | R-410A
214331838 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M060B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331871 | 2.52 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M100C5B | 30200 | 18.5 | 11 | 8.8 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
214331872 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M100C5B | 31200 | 18.5 | 11.9 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
214595294 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24D36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 17400 | 73.11% | 1.9 | 19400 | R-410A
214595324 | 1.87 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D36+TDR |  | 22400 | 15.2 | 12 | 9 | 24000 | 34000 | 141.7% | 1.83 | 19400 | R-410A
214595325 | 1.88 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30D46+TDR |  | 22600 | 15.2 | 12 | 9 | 24000 | 24200 | 100.8% | 1.8 | 19400 | R-410A
214595326 | 1.88 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C46+TDR |  | 22600 | 15.2 | 12 | 9 | 24000 | 24200 | 100.8% | 1.8 | 19400 | R-410A
215375412 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080C4B | 31600 | 17.5 | 10.9 | 8.6 | 33800 | 24800 | 73.37% | 2.42 | 26400 | R-410A
212627868 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627884 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TL9E080C16UH11 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627902 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TL9E080C16UH11 | 30800 | 17.3 | 9.2 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214331688 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M060B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
215057476 | 1.78 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M24F4 |  | 21400 | 18 | 12 | 8.1 | 23400 | 17600 | 75.21% | 2 | 22400 | R-410A
212675683 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | L(E,G)M24H4 |  | 23600 | 19.5 | 12.5 | 9 | 24000 | 26400 | 110% | 2.46 | 22000 | R-410A
212675684 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | L(E,G)M36F4 |  | 34200 | 19 | 12 | 9.5 | 34200 | 30800 | 90.06% | 2.64 | 27400 | R-410A
212627969 | 2.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TM8Y100C16MP11 | 32800 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213205938 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 58TP*A090V17**16 | 23600 | 16 | 9.5 | 8.1 | 25200 | 22400 | 88.89% | 2.94 | 20000 | R-410A
213205965 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 58TP*A110V21**22 | 23800 | 16.5 | 9.5 | 8.1 | 25000 | 22200 | 88.8% | 2.94 | 19900 | R-410A
213206013 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2D060E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.9 | 20400 | R-410A
213206049 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC2D100E21**20 | 23800 | 16 | 9 | 8.5 | 26000 | 23000 | 88.46% | 2.92 | 20600 | R-410A
213206097 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC5B060E17**14 | 23400 | 15.3 | 9.3 | 8.4 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213206197 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59TP6B080V21**20 | 23600 | 16 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
214521937 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | Z8ES100C16SMPS1 | 32200 | 18 | 9.4 | 8.5 | 33200 | 28200 | 84.94% | 2.7 | 25600 | R-410A
214521953 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z8ES120C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.64 | 25600 | R-410A
212627801 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLV100C16MP12 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627802 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TMLV100C16MP12 | 32400 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627836 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.47 | 25400 | R-410A
212627867 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212627885 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TL9E080C16UH11 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627900 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TL9E080C16UH11 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212627968 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8Y100C16MP11 | 30200 | 17.9 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212628001 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TP9C100C16MP13 | 29200 | 16.7 | 9.4 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
213753826 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SP6A060V17**14 | 33800 | 15.5 | 9.4 | 8.1 | 38500 | 31400 | 81.56% | 2.71 | 29000 | R-410A
213753842 | 2.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)42B34+TDR | 59SP6A100V21**20 | 35200 | 16 | 9.5 | 8.1 | 39000 | 31800 | 81.54% | 2.51 | 29400 | R-410A
213206910 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30D44+TDR | 59SC2D080E21**20 | 29600 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.49 | 23200 | R-410A
213752429 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC6A026M14**10 | 23400 | 15.5 | 9 | 8.1 | 25200 | 22600 | 89.68% | 2.86 | 20200 | R-410A
213752436 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC6A040M14**10 | 22600 | 15.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
215375406 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M060B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 19500 | 82.63% | 2.17 | 22200 | R-410A
214331694 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M080B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
214331695 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331696 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M080B3B | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214331830 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M060B3A | 22600 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214331844 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M080B3A | 22400 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214331847 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3A | 31000 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.31 | 24800 | R-410A
214331864 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4B | 31600 | 17.5 | 10.9 | 8.6 | 33800 | 26400 | 78.11% | 2.42 | 24800 | R-410A
212624787 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TL8E080C16UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
212624807 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL8E080C16UH11 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27800 | 81.76% | 2.68 | 25600 | R-410A
213752556 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SP6A100V21**20 | 23800 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213752561 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6C040V14**10 | 22400 | 15.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
212624848 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TL9E080C16UH11 | 32600 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
212624873 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | CP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212624907 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM8Y080C16MP11 | 29800 | 17.8 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212624923 | 2.67 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM8Y080C16MP11 | 32000 | 18.5 | 9.9 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214056977 | 4.21 | No | No | American Standard | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2060A10NU** | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
212507780 | 2.82 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M15G | L(E,G)M36F4 |  | 33800 | 15.2 | 10 | 8.1 | 33800 | 25000 | 73.96% | 2.23 | 24000 | R-410A
215934537 | 3.71 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *96CTN1202422B* | 44500 | 20 | 10.5 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
214063993 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M060B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214064027 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M100C5B | 31200 | 18.5 | 11.9 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
214064029 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M100C5B | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
213752609 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C100V21**20 | 23400 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
212624980 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM8Y100C16MP11 | 30600 | 18.1 | 9.6 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
212625096 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TP9C100C16MP13 | 32400 | 17.5 | 10 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625132 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TP9C100C16MP13 | 30200 | 17 | 9 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212625221 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212625248 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TL8E100C20UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625266 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TL8E100C20UH11 | 30200 | 17 | 9 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212625298 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | CP9C100C20MP13 | 30000 | 17 | 9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212625341 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | CP9C100C20MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
213927971 | 3.42 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)43E44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
212625348 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625389 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9V100C20MP12 | 30800 | 17.3 | 9.2 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
213752622 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6C100V21**22 | 23800 | 16.5 | 9 | 8.5 | 25200 | 22400 | 88.89% | 2.91 | 20000 | R-410A
213206022 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59SC2D080E17**16 | 23800 | 16.5 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.93 | 20200 | R-410A
213206183 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6B080V17**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.92 | 20200 | R-410A
213206190 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6B080V21**20 | 23400 | 16 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
211173336 | 2.95 | No | Yes | Century | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1536S1R-**A | C(A,C,D,E)48D34+TDR | GDD96C110C5M | 35400 | 16.4 | 13 | 8.2 | 32000 | 22400 | 70% | 2.8 | 18600 | R-410A
212625423 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TM9V100C20MP12 | 30800 | 17.3 | 9.2 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
212625439 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TP9C100C20MP13 | 30400 | 17.1 | 9 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625457 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212625582 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8V120C20MP12 | 31600 | 16.5 | 8.9 | 8.5 | 32200 | 27600 | 85.71% | 2.7 | 25000 | R-410A
213753622 | 2.47 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | D(A,C,E)30C44+TDR | 59TP6C100V21**22 | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
214595315 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A46+TDR |  | 21800 | 15.2 | 11.8 | 8.7 | 23800 | 33000 | 138.7% | 1.9 | 19300 | R-410A
214595320 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30D36+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 29600 | 123.3% | 1.96 | 19400 | R-410A
214595322 | 1.87 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24D46+TDR |  | 22400 | 15.2 | 12 | 8.9 | 24000 | 34000 | 141.7% | 1.83 | 19400 | R-410A
214331684 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M060B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.23 | 19500 | R-410A
214331700 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
212625632 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TP9C120D20MP13 | 31800 | 17 | 9.4 | 8.1 | 32200 | 28200 | 87.58% | 2.5 | 25400 | R-410A
212625639 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CPLC120C20MP13 | 28600 | 15.6 | 8.4 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625650 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C26+TDR | TM8V120C20MP12 | 29600 | 15.9 | 8 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
212625657 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TPLC100C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212625666 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | CPLC100C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625673 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625689 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | CPLC120C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625714 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM8V100C20MP12 | 32600 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212628019 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C26+TDR | TP9C100C16MP13 | 30600 | 17.2 | 9.6 | 8.1 | 34000 | 27400 | 80.59% | 2.47 | 25400 | R-410A
212628036 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM8Y100C20MP11 | 33000 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628067 | 2.43 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CP9C100C20MP13 | 29200 | 16.7 | 8.9 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
212628086 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | CP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
212628100 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9V100C20MP12 | 30400 | 17.1 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
216055693 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055747 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9Y080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
216055760 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
214331865 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M100C5A | 29800 | 18.5 | 11 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214331867 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M100C5A | 31200 | 18.5 | 11.9 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
213927959 | 3.42 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)61C44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
213205815 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 58S(B,C)*A045E17**12 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.92 | 20200 | R-410A
213206015 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59SC2D060E17**14 | 23800 | 16 | 9.5 | 8.1 | 25800 | 22800 | 88.37% | 2.91 | 20400 | R-410A
213206106 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 59SC5B060E17**14 | 23800 | 15.4 | 9.3 | 8.5 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
212627656 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216055732 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V080B12MP12 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
212625732 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TM8V120C20MP12 | 30000 | 16 | 8.6 | 8.5 | 32400 | 27800 | 85.8% | 2.7 | 25200 | R-410A
212625741 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TMLV120C20MP12 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625750 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C36+TDR | TMLV120C20MP12 | 32200 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625789 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D26+TDR | TPLC120C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212625807 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B46+TDR | TM9Y120D20MP11 | 32600 | 16.5 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.77 | 25400 | R-410A
212625823 | 2.4 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | CP9C120D20MP13 | 28800 | 16.1 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.52 | 25200 | R-410A
214595321 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C36+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 29400 | 122.5% | 1.95 | 19400 | R-410A
215375391 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080B3B | 31000 | 17.5 | 10.5 | 8.6 | 33600 | 24800 | 73.81% | 2.31 | 26600 | R-410A
212625843 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | CP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625850 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | CP9C120D20MP13 | 30600 | 16.6 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625882 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TP9C120D20MP13 | 32000 | 17 | 9.4 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212625916 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C26+TDR | TM9V040A10MP12 | 30400 | 16.7 | 9 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625918 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V040A10MP12 | 31600 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212625932 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D26+TDR | TM9V040A10MP12 | 30800 | 16.8 | 9.3 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212626075 | 2.75 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8Y080B12MP11 | 33000 | 18 | 10 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212626282 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9E080B12MP12 | 30000 | 16.9 | 9.5 | 8.3 | 33600 | 27600 | 82.14% | 2.59 | 25400 | R-410A
212626334 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
212626400 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9E100C16MP12 | 33200 | 18 | 10 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
212626409 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TL8E100C20UH11 | 29600 | 16.9 | 9.5 | 8.3 | 33600 | 27200 | 80.95% | 2.65 | 25200 | R-410A
212626418 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A26+TDR | TM9V100C20MP12 | 29600 | 16.9 | 9 | 8.4 | 33600 | 28000 | 83.33% | 2.68 | 25600 | R-410A
212626620 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9Y100C16MP11 | 32800 | 18 | 10 | 8.3 | 33800 | 28600 | 84.62% | 2.69 | 26000 | R-410A
212626693 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TM9Y100C16MP11 | 30600 | 17.9 | 9.8 | 8.3 | 33800 | 28600 | 84.62% | 2.68 | 26000 | R-410A
214331833 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M060B3A | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.34 | 24800 | R-410A
214331835 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M060B3B | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.23 | 19500 | R-410A
213752426 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59SC6A026M14**10 | 23400 | 15.5 | 9 | 8.1 | 25200 | 22600 | 89.68% | 2.86 | 20200 | R-410A
213752559 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 59TP6C040V14**10 | 22400 | 15.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213752593 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6C080V17**16 | 23400 | 16 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.84 | 19800 | R-410A
214595318 | 1.83 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B46+TDR |  | 22000 | 15.2 | 11.9 | 8.8 | 24000 | 34400 | 143.3% | 1.77 | 19400 | R-410A
214331697 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
214331846 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M080B3A | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331861 | 2.62 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M080C4B | 31400 | 17.5 | 10.8 | 8.7 | 34000 | 26400 | 77.65% | 2.44 | 24800 | R-410A
216055737 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
212626702 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.2 | 33800 | 28600 | 84.62% | 2.71 | 26000 | R-410A
212626834 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM9E080B12MP12 | 32200 | 17.5 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626836 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TM9E080B12MP12 | 32600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626852 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM9E080B12MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626854 | 2.8 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM9E080B12MP12 | 33600 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212626893 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM8E060A12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626895 | 2.72 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B36+TDR | TM8E060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626904 | 2.8 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+TDR | TM8E060A12MP11 | 33600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
216055770 | 2.62 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C16MP11 | 31400 | 18 | 10.5 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055788 | 2.57 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080B12MP13 | 30800 | 18 | 10.5 | 8.1 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055803 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055804 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TPLC080C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055821 | 2.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31400 | 25200 | 80.25% | 2 | 27600 | R-454B
216055993 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216056016 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
215375436 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M060B3B | 23400 | 18.5 | 12 | 9 | 20000 | 20000 | 100% | 2.86 | 25000 | R-410A
214331683 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M060B3A | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214331708 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4B | 31600 | 17.5 | 10.9 | 8.6 | 33800 | 26400 | 78.11% | 2.42 | 24800 | R-410A
214331849 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
215375393 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M100C5B | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 25400 | 74.71% | 2.43 | 27400 | R-410A
216055809 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES080B12SMPS1 | 30800 | 18 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216055816 | 2.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES080C20SMPS1 | 32000 | 19 | 10.5 | 8.5 | 32200 | 25800 | 80.12% | 2 | 28200 | R-454B
216055825 | 2.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
216055841 | 2.67 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z9ES100C16SMPS1 | 32000 | 17.5 | 10.5 | 8.1 | 32400 | 24600 | 75.93% | 2 | 26400 | R-454B
216055741 | 2.63 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V100C20MP12 | 31600 | 18 | 9.8 | 8.5 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
216055757 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055775 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TMLE120C16MP11 | 30600 | 18 | 11 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055782 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLV100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
214521989 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | Z9ES100C20SMPS1 | 31200 | 17.4 | 9.3 | 8.3 | 33000 | 27600 | 83.64% | 2.65 | 25200 | R-410A
216055734 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9V080C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055759 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055818 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES100B12SMPS1 | 31000 | 18 | 11.2 | 8.1 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
214864383 | 2.6 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE*S+CM48E34+TDR |  | 31200 | 18.3 | 10.3 | 8.4 | 32800 | 23200 | 70.73% | 2.1 | 24600 | R-410A
214331868 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M100C5A | 31000 | 18.5 | 11.8 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
214331841 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M080B3A | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214331850 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214331859 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4A | 31600 | 17.5 | 10.9 | 8.6 | 33800 | 26400 | 78.11% | 2.42 | 24800 | R-410A
213892471 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG1K942+TXV | A96DS2V070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
216055723 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9E100C16MP12 | 30800 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216055750 | 2.6 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9Y080C16MP11 | 31200 | 18 | 10.5 | 8.5 | 32000 | 25800 | 80.62% | 2 | 28200 | R-454B
216055791 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055823 | 2.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ES100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
215057483 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M24H4 |  | 22400 | 18.5 | 12.5 | 8.5 | 23000 | 17600 | 76.52% | 2 | 22400 | R-410A
214584488 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24D34+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 17400 | 73.11% | 1.9 | 19400 | R-410A
214625049 | 1.72 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ24AB3 | D(A,C,E)24A24+TDR |  | 20600 | 15.2 | 10 | 9.3 | 21000 | 20000 | 95.24% | 1.95 | 21000 | R-410A
213803496 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ET100C20LMPS1 | 33600 | 18.5 | 9.5 | 8.4 | 33000 | 29600 | 89.7% | 2.81 | 26400 | R-410A
213803497 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ET100C20LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.7 | 26200 | R-410A
215487447 | 3.79 | Yes | Yes | DAIKIN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DH7VSA4810A* | CHPEA4830*3A* | D*80VC0804C*A* | 45500 | 16.5 | 10 | 8.5 | 46000 | 33600 | 73.04% | 2 | 28400 | R-32
216055748 | 2.6 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y080C16MP11 | 31200 | 18 | 10.5 | 8.5 | 32000 | 25800 | 80.62% | 2 | 28200 | R-454B
216055832 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Z8ET080B12LMPS1 | 30600 | 19 | 11 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
214331713 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M100C5B | 31000 | 18.5 | 11.8 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
214331714 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5B | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214331827 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M060B3A | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214331828 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M060B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.23 | 19500 | R-410A
214331829 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M060B3A | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214331831 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M060B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214061876 | 1.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | HG80936 | SL280UH090V48B* | 22400 | 22 | 14.5 | 9.3 | 20000 | 20000 | 100% | 1.84 | 23000 | R-410A
214595300 | 1.83 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30B46+TDR |  | 22000 | 15.2 | 11.9 | 8.8 | 24000 | 16900 | 70.42% | 1.98 | 19400 | R-410A
214595302 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30D36+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 22400 | 93.33% | 2 | 19400 | R-410A
214625048 | 1.29 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ18AB3 | D(A,C,E)24A24+TDR |  | 15500 | 15.2 | 11 | 9.3 | 14700 | 15000 | 102% | 2.2 | 14700 | R-410A
216055688 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055702 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y100C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216055703 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y100C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
214775803 | 4.42 | No | No | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV4860RA1-N | H,DE48960 | WPV090T5BA | 53000 | 15.2 | 9.5 | 8.4 | 56000 | 40500 | 72.32% | 1.78 | 37000 | R-410A
213286705 | 2.45 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | CE2903A+TXV |  | 29400 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
207455308 | 1.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*23/37Z9 | SL280UH080NV48B* | 22600 | 21 | 14 | 9.4 | 19800 | 19600 | 98.99% | 1.94 | 22400 | R-410A
213205907 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A110E21**20 | 23800 | 15.5 | 9.5 | 8.5 | 26200 | 22800 | 87.02% | 2.85 | 20600 | R-410A
213205957 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)24B44+TDR | 58TP*A110V21**22 | 23600 | 16.5 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.98 | 19900 | R-410A
215850380 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 31000 | 18 | 11.2 | 8.1 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
214063855 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M080B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214584508 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30C34+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 28400 | 119.3% | 1.9 | 19400 | R-410A
213821023 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80MS(N,L)0701412A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821025 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80MS(N,L)0701412A* | 23800 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
212675692 | 4.67 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M15G | L(E,G)M60F4 |  | 56000 | 15.5 | 10 | 8.5 | 56000 | 42000 | 75% | 2.39 | 40000 | R-410A
216056019 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES130D20SMPS1 | 40500 | 17.5 | 11.7 | 8.5 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
213160938 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | PL36H175P069+AEFE4B* |  | 29800 | 15.2 | 8.5 | 8.2 | 33200 | 27000 | 81.33% | 1.78 | 22600 | R-410A
213821034 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0701716A* | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821041 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0901714A* | 23600 | 16.5 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821052 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0902120A* | 23400 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821066 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80VTL0701716B* | 23400 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821068 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *80VTL0701716B* | 23800 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.89 | 19900 | R-410A
213821075 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *80VTL0902120B* | 23800 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.9 | 19900 | R-410A
213821116 | 1.88 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *96MSN0401410A* | 22600 | 15.3 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
213821118 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96MSN0401410A* | 23200 | 15.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.87 | 19700 | R-410A
207454732 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LH35/38F9 | EL296UH090XV48C* | 22200 | 21 | 14.5 | 9.4 | 19800 | 19600 | 98.99% | 1.9 | 22600 | R-410A
207454815 | 1.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LH29/36F9 | SL280UH090V36B* | 21400 | 22 | 14 | 9.45 | 19800 | 19500 | 98.48% | 1.94 | 22200 | R-410A
207454816 | 1.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*19/36S9 | SL280UH090V36B* | 21400 | 22 | 14 | 9.45 | 19800 | 19500 | 98.48% | 1.94 | 22200 | R-410A
207454901 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*35/36U9 | SL297UH040NV36B* | 22200 | 22 | 14 | 9.9 | 19800 | 20000 | 101% | 1.84 | 23000 | R-410A
213821143 | 1.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0401410B* | 23000 | 15.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
213821157 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0801716B* | 23200 | 16 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
213825962 | 2.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X36A1 | 4TXCC005DS3 | *UHMC100CCV4 | 34200 | 18 | 12 | 8.2 | 28800 | 20200 | 70.14% | 1.8 | 26000 | R-410A
213160941 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | PL36H175P789+AEFE4B* |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
216055762 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE080C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216055882 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C16MP12 | 40500 | 16.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
212614361 | 2.52 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*BB8937 |  | 30200 | 15.2 | 9 | 8.1 | 32400 | 27000 | 83.33% | 1.78 | 22400 | R-410A
212614366 | 2.52 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*E34936 |  | 30200 | 15.2 | 9 | 8.4 | 33400 | 27000 | 80.84% | 1.8 | 22600 | R-410A
213163581 | 2.47 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | H,FG32936+AEFE4B* |  | 29600 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
213160939 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | PL36H175P159+AEFE4B* |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
216055792 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
213160942 | 2.53 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | V,G36H***P449+AEFE3A* |  | 30400 | 15.2 | 9 | 8.5 | 33400 | 27000 | 80.84% | 1.82 | 22600 | R-410A
214595306 | 1.87 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D36+TDR |  | 22400 | 15.2 | 12 | 9 | 24000 | 22600 | 94.17% | 2 | 19400 | R-410A
212479843 | 1.48 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A36VCA+TXV | 59TP6B040V17**12 | 17700 | 15.2 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.28 | 11500 | R-410A
214394736 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R951V0855A21M4S | 52000 | 17 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
207454967 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*35/36S9 | SLP99UH090XV36C* | 22200 | 22 | 14.5 | 9.3 | 19800 | 19800 | 100% | 1.9 | 22800 | R-410A
207455326 | 1.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*23/37Z9 | SLP99UH070XV36B* | 22800 | 22 | 14.5 | 10.1 | 19600 | 19600 | 100% | 1.96 | 22400 | R-410A
207454824 | 1.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*35/36U9 | SL280UH090V48B* | 22400 | 22 | 14.5 | 9.3 | 20000 | 20000 | 100% | 1.84 | 23000 | R-410A
207454842 | 1.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*19/36S9 | SL280UH090XV48B* | 21400 | 21 | 14 | 9.35 | 19800 | 19500 | 98.48% | 1.94 | 22200 | R-410A
207454924 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LH23/37W9 | SL297UH080NV48C* | 22200 | 21 | 14 | 9.3 | 19800 | 19800 | 100% | 1.9 | 22800 | R-410A
214336682 | 4.33 | No | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | CP61C34+TDR | R802VA100521M | 52000 | 18.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214331834 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M060B3B | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
213785113 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3721AL*+UI | 58TN*B090C21**20 | 24200 | 20 | 13 | 10.5 | 26400 | 19700 | 74.62% | 2.54 | 24800 | R-410A
213785197 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*3012AL*+UI | 58TN*B135C24**22 | 23400 | 18.5 | 12.5 | 10 | 26800 | 19900 | 74.25% | 2.44 | 25000 | R-410A
213785233 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*3612AL*+UI | 59MN7C100C21**22 | 23800 | 19 | 13 | 10 | 26600 | 19700 | 74.06% | 2.5 | 24800 | R-410A
213785247 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*4212AL*+UI | 58TN*B070C14**12 | 23600 | 19.5 | 13 | 9.5 | 26400 | 19800 | 75% | 2.5 | 24800 | R-410A
212624451 | 2.48 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TMLV100C16MP12 | 29800 | 16.9 | 9.5 | 8.1 | 33800 | 27200 | 80.47% | 2.48 | 25200 | R-410A
212614363 | 2.45 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*E32936 |  | 29400 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
213782025 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 59TN6C100C21**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.94 | 31400 | R-410A
216055834 | 2.53 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ET080B12LMPS1 | 30400 | 19 | 11.2 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
214720231 | 1.33 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24HDN1-M15G | AEW254+TDR |  | 15900 | 15.2 | 10 | 8.1 | 17500 | 12900 | 73.71% | 1.81 | 15000 | R-410A
213785398 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**3721AL*+UI | 58TN*B090C17**16 | 33800 | 19 | 12 | 9 | 36400 | 25800 | 70.88% | 2.04 | 30800 | R-410A
213785466 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4321AL*+UI | 59CU5B060C17**16 | 33800 | 19 | 11.7 | 9 | 36600 | 25800 | 70.49% | 2.02 | 31000 | R-410A
213785482 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4821AL*+UI | 58TN*B070C17**16 | 33000 | 19 | 11.7 | 9 | 36600 | 25800 | 70.49% | 2.02 | 31200 | R-410A
216794323 | 1.64 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B080D4VSB+LRP | 19700 | 20.6 | 11.2 | 9.5 | 23000 | 22000 | 95.65% | 2.92 | 27000 | R-454B
213160940 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | V,G36H175P159+AEFE4B* |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
211206845 | 1.87 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B2421 | XAMB24DE1N1+CC | TM8V080B12MP12 | 22400 | 18 | 12 | 8.5 | 23600 | 18400 | 77.97% | 1.92 | 23000 | R-410A
213821019 | 1.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0451412A* | 23000 | 16.4 | 9.3 | 8.1 | 24400 | 22200 | 90.98% | 2.92 | 19700 | R-410A
213821021 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)24B44+TDR | *80MS(N,L)0701412A* | 23400 | 16.5 | 9 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
213821087 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *92MSN0601412A* | 23600 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.88 | 20000 | R-410A
213821137 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96MSN0802120A* | 23600 | 16 | 9 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
213821153 | 1.97 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30C44+TDR | *96VTN0601412B* | 23600 | 16 | 9 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
213821154 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *96VTN0601412B* | 23400 | 16 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.87 | 19900 | R-410A
214331762 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331929 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080C4B | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
213278579 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+JMET12BS2N1+TDR |  | 34000 | 18 | 8.9 | 8.1 | 36000 | 26000 | 72.22% | 2.8 | 25200 | R-410A
210693338 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VM970804CNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693354 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VS960805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693397 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VM970804CNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693322 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VS800604BUA* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214584490 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30C34+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 17400 | 73.11% | 1.9 | 19400 | R-410A
215934587 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU1002122B* | 45000 | 20.5 | 11.5 | 9 | 48500 | 36400 | 75.05% | 1.84 | 39500 | R-454B
216764077 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*DD10AS3 | S9V2D120D5PSC | 51000 | 16 | 11 | 9 | 51000 | 38500 | 75.49% | 2.1 | 33800 | R-454B
214063911 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M080B3A | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214063930 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M100C5B | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 38500 | 83.7% | 2.27 | 35400 | R-410A
214063945 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M120D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
213885831 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | AE(D,N,U)+CM36B34+TDR |  | 22600 | 20 | 12.8 | 9.2 | 23800 | 27200 | 114.3% | 2.52 | 22400 | R-410A
213927952 | 2.4 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)42A44+TDR |  | 28800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
212989235 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *95MSU0601716A* | 23600 | 17 | 10.5 | 8.5 | 26400 | 24400 | 92.42% | 2.02 | 19100 | R-410A
213885829 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | AE(D,N,U)+CM36A34+TDR |  | 22200 | 19.9 | 12.7 | 8.9 | 23600 | 27000 | 114.4% | 2.45 | 22200 | R-410A
214331954 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M120D5B | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331755 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3A | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
215941233 | 3.67 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0801716A* | 44000 | 19.5 | 10.5 | 9 | 49000 | 37400 | 76.33% | 1.8 | 40500 | R-454B
212970458 | 2.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | END4X42L17** | *80VSL0701716B* | 35600 | 15.5 | 10 | 8.1 | 38500 | 35000 | 90.91% | 1.94 | 29400 | R-410A
212971877 | 2.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *80VTL0701716B* | 35600 | 16 | 10 | 8.5 | 37800 | 34800 | 92.06% | 2.02 | 29000 | R-410A
212969788 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *80VSL0451412B* | 24200 | 17 | 10 | 8.5 | 25200 | 22000 | 87.3% | 1.84 | 18700 | R-410A
212971209 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *80VTL0451412B* | 23400 | 17 | 10 | 8.5 | 27000 | 25000 | 92.59% | 2.08 | 19500 | R-410A
214331943 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
215057490 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M24J4 |  | 23000 | 19 | 12.5 | 9 | 23200 | 17600 | 75.86% | 2 | 22400 | R-410A
214094160 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | DM59A44+TDR | BGH96M080C4A | 40500 | 17 | 11.5 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214063910 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080B3A | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
216763692 | 2.78 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C007AS3 |  | 33400 | 16 | 11.5 | 8.7 | 33200 | 24600 | 74.1% | 2.1 | 21800 | R-454B
214331946 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100D5B | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331947 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M120D5A | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
213785500 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4821AL*+UI | 59TN6C080C17**14 | 33000 | 19 | 11.7 | 9 | 36600 | 26000 | 71.04% | 2.02 | 31200 | R-410A
212675689 | 4.33 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | L(E,G)M60F4 |  | 52000 | 18 | 11.7 | 9.5 | 55000 | 48500 | 88.18% | 2.48 | 43500 | R-410A
214331777 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100C5B | 44000 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331780 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100D5A | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
210693345 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC800804C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693347 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC800805C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693386 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC801005C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214331765 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331774 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100C5A | 43500 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331924 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080C4A | 40500 | 17 | 11 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
212675688 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | L(E,G)M48G4 |  | 47000 | 18.5 | 12 | 9.5 | 48000 | 46000 | 95.83% | 2.48 | 40000 | R-410A
213782215 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*6012AL*+UI | 58TN*B070C14**12 | 32800 | 16.5 | 11 | 8.1 | 32400 | 25600 | 79.01% | 2 | 31800 | R-410A
214331769 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080C4B | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
215942369 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CMN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
215942469 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *96CTN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2 | 32000 | R-454B
212479811 | 1.47 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A24VBA+TXV | 58TP*A070V14**12 | 17600 | 16 | 10.5 | 8.5 | 16900 | 18700 | 110.7% | 2.3 | 11400 | R-410A
212614367 | 2.52 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*E34930 |  | 30200 | 15.2 | 9 | 8.4 | 33400 | 27000 | 80.84% | 1.8 | 22600 | R-410A
211206979 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | TM8V100C16MP12 | 43500 | 19 | 12 | 9 | 44500 | 36200 | 81.35% | 2.14 | 41500 | R-410A
214331784 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100D5B | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
212851685 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | L(E,G)M48B4 |  | 46000 | 17.5 | 11.7 | 9 | 47000 | 44500 | 94.68% | 2.36 | 39000 | R-410A
213885833 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | AE(D,N,U)+CM60A34+TDR |  | 43000 | 18.2 | 11.6 | 8.8 | 47000 | 45500 | 96.81% | 2.45 | 39500 | R-410A
214320274 | 4.21 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | C(A,C,D,E)60A44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
213780855 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3721AL*+UI | 58TN*B070C17**16 | 32800 | 17 | 11 | 8.5 | 33000 | 25200 | 76.36% | 1.96 | 31800 | R-410A
211206975 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | LPLC100C20MP13 | 43500 | 19 | 12 | 9 | 44500 | 36200 | 81.35% | 2.14 | 41500 | R-410A
214331771 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5A | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 38500 | 83.7% | 2.27 | 35400 | R-410A
216763726 | 2.73 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD07AS3 |  | 32800 | 16 | 11.5 | 8.5 | 33600 | 24800 | 73.81% | 2 | 21800 | R-454B
216763744 | 2.78 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*D008AS3 |  | 33400 | 16 | 11.5 | 8.7 | 33200 | 24600 | 74.1% | 2.1 | 21800 | R-454B
214331710 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M100C5B | 29800 | 18.5 | 11 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214331712 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M100C5B | 31200 | 18.5 | 11.9 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
216764463 | 3.58 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCC009AS3 |  | 43000 | 15.5 | 11.7 | 8.7 | 44500 | 32600 | 73.26% | 2.1 | 29800 | R-454B
212507782 | 3.88 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M15G | L(E,G)M48A4 |  | 46500 | 15.2 | 10 | 8.1 | 46500 | 41500 | 89.25% | 2.31 | 37000 | R-410A
216980135 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | L(E,G)M24DJ |  | 21800 | 19 | 12.6 | 8.5 | 23400 | 17400 | 74.36% | 2 | 20800 | R-454B
214584515 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C34+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 29400 | 122.5% | 1.95 | 19400 | R-410A
212614365 | 2.52 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*G34936 |  | 30200 | 15.2 | 9 | 8.4 | 33400 | 27000 | 80.84% | 1.8 | 22600 | R-410A
212608496 | 2.6 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*SS9937 |  | 31200 | 15.2 | 9 | 8.5 | 33800 | 26400 | 78.11% | 1.86 | 22800 | R-410A
212972145 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *80VTL0902120B* | 23400 | 17 | 10 | 8.5 | 26200 | 24600 | 93.89% | 2.06 | 19100 | R-410A
212973564 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96VSN0601412B* | 23400 | 16.5 | 10 | 8.5 | 26400 | 24800 | 93.94% | 2.06 | 19100 | R-410A
214331756 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080B3A | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331776 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331783 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214331933 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100C5A | 44000 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331935 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5B | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 38500 | 83.7% | 2.27 | 35400 | R-410A
214331952 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M120D5B | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331766 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331775 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5B | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 38500 | 83.7% | 2.27 | 35400 | R-410A
214331782 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215406385 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVD-36HDN1-M20G | CM36B34+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 16900 | 71.01% | 1.97 | 19000 | R-410A
214331791 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M120D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214331945 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100D5B | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215375404 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.7 | 46500 | 35600 | 76.56% | 2.32 | 39000 | R-410A
215375421 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M120D5B | 43500 | 17.5 | 11.6 | 8.9 | 47000 | 35600 | 75.74% | 2.29 | 38500 | R-410A
215375423 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M080C4B | 41000 | 17 | 11.6 | 8.7 | 44500 | 35000 | 78.65% | 2.37 | 39000 | R-410A
212841770 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | A(E,F)M254+TDR |  | 23800 | 19.5 | 12.5 | 9 | 23800 | 26600 | 111.8% | 2.61 | 22000 | R-410A
214723126 | 1.77 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | L(E,F)W36A4 |  | 21200 | 18 | 11.7 | 8.5 | 23600 | 17600 | 74.58% | 2 | 22400 | R-410A
216035497 | 2.63 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | AE*L+CM48A3J+TDR |  | 31600 | 19 | 11.7 | 9 | 31800 | 30200 | 94.97% | 2.66 | 26200 | R-454B
214331772 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100C5A | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331938 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100C5B | 43500 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331939 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100D5A | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
215375415 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080C4B | 39500 | 17 | 11.4 | 8.5 | 44000 | 34800 | 79.09% | 2.31 | 38500 | R-410A
210693315 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VC960403BNB* | 33600 | 18 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693316 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VS960603BUA* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215940213 | 2.82 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN0601716A* | 33800 | 18.5 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30600 | R-454B
215940663 | 2.85 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *97CTN0801716A* | 34200 | 20.5 | 11.5 | 8.5 | 39000 | 28600 | 73.33% | 2.04 | 32600 | R-454B
212626929 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TMLE060A12MP11 | 29400 | 17.2 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626952 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B26+TDR | TMLE100B12MP11 | 29400 | 17.2 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626968 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TMLE100B12MP11 | 33200 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212626979 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B36+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.2 | 33800 | 30000 | 88.76% | 2.76 | 26800 | R-410A
214331840 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M060B3B | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.34 | 24800 | R-410A
214331842 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B3G+TXV+TDR | BGH96M080B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
216797055 | 1.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X24A1 | D(A,C,E)30A4J+TDR | S9V2B060U3VSB+LRP | 20400 | 18 | 11 | 8.5 | 24400 | 24400 | 100% | 3.04 | 28600 | R-454B
212628119 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C36+TDR | TP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
216055746 | 2.57 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y080B12MP11 | 30800 | 18 | 10.5 | 8.1 | 31000 | 25400 | 81.94% | 2 | 27200 | R-454B
216055761 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C16MP11 | 31200 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
215375394 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080B3B | 39500 | 17 | 11.4 | 8.5 | 43000 | 34800 | 80.93% | 2.33 | 39000 | R-410A
213927958 | 3.42 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)49D44+TDR |  | 41000 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
214331916 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080B3A | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214064098 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M100D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214063925 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M080C4B | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214063932 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M100C5B | 44000 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214064082 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080C4B | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214063916 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214723128 | 1.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | L(E,F)W30E4 |  | 21600 | 19 | 11.7 | 9 | 23600 | 17600 | 74.58% | 2 | 22400 | R-410A
214094119 | 2.45 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | DM36A34+TDR | BGH96M080B3B | 29400 | 18 | 10.8 | 8.5 | 33800 | 27400 | 81.07% | 2.38 | 25400 | R-410A
213927962 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)37B44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
216687209 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF97MV510021DH | 45500 | 19 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
214063851 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24B34+TDR | BGH96M080B3B | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214064004 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B34+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
214331763 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4A | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214331778 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100C5B | 43500 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331944 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100D5B | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215683928 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 986TD42080C17*** | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30600 | R-454B
215683942 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4221AM*+UI | 88*TB60070C21*** | 33000 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
212846384 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | L(E,G)M48B4 |  | 46000 | 17.5 | 11.7 | 8.5 | 47000 | 44500 | 94.68% | 2.4 | 39000 | R-410A
214723115 | 1.4 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24HDN1-M15G | L(E,F)W30B4 |  | 16800 | 15.2 | 10.5 | 8.1 | 17900 | 12900 | 72.07% | 1.81 | 15000 | R-410A
214331767 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4B | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214331781 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100D5A | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331785 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100D5B | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331790 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M120D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331792 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M120D5B | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
211206971 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | TPLC120C20MP13 | 43500 | 19 | 12 | 9 | 44500 | 36200 | 81.35% | 2.14 | 41500 | R-410A
214331926 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331951 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M120D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214731135 | 1.41 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG7J936 | 916SA48060M17*** | 16900 | 16 | 10 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
214731144 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG9J936 | 926TC36040V17*** | 17200 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
214731153 | 1.43 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG31930 | 926TC48080V17*** | 17100 | 15.2 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
214320277 | 4.21 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | D(A,C,E)60C44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
214731210 | 2.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG9J936 | 926TC48080V17*** | 34600 | 16 | 9.5 | 8.1 | 36200 | 34400 | 95.03% | 2 | 28000 | R-410A
216687210 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF98MV508521UP | 45500 | 19 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
214063848 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24B34+TDR | BGH96M080B3A | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214063850 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M080B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214063857 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080B3B | 31000 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.31 | 24800 | R-410A
214063859 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M080C4B | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 26400 | 78.11% | 2.41 | 24800 | R-410A
214063984 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M060B3A | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214064000 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M080B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
215375428 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)30B36+TDR | BGH96M060B3B | 22400 | 18.4 | 11.8 | 8.7 | 19900 | 20000 | 100.5% | 2.9 | 25000 | R-410A
215472282 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV0X36A1 | D(A,C,E)48C34+TDR | S9V2C080U5PSC+RP | 33400 | 19.5 | 12 | 8.7 | 34200 | 28200 | 82.46% | 2.59 | 32400 | R-410A
215057523 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M48K4 |  | 30800 | 19 | 12 | 9.5 | 33000 | 24000 | 72.73% | 1.9 | 28000 | R-410A
214331853 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M080B3B | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331919 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3B | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
214331921 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331936 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
215684078 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 935CB48060C17*** | 33800 | 16 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
213753864 | 2.78 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | 59TP6C080V21**20 | 33400 | 16.4 | 9.8 | 8.1 | 37800 | 31400 | 83.07% | 2.72 | 28800 | R-410A
213780638 | 2.6 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X36L17A*+WALLCON | *80CTL0451712B* | 31200 | 16.5 | 10.5 | 8.1 | 33400 | 24600 | 73.65% | 1.8 | 31600 | R-410A
213780708 | 2.6 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X36L17A*+WALLCON | *96CTN0601714B* | 31200 | 16.5 | 10.5 | 8.1 | 33400 | 24600 | 73.65% | 1.82 | 31400 | R-410A
214331918 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080B3A | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331934 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100C5A | 43500 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331948 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M120D5A | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214723114 | 1.39 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24HDN1-M15G | A(E,F)W184+TDR |  | 16700 | 15.2 | 11.5 | 8.1 | 17800 | 12900 | 72.47% | 1.81 | 15000 | R-410A
214331858 | 2.68 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M080C4A | 32200 | 17.5 | 11 | 8.9 | 34200 | 26600 | 77.78% | 2.5 | 25000 | R-410A
216055839 | 2.62 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C20SMPS1 | 31400 | 18 | 10.5 | 8.1 | 31800 | 24200 | 76.1% | 2 | 26200 | R-454B
214331703 | 2.72 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080C4A | 32600 | 17.5 | 11 | 9 | 34200 | 26600 | 77.78% | 2.51 | 25000 | R-410A
215375413 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M100C5B | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 25400 | 74.71% | 2.43 | 27400 | R-410A
213286673 | 1.45 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CP1903A+TXV+TD |  | 17400 | 15.2 | 10.5 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
212675691 | 4.33 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | L(E,G)M60F4 |  | 52000 | 18 | 11.7 | 9.5 | 55000 | 48500 | 88.18% | 2.48 | 43500 | R-410A
214331760 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080B3B | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331761 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331794 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M120D5B | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
213885826 | 1.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | AE(D,N,U)+CM24A34+TDR |  | 21600 | 19.5 | 12.5 | 8.8 | 23600 | 27000 | 114.4% | 2.42 | 22200 | R-410A
215057504 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M36C4 |  | 31200 | 17 | 11 | 8.1 | 33000 | 24000 | 72.73% | 1.9 | 28000 | R-410A
215057513 | 2.68 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M36F4 |  | 32200 | 18 | 11.7 | 9 | 33200 | 24000 | 72.29% | 1.9 | 28000 | R-410A
213163582 | 2.45 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | H,FG32936+AEFE3A* |  | 29400 | 15.2 | 8.5 | 8.15 | 33200 | 27000 | 81.33% | 1.76 | 22600 | R-410A
214331920 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080B3B | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331922 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331937 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100C5B | 44000 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214331770 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080C4B | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331787 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M120D5A | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
215057510 | 2.68 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M36E4 |  | 32200 | 17.5 | 11.5 | 8.5 | 33200 | 24000 | 72.29% | 1.9 | 28000 | R-410A
214320275 | 4.21 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215375400 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.7 | 46500 | 35600 | 76.56% | 2.32 | 39000 | R-410A
214331758 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080B3A | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331915 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3A | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
215941763 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *97CTN1202422A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.95 | 43000 | R-454B
215057507 | 2.65 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M36D4 |  | 31800 | 17 | 11 | 8.1 | 33000 | 24000 | 72.73% | 1.9 | 28000 | R-410A
214331942 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M100D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215940323 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215057520 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | L(E,G)M48B4 |  | 31600 | 19 | 12 | 9.5 | 33200 | 24000 | 72.29% | 1.9 | 28000 | R-410A
215683892 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 83*CA36040C17*** | 34400 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
212624413 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM9Y080C16MP11 | 30600 | 18.1 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
214731219 | 2.93 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG7J936 | 926TC60100V21*** | 35200 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
215291864 | 1.92 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32930 | *92MSN0401712A* | 23000 | 16 | 9.5 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291866 | 1.92 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG32924 | *92MSN0401712A* | 23000 | 16 | 9.5 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291880 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG35936 | *92MSN0401712A* | 23600 | 16 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
214802756 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R801V0754A17DZ | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20200 | 71.13% | 2.62 | 21000 | R-410A
213780875 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**3721AL*+UI | 58TN*B090C21**20 | 32800 | 17 | 11 | 8.5 | 33000 | 25000 | 75.76% | 1.98 | 31600 | R-410A
215683596 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2417AM*+UI | 986TD42060C17*** | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215683698 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 88*TB48090C17*** | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
214331931 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5A | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 38500 | 83.7% | 2.27 | 35400 | R-410A
215375422 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M080B3B | 41000 | 17 | 11.6 | 8.7 | 43500 | 35000 | 80.46% | 2.38 | 39500 | R-410A
215375437 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M080B3B | 23400 | 18.5 | 12 | 9 | 20000 | 20000 | 100% | 2.86 | 25000 | R-410A
215375440 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C46+TDR | BGH96M080B3B | 23400 | 18.5 | 12 | 9 | 20000 | 20000 | 100% | 2.86 | 25000 | R-410A
214063920 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214063937 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M100D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214064070 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080B3A | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
214064071 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M080B3A | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214064087 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M100C5A | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214064103 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M120D5A | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
213885828 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | AE(D,N,U)+CM30B34+TDR |  | 22400 | 19.9 | 12.7 | 9.1 | 23800 | 26800 | 112.6% | 2.5 | 22200 | R-410A
214331691 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M060B3B | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331707 | 2.68 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M080C4B | 32200 | 17.5 | 11 | 8.9 | 34200 | 26600 | 77.78% | 2.5 | 25000 | R-410A
214331832 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M060B3A | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
215940373 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *97CTN0801716A* | 35400 | 21 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33400 | R-454B
215940493 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M24A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215942449 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X61M24A*+WALLCON | *97CMN0802120B* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215942529 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN0802120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215942479 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *80CSU0601716A* | 35800 | 22 | 12 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
216980137 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | L(E,G)M36FJ |  | 23400 | 19.6 | 13 | 9 | 24000 | 17400 | 72.5% | 2 | 21000 | R-454B
215683878 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3717AM*+UI | 88*TB48090C17*** | 34000 | 17.5 | 9.5 | 9 | 35800 | 25400 | 70.95% | 1.88 | 30800 | R-454B
215683898 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 88*TB36045C17*** | 34000 | 17.5 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.86 | 30800 | R-454B
214094141 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | DM59A44+TDR | BGH96M080C4B | 40500 | 17 | 11.5 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214063939 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M100D5B | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
207172522 | 2 | Yes | Yes | DUCANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | 48BP**+TXV | 80G1UH070BE12 | 24000 | 19 | 12 | 8.5 | 22400 | 18900 | 84.38% | 2.22 | 13700 | R-410A
214331949 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M120D5A | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
210693389 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC960603BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213885834 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | AE(D,N,U)+CM60B34+TDR |  | 43000 | 18.3 | 11.7 | 8.9 | 47000 | 45500 | 96.81% | 2.45 | 39500 | R-410A
215669233 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 987MC42080C17*** | 33600 | 17.5 | 9.5 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
212627002 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9V080C16MP12 | 31600 | 17.5 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
214848951 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | F,PE*E34925 |  | 17800 | 17 | 11 | 9 | 17100 | 19400 | 113.5% | 2.4 | 11500 | R-410A
214331874 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100C5B | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214063847 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M060B3B | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.34 | 24800 | R-410A
214331843 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A3G+TXV+TDR | BGH96M080B3A | 22200 | 18 | 11.8 | 8.4 | 23600 | 22200 | 94.07% | 2.17 | 19500 | R-410A
214331873 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D3G+TXV+TDR | BGH96M100C5B | 31000 | 18.5 | 11.8 | 9 | 34200 | 27600 | 80.7% | 2.51 | 25600 | R-410A
214331757 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080B3A | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331793 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M120D5B | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331923 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4A | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214331925 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
215683946 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4221AM*+UI | 88*TB60090C21*** | 33200 | 18 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 30800 | R-454B
215683964 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4221AM*+UI | 987MC66100C21*** | 33200 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.84 | 31000 | R-454B
210693372 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC960804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693377 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VM970804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214094133 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | DM42B34+TDR | BGH96M080C4B | 31600 | 17.5 | 10.9 | 8.6 | 33800 | 26400 | 78.11% | 2.42 | 24800 | R-410A
214063849 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30B34+TDR | BGH96M080B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
214063856 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D34+TDR | BGH96M080B3B | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214331788 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M120D5A | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215375398 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M080B3B | 41000 | 17 | 11.6 | 8.7 | 43500 | 35000 | 80.46% | 2.38 | 39500 | R-410A
216980141 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | L(E,G)M48FJ |  | 46000 | 18.5 | 11.9 | 9.5 | 48000 | 48500 | 101% | 2.1 | 37800 | R-454B
213785013 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**2417AL*+UI | 58TN*B070C17**16 | 23000 | 19.5 | 12.5 | 10 | 27000 | 20200 | 74.81% | 2.28 | 25200 | R-410A
213785029 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**2517AL*+UI | 58TN*B070C14**12 | 23800 | 20 | 13 | 10.5 | 26400 | 19800 | 75% | 2.52 | 24800 | R-410A
213785031 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**2517AL*+UI | 58TN*B070C17**16 | 24000 | 20 | 13 | 10.5 | 26400 | 19800 | 75% | 2.5 | 24800 | R-410A
213785047 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3014AL*+UI | 59TN6C040C14**10 | 22800 | 17.5 | 11.5 | 9.5 | 27200 | 20600 | 75.74% | 2.26 | 25600 | R-410A
213785097 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3621AL*+UI | 59MN7C080C17**14 | 23200 | 20 | 12.5 | 10 | 26600 | 19900 | 74.81% | 2.4 | 25000 | R-410A
213785099 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3621AL*+UI | 59MN7C100C21**22 | 23400 | 20 | 13 | 10 | 26600 | 19800 | 74.44% | 2.42 | 24800 | R-410A
215375427 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)30B34+TDR | BGH96M080B3B | 22400 | 18.4 | 11.8 | 8.7 | 19900 | 20000 | 100.5% | 2.9 | 25000 | R-410A
215375434 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M080B3B | 22400 | 18.4 | 11.8 | 8.5 | 19900 | 20000 | 100.5% | 2.92 | 25000 | R-410A
215375395 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080C4B | 39500 | 17 | 11.4 | 8.5 | 44000 | 34800 | 79.09% | 2.31 | 38500 | R-410A
215375416 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M100C5B | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 35400 | 76.96% | 2.27 | 38500 | R-410A
214063992 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B34+TDR | BGH96M060B3B | 22600 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214064015 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M080C4B | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 26400 | 78.11% | 2.41 | 24800 | R-410A
214064017 | 2.72 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M080C4B | 32600 | 17.5 | 11 | 9 | 34200 | 26600 | 77.78% | 2.51 | 25000 | R-410A
215683578 | 1.9 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2417AM*+UI | 83*CA36040C17*** | 22800 | 16.5 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20200 | R-454B
215940713 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M24A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215939643 | 2.67 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *97CTN0801716A* | 32000 | 19 | 10.5 | 9.5 | 35600 | 27400 | 76.97% | 1.98 | 31400 | R-454B
215939693 | 2.7 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CTN0801716A* | 32400 | 19.5 | 11 | 9.5 | 35200 | 27200 | 77.27% | 2 | 31000 | R-454B
215939743 | 2.78 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716B* | 33400 | 20.5 | 11.7 | 9.5 | 34400 | 26200 | 76.16% | 2.04 | 30200 | R-454B
215932047 | 2.68 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0601716A* | 32200 | 19.5 | 11 | 9.5 | 35000 | 27000 | 77.14% | 2 | 30800 | R-454B
215932667 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716A* | 34400 | 20.5 | 11.7 | 9.5 | 34400 | 26000 | 75.58% | 2.06 | 30000 | R-454B
216980134 | 1.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | L(E,G)M24BJ |  | 21000 | 18.7 | 12.4 | 8.1 | 23400 | 17400 | 74.36% | 2 | 22000 | R-454B
213927966 | 2.48 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)37E34+TDR |  | 29800 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215934987 | 2.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU1002120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 32800 | R-454B
215934837 | 2.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CTL0901716B* | 35600 | 22 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
215934957 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X48M21A*+WALLCON | *97CMN0601714B* | 34400 | 20.5 | 11 | 8.5 | 38000 | 27600 | 72.63% | 2.08 | 31400 | R-454B
215935057 | 2.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *95CSU0601716B* | 35400 | 21.5 | 12 | 8.5 | 38500 | 29000 | 75.32% | 2.02 | 33400 | R-454B
215292007 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG81936 | *92MSN0601714A* | 23600 | 17 | 10.5 | 8.5 | 24800 | 24000 | 96.77% | 2.02 | 18100 | R-410A
213785115 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3721AL*+UI | 58TN*B110C21**20 | 24200 | 20 | 13 | 10.5 | 26400 | 19700 | 74.62% | 2.54 | 24600 | R-410A
215669495 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL1102120B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215375429 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)30B36+TDR | BGH96M080B3B | 22400 | 18.4 | 11.8 | 8.7 | 19900 | 20000 | 100.5% | 2.9 | 25000 | R-410A
215375418 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M080B3B | 41000 | 17 | 11.6 | 8.7 | 43500 | 35000 | 80.46% | 2.38 | 39500 | R-410A
214094140 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | DM59A44+TDR | BGH96M080C4A | 40500 | 17 | 11.5 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214094142 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | DM59A44+TDR | BGH96M100C5A | 42500 | 17.5 | 11 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214064083 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M080C4B | 40500 | 17 | 11 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214064108 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M120D5B | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
213279292 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A46+TDR | TPLC100C16MP13 | 43000 | 16 | 11.5 | 8.2 | 44000 | 31200 | 70.91% | 3.16 | 30400 | R-410A
215375409 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M100C5B | 29800 | 18.5 | 11 | 8.7 | 34000 | 25400 | 74.71% | 2.43 | 27400 | R-410A
214063983 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B34+TDR | BGH96M060B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.23 | 19500 | R-410A
215291879 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG35936 | *92MSN0401712A* | 23600 | 16 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291890 | 1.92 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J924 | *92MSN0401712A* | 23000 | 16 | 9.5 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291899 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG1K936 | *92MSN0401712A* | 23600 | 16 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291938 | 1.92 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE30924 | *92MSN0601412A* | 23000 | 16 | 9.5 | 9 | 25400 | 25000 | 98.43% | 2.12 | 18500 | R-410A
215291972 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32930 | *92MSN0601714A* | 23400 | 17 | 10 | 8.5 | 25200 | 26000 | 103.2% | 2.24 | 18400 | R-410A
215291990 | 1.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE30924 | *92MSN0601714A* | 22400 | 17 | 9.5 | 8.5 | 24600 | 23200 | 94.31% | 1.96 | 18100 | R-410A
215375388 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M080C4B | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 24800 | 73.37% | 2.41 | 26400 | R-410A
215375390 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M060B3B | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 24800 | 73.81% | 2.34 | 26600 | R-410A
215375407 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 19500 | 82.63% | 2.17 | 22200 | R-410A
214595283 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CM36B36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 16900 | 71.01% | 1.97 | 19000 | R-410A
214595284 | 1.82 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CM36B36+TDR |  | 21800 | 15.2 | 11.9 | 8.8 | 23800 | 16900 | 71.01% | 1.75 | 19000 | R-410A
214595301 | 1.83 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B46+TDR |  | 22000 | 15.2 | 11.9 | 8.8 | 23800 | 16900 | 71.01% | 1.99 | 19400 | R-410A
214595303 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C36+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 19400 | 80.83% | 1.98 | 19400 | R-410A
210693333 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VS960805CUA* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693350 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VS960603BUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214094104 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | AE(D,N,U)+DM36A34+TDR |  | 22200 | 19.9 | 12.7 | 8.9 | 23600 | 27000 | 114.4% | 2.45 | 22200 | R-410A
214094135 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | DM42B34+TDR | BGH96M100C5B | 30400 | 18.3 | 11.7 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
214063986 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M060B3A | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214064003 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24B34+TDR | BGH96M080B3B | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
216494154 | 3.58 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)4824G1K*+TXV | 88*TB36070C14*** | 43000 | 19 | 11 | 8.5 | 47000 | 35000 | 74.47% | 1.8 | 35200 | R-454B
213612072 | 3.21 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | D(A,C,E)48B44+TDR | R802V1005A21DZ | 38500 | 15.4 | 11.7 | 8.1 | 40000 | 30000 | 75% | 2.93 | 28600 | R-410A
212675690 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | L(E,G)M48G4 |  | 47000 | 18.5 | 12 | 9.5 | 48000 | 46000 | 95.83% | 2.61 | 40000 | R-410A
215375424 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.7 | 46500 | 35600 | 76.56% | 2.32 | 39000 | R-410A
215669061 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *97CMN0802120B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.88 | 30400 | R-454B
215669195 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0802120B* | 33800 | 17.5 | 9.5 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215670079 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN1202422B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215670299 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0802120B* | 34200 | 16.5 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215670399 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0451712B* | 34200 | 16.5 | 9 | 8.5 | 35000 | 25200 | 72% | 1.78 | 30400 | R-454B
215670449 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0902120B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
214064001 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36D34+TDR | BGH96M080B3A | 23000 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214064024 | 2.53 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M100C5A | 30400 | 18.5 | 11.7 | 8.7 | 34000 | 27400 | 80.59% | 2.43 | 25400 | R-410A
213160923 | 1.46 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | PL36H***P039+AEFE3A* |  | 17500 | 17 | 10.5 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
213885827 | 1.73 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24HDN1-M15G | AE(D,N,U)+CM30B24+TDR |  | 20800 | 15.6 | 11.2 | 8.5 | 23600 | 23400 | 99.15% | 2.48 | 20200 | R-410A
214063931 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214064074 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080B3B | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
213206247 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A045E17**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.97 | 19100 | R-410A
213206383 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58TP*A090V21**20 | 23000 | 16.9 | 10.3 | 8.1 | 25400 | 19800 | 77.95% | 2.97 | 18600 | R-410A
213206408 | 1.97 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC2D040E14**10 | 23600 | 15.5 | 9.9 | 8.1 | 26000 | 20400 | 78.46% | 2.89 | 19100 | R-410A
213206474 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC2D100E21**20 | 23800 | 17 | 10.4 | 8.1 | 26000 | 20200 | 77.69% | 2.98 | 19000 | R-410A
213206531 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC5B060E17**14 | 23800 | 16.5 | 10.4 | 8.1 | 26000 | 20200 | 77.69% | 2.76 | 19000 | R-410A
213206606 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59TP6B060V17**14 | 23800 | 16.5 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.75 | 19100 | R-410A
215291999 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HE8J936 | *92MSN0601714A* | 23400 | 17 | 10.5 | 8.5 | 24800 | 23800 | 95.97% | 2.02 | 18100 | R-410A
215292008 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG81936 | *92MSN0601714A* | 23600 | 17 | 10.5 | 8.5 | 24800 | 24000 | 96.77% | 2.02 | 18100 | R-410A
215292013 | 1.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG31924 | *92MSN0801716A* | 22400 | 17 | 10 | 8.5 | 24600 | 24200 | 98.37% | 2.04 | 18100 | R-410A
215292022 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG32924 | *92MSN0801716A* | 23200 | 17 | 10 | 9 | 25200 | 26400 | 104.8% | 2.3 | 18300 | R-410A
213206249 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 58S(B,C)*A070E14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.94 | 19100 | R-410A
214595155 | 1.95 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24G4 |  | 23400 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212841209 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | A(E,F)M604+TDR |  | 46500 | 18 | 11.7 | 9 | 47500 | 45000 | 94.74% | 2.47 | 39500 | R-410A
214731155 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG7J936 | 926TC48080V17*** | 17500 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215375431 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M080B3B | 22400 | 18.4 | 11.8 | 8.5 | 19900 | 20000 | 100.5% | 2.92 | 25000 | R-410A
215375432 | 2.48 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M100C5B | 29800 | 18 | 11 | 8.7 | 25400 | 25600 | 100.8% | 3.03 | 32000 | R-410A
210693351 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC960603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214802757 | 2.28 | Yes | No | RHEEM | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)30B34+TDR | R801V0754A17UH | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 20000 | 70.42% | 2.62 | 20800 | R-410A
214064026 | 2.52 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B34+TDR | BGH96M100C5B | 30200 | 18.5 | 11 | 8.8 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
214584500 | 1.87 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36D34+TDR |  | 22400 | 15.2 | 12 | 9 | 24000 | 22600 | 94.17% | 2 | 19400 | R-410A
215375420 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.7 | 46500 | 35600 | 76.56% | 2.32 | 39000 | R-410A
214063915 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M080B3B | 40500 | 17 | 11 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
215292105 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG9J936 | *92MSN0802120A* | 23400 | 17 | 10.5 | 8.5 | 24600 | 24400 | 99.19% | 2.08 | 18000 | R-410A
215292123 | 1.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HE31930 | *92MSN1002120A* | 22600 | 17 | 10 | 8.5 | 24800 | 23800 | 95.97% | 2.02 | 18100 | R-410A
215292130 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HE32936 | *92MSN1002120A* | 23000 | 17 | 10 | 8.5 | 24800 | 23800 | 95.97% | 2.02 | 18100 | R-410A
215292189 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE34936 | *96MSN0261410A* | 23400 | 16 | 10 | 8.5 | 24800 | 24200 | 97.58% | 2.04 | 18200 | R-410A
215292214 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG80936 | *96MSN0261410A* | 23400 | 16 | 10 | 8.5 | 24800 | 24200 | 97.58% | 2.04 | 18200 | R-410A
215292241 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE34936 | *96MSN0401410A* | 23600 | 16 | 10 | 8.5 | 24600 | 23600 | 95.93% | 1.98 | 18200 | R-410A
215292257 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG8J936 | *96MSN0401410A* | 23400 | 16 | 10 | 8.5 | 24600 | 23600 | 95.93% | 1.98 | 18200 | R-410A
215292273 | 1.9 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG31924 | *96MSN0401712A* | 22800 | 15.2 | 9.5 | 8.5 | 25600 | 24400 | 95.31% | 2.04 | 18700 | R-410A
215375414 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080B3B | 39500 | 17 | 11.4 | 8.5 | 43000 | 34800 | 80.93% | 2.33 | 39000 | R-410A
214063918 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080C4A | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214063921 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214063936 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M100D5A | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
216980136 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | L(E,G)M24JJ |  | 23000 | 19.5 | 13 | 9 | 23800 | 17400 | 73.11% | 2 | 22200 | R-454B
216687200 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF97MV510021DH | 34200 | 21 | 12 | 10 | 34200 | 29400 | 85.96% | 2 | 30000 | R-454B
214063942 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M120D5A | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214063949 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M120D5B | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214064081 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M080C4A | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214063845 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M060B3B | 23200 | 18 | 12 | 9 | 24000 | 22200 | 92.5% | 2.28 | 19600 | R-410A
214063861 | 2.72 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M080C4B | 32600 | 17.5 | 11 | 9 | 34200 | 26600 | 77.78% | 2.51 | 25000 | R-410A
214063995 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M060B3B | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 26600 | 79.17% | 2.34 | 24800 | R-410A
214063996 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24B34+TDR | BGH96M080B3A | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214063997 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30B34+TDR | BGH96M080B3A | 22200 | 18 | 11.8 | 8.7 | 23800 | 22200 | 93.28% | 2.21 | 19500 | R-410A
214064010 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A34+TDR | BGH96M080C4A | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 26400 | 78.11% | 2.41 | 24800 | R-410A
214063927 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M100C5A | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214064077 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214094144 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | DM59A44+TDR | BGH96M100D5A | 43000 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214094146 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | DM59A44+TDR | BGH96M120D5A | 43000 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214094159 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | DM59A44+TDR | BGH96M080B3B | 40500 | 17 | 11.5 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214094161 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | DM59A44+TDR | BGH96M080C4B | 40500 | 17 | 11.5 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214064078 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M080C4A | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214064096 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M100D5A | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
210693376 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VM970803BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693373 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VS960805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214723116 | 1.43 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24HDN1-M15G | L(E,F)W30D4 |  | 17100 | 15.2 | 10.5 | 8.1 | 17900 | 12900 | 72.07% | 1.81 | 15000 | R-410A
213785648 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*3612AL*+UI | 59CU5B060C17**16 | 33000 | 18 | 11 | 8.5 | 37200 | 26400 | 70.97% | 2 | 31800 | R-410A
213785682 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*4212AL*+UI | 59MN7C060C17**14 | 33000 | 18 | 11 | 8.5 | 37000 | 26200 | 70.81% | 2 | 31600 | R-410A
213785684 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*4212AL*+UI | 59MN7C080C17**14 | 33200 | 18 | 11.5 | 8.5 | 36800 | 26200 | 71.2% | 2 | 31400 | R-410A
213785714 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*4812AL*+UI | 59MN7C060C17**14 | 33200 | 18 | 11 | 8.5 | 36800 | 26200 | 71.2% | 2 | 31400 | R-410A
213927972 | 3.38 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)49C44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
214331927 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080C4B | 39500 | 17 | 11.4 | 8.5 | 44000 | 38500 | 87.5% | 2.31 | 34800 | R-410A
214331932 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100C5A | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
213753062 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59TP6C100V21**22 | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.94 | 19100 | R-410A
213206305 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A090E17**14 | 23800 | 17 | 10.3 | 8.1 | 25800 | 20000 | 77.52% | 3 | 18900 | R-410A
213779168 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L21A*+WALLCON | *96CTN1002122B* | 31800 | 17 | 11 | 8.1 | 32800 | 24400 | 74.39% | 1.88 | 31200 | R-410A
213779318 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X43L21A*+WALLCON | *97CMN0801714B* | 32800 | 17 | 11 | 8.1 | 33000 | 25200 | 76.36% | 1.96 | 31800 | R-410A
213779368 | 2.67 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L21A*+WALLCON | *80CTL0451712B* | 32000 | 16.5 | 10.5 | 8.1 | 32800 | 25200 | 76.83% | 1.92 | 31800 | R-410A
213779418 | 2.68 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L21A*+WALLCON | *95CSU0601716B* | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.94 | 31600 | R-410A
215292280 | 1.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32930 | *96MSN0401712A* | 22600 | 16 | 9 | 8.5 | 24800 | 24600 | 99.19% | 2.08 | 18200 | R-410A
215292307 | 1.9 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96MSN0401712A* | 22800 | 16 | 9 | 8.5 | 24600 | 23800 | 96.75% | 2 | 18200 | R-410A
215292339 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG33936 | *96MSN0601412A* | 23400 | 16 | 10 | 8.5 | 24600 | 23800 | 96.75% | 2 | 18100 | R-410A
212480167 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 59TP6B080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
213613380 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24C4 |  | 23400 | 16 | 10 | 9 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
213613391 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36C4 |  | 23800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212479861 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 58S(B,C)*A070E17**16 | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212479878 | 2.07 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L159 | 58S(B,C)*A070E17**16 | 24800 | 16 | 10.5 | 8.1 | 25200 | 21800 | 86.51% | 1.82 | 18400 | R-410A
212479927 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P149 | 58SP*A070V17**16 | 24000 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
212479961 | 2.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 58SU*A060E17**16 | 25000 | 17 | 10.5 | 8.5 | 25000 | 21400 | 85.6% | 1.82 | 18300 | R-410A
212479980 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 58TP*A070V17**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
214584495 | 1.83 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B44+TDR |  | 22000 | 15.2 | 11.9 | 8.8 | 23800 | 16900 | 71.01% | 1.99 | 19400 | R-410A
214584496 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)30D34+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 22400 | 93.33% | 2 | 19400 | R-410A
214584497 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C34+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 19400 | 80.83% | 1.98 | 19400 | R-410A
216687167 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF95SV306017M4 | 22800 | 21 | 13 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
213927954 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)42D34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213206547 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC5B080E17**16 | 23800 | 16 | 9.8 | 8.1 | 26200 | 20200 | 77.1% | 2.71 | 19100 | R-410A
214584514 | 1.85 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)30D34+TDR |  | 22200 | 15.2 | 11.9 | 8.9 | 24000 | 29600 | 123.3% | 1.96 | 19400 | R-410A
215939893 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN1002122A* | 34400 | 20.5 | 12 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 30000 | R-454B
213613383 | 1.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24F4 |  | 22800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214064090 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M100C5B | 41500 | 17.5 | 11.4 | 8.5 | 46000 | 38500 | 83.7% | 2.27 | 35400 | R-410A
213752804 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC2E060M17**14 | 23400 | 17.5 | 10 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
213752845 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC6A026M14**10 | 23200 | 16.5 | 10 | 8.5 | 27000 | 20600 | 76.3% | 2.86 | 19500 | R-410A
213752865 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | 59SC6A040M17**12 | 23200 | 16 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19200 | R-410A
213752870 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC6A040M17**12 | 23200 | 16 | 9.5 | 8.5 | 26400 | 20400 | 77.27% | 2.84 | 19200 | R-410A
213752956 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SP6A080V17**16 | 23000 | 16.9 | 10.3 | 8.5 | 25600 | 19900 | 77.73% | 2.98 | 18700 | R-410A
213206258 | 1.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 58S(B,C)*A070E14**12 | 23800 | 17 | 10 | 8.1 | 26200 | 20200 | 77.1% | 2.94 | 19100 | R-410A
213206267 | 1.93 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 58S(B,C)*A070E17**12 | 23200 | 17 | 10 | 8.1 | 25600 | 20000 | 78.12% | 2.94 | 18800 | R-410A
213206510 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | 59SC5B040E17**12 | 23800 | 15.2 | 9.5 | 8.1 | 26400 | 20400 | 77.27% | 2.85 | 19300 | R-410A
215289856 | 1.36 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG30924 | *96MSN0401712A* | 16300 | 15.2 | 9.5 | 8.5 | 16700 | 19000 | 113.8% | 2.32 | 11300 | R-410A
215289870 | 1.46 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG80936 | *96MSN0401712A* | 17500 | 15.2 | 10.5 | 8.5 | 17100 | 18800 | 109.9% | 2.3 | 11500 | R-410A
215289871 | 1.46 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG80936 | *96MSN0401712A* | 17500 | 15.2 | 10.5 | 8.5 | 17100 | 18800 | 109.9% | 2.3 | 11500 | R-410A
215289886 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG32936 | *96MSN0601412A* | 17400 | 16 | 10.5 | 8.5 | 17000 | 19400 | 114.1% | 2.38 | 11500 | R-410A
215289888 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE32936 | *96MSN0601412A* | 17400 | 16 | 10.5 | 8.5 | 17000 | 19400 | 114.1% | 2.38 | 11500 | R-410A
215289920 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE24936 | *96MSN0601716A* | 17200 | 16 | 10.5 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
215289938 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE33936 | *96MSN0601716A* | 17100 | 16 | 10.5 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
215289939 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG34936 | *96MSN0601716A* | 17200 | 16 | 10.5 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
215289940 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG34936 | *96MSN0601716A* | 17200 | 16 | 10.5 | 8.5 | 16500 | 19000 | 115.2% | 2.32 | 11300 | R-410A
215289973 | 1.44 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32930 | *96MSN0801716A* | 17300 | 16 | 10.5 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11500 | R-410A
215289987 | 1.47 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE34936 | *96MSN0801716A* | 17600 | 16 | 11 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11500 | R-410A
215290023 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE32936 | *96VTN0401410A* | 17100 | 16 | 10 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290038 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE7J924 | *96VTN0401410A* | 17200 | 16 | 10 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290105 | 1.46 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG32924 | *96VTN0401712A* | 17500 | 15.2 | 10 | 8.5 | 17100 | 18700 | 109.4% | 2.28 | 11500 | R-410A
215290106 | 1.46 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG32936 | *96VTN0401712A* | 17500 | 15.2 | 10 | 8.5 | 17100 | 18700 | 109.4% | 2.28 | 11500 | R-410A
215290120 | 1.41 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG30924 | *96VTN0401712A* | 16900 | 15.2 | 10 | 8.5 | 17100 | 18400 | 107.6% | 2.26 | 11500 | R-410A
215290156 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG34936 | *96VTN0401712B* | 17200 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290171 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG8J936 | *96VTN0401712B* | 17200 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290172 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE8J936 | *96VTN0401712B* | 17200 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
215290221 | 1.44 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE23936 | *96VTN0601412B* | 17300 | 16 | 10.5 | 8.5 | 16900 | 19400 | 114.8% | 2.38 | 11400 | R-410A
215290237 | 1.43 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE32936 | *96VTN0601412B* | 17200 | 16 | 10.5 | 8.5 | 16900 | 19400 | 114.8% | 2.38 | 11400 | R-410A
215290240 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE33936 | *96VTN0601412B* | 17400 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215290271 | 1.43 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE31924 | *96VTN0601714A* | 17100 | 15.2 | 10 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11400 | R-410A
215375411 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080B3B | 31000 | 17.5 | 10.5 | 8.6 | 33600 | 24800 | 73.81% | 2.31 | 26600 | R-410A
214063938 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M100D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214064072 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M080B3A | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214731162 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG31930 | 926TC30040V14*** | 22600 | 16 | 9 | 8.5 | 25400 | 26800 | 105.5% | 2.3 | 18500 | R-410A
214731178 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG35936 | 926TC48060V17*** | 24000 | 16 | 10.5 | 9 | 24400 | 22800 | 93.44% | 1.92 | 18100 | R-410A
210693346 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VS800805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214331789 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M120D5A | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215375397 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M120D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 35400 | 76.13% | 2.27 | 38500 | R-410A
213286708 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | CE3005C+TXV |  | 29800 | 15.2 | 8.5 | 8.2 | 33200 | 27000 | 81.33% | 1.78 | 22600 | R-410A
212509291 | 1.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | C24A***L039 | 58TN*A070C14**12 | 22600 | 21 | 12.5 | 9 | 25400 | 19600 | 77.17% | 2.32 | 24200 | R-410A
215684060 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 83*CA60100C21*** | 34000 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
215290274 | 1.43 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE31930 | *96VTN0601714A* | 17100 | 15.2 | 10 | 8.5 | 17000 | 18700 | 110% | 2.3 | 11400 | R-410A
215290337 | 1.38 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE30924 | *96VTN0601716B* | 16600 | 15.2 | 10 | 8.5 | 16800 | 19100 | 113.7% | 2.34 | 11400 | R-410A
215290354 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GE24936 | *96VTN0801716A* | 17400 | 16 | 10.5 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290372 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG34936 | *96VTN0801716A* | 17400 | 16 | 10.5 | 8.5 | 16700 | 18800 | 112.6% | 2.3 | 11300 | R-410A
215290391 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG80936 | *96VTN0801716A* | 17500 | 16 | 10.5 | 8.5 | 16500 | 18200 | 110.3% | 2.24 | 11200 | R-410A
215290404 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | H,GG32936 | *96VTN0801716B* | 17400 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215290424 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG7J924 | *96VTN0801716B* | 17500 | 16 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
214331917 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M080B3A | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
214331940 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M100D5A | 43500 | 17.5 | 11.6 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215375425 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M120D5B | 43500 | 17.5 | 11.6 | 8.9 | 47000 | 35600 | 75.74% | 2.29 | 38500 | R-410A
215375402 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M080B3B | 41000 | 17 | 11.6 | 8.7 | 43500 | 35000 | 80.46% | 2.38 | 39500 | R-410A
212480062 | 2.05 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 59SC5B080E17**16 | 24600 | 15.2 | 10 | 8.5 | 25200 | 21600 | 85.71% | 1.8 | 18400 | R-410A
210693318 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VC960803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693366 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC800805C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214063941 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M100D5B | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214064084 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M080C4B | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214064091 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B44+TDR | BGH96M100C5B | 43000 | 17.5 | 11.6 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
214064093 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M100C5B | 43500 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
216734698 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VSN0401712B* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
215290423 | 1.4 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE30924 | *96VTN0801716B* | 16800 | 15.2 | 10.5 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215669403 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6024AM*+UI | 986TD66100C21*** | 34400 | 18 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
216980132 | 1.38 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | L(E,G)M24AJ |  | 16600 | 15.3 | 11.4 | 8.1 | 18000 | 12900 | 71.67% | 1.81 | 14800 | R-454B
214723130 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | L(E,F)W36B4 |  | 21800 | 18 | 11.7 | 8.5 | 23600 | 17600 | 74.58% | 2 | 22400 | R-410A
210693317 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VC960603BNB* | 33600 | 18 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693349 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC960403BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214595317 | 1.83 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24C46+TDR |  | 22000 | 15.2 | 11.9 | 8.8 | 24000 | 28000 | 116.7% | 1.9 | 19400 | R-410A
214331764 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080C4A | 40500 | 17 | 11 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331779 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M100D5A | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
214331928 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080C4B | 40500 | 17 | 11 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331930 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M080C4B | 41500 | 17 | 11.7 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
213779438 | 2.68 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L21A*+WALLCON | *97CMN0801714B* | 32200 | 17 | 11 | 8.1 | 32600 | 25000 | 76.69% | 1.94 | 31600 | R-410A
213779488 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L24A*+WALLCON | *80CTL0902120B* | 32400 | 17 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213779518 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L24A*+WALLCON | *97CMN1002122B* | 32400 | 17 | 11 | 8.5 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213779538 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X48L24A*+WALLCON | *96CTN1002122B* | 32400 | 17 | 11 | 8.5 | 32200 | 24800 | 77.02% | 1.98 | 31200 | R-410A
213779588 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X60L24A*+WALLCON | *97CMN1002122B* | 32800 | 17.5 | 11.5 | 8.1 | 31800 | 24600 | 77.36% | 1.98 | 30800 | R-410A
213779718 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X61L21A*+WALLCON | *96CTN0601714B* | 33000 | 17 | 11 | 8.1 | 32200 | 25000 | 77.64% | 1.96 | 31400 | R-410A
215683630 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3017AM*+UI | 88*TB48070C17*** | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.96 | 20200 | R-454B
215683662 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3617AM*+UI | 986TD42060C17*** | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.96 | 20000 | R-454B
212675693 | 3.92 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M15G | L(E,G)M48G4 |  | 47000 | 15.5 | 10 | 8.2 | 47000 | 41000 | 87.23% | 2.3 | 37000 | R-410A
207455353 | 3.75 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LH40/61W9 | EL296UH110XV60C* | 45000 | 20 | 12 | 9.2 | 43500 | 37000 | 85.06% | 1.82 | 44500 | R-410A
214731160 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG9J936 | 916SA48060M17*** | 23600 | 17 | 10 | 9 | 24200 | 23200 | 95.87% | 1.96 | 17900 | R-410A
210693367 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC801005C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215683896 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 83*CA60100C21*** | 34400 | 17.5 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215683980 | 2.87 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 88*TB48070C17*** | 34400 | 18 | 10 | 8.1 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215684062 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 88*TB36045C17*** | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215684064 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 88*TB36070C14*** | 33800 | 16.5 | 9 | 8.5 | 35800 | 25400 | 70.95% | 1.78 | 30800 | R-454B
215684098 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 986TD42080C17*** | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
212480143 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV | 59TP6B040V17**12 | 23200 | 16 | 10 | 8.5 | 24200 | 23200 | 95.87% | 1.94 | 18000 | R-410A
214595153 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24E4 |  | 22600 | 15.2 | 9.5 | 8.1 | 26200 | 23400 | 89.31% | 1.92 | 19200 | R-410A
210693382 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC800604B*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693314 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VC800604B*A* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693332 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC960804CNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693368 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC960403BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693398 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VM971005CNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216794592 | 3.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2D120D5VSB+LRP | 40500 | 20 | 11.7 | 9 | 45500 | 41500 | 91.21% | 2.63 | 49500 | R-454B
210693362 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VS800604BUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212674056 | 2.87 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48B4 |  | 34400 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
210693312 | 2.83 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+MBVC1201**-1A*+TXV |  | 34000 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693319 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VM970603BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693328 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC960403BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693369 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VS960603BUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693387 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC960403BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693326 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC800805C*A* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693399 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VM971205DNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213206483 | 1.92 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC5B026E14**10 | 23000 | 16.5 | 10 | 8.1 | 25800 | 20000 | 77.52% | 2.86 | 18900 | R-410A
213206506 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | 59SC5B040E17**12 | 23800 | 15.2 | 9.5 | 8.1 | 26400 | 20400 | 77.27% | 2.85 | 19300 | R-410A
213206508 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30C44+TDR | 59SC5B040E17**12 | 23800 | 15.2 | 9.5 | 8.1 | 26400 | 20400 | 77.27% | 2.85 | 19300 | R-410A
214389571 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | AEW254+TDR |  | 23000 | 16 | 10 | 8.5 | 26000 | 23400 | 90% | 2.77 | 19000 | R-410A
213785129 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**4221AL*+UI | 58TN*B045C17**12 | 23400 | 19.5 | 12.5 | 10 | 26600 | 20000 | 75.19% | 2.4 | 25000 | R-410A
213785163 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**4321AL*+UI | 58TN*B045C17**12 | 24000 | 19.5 | 13 | 10.5 | 26600 | 19900 | 74.81% | 2.5 | 25000 | R-410A
213785181 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**4321AL*+UI | 59TN6C080C17**14 | 24000 | 20 | 13 | 10.5 | 26400 | 19800 | 75% | 2.52 | 24800 | R-410A
213785215 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*3612AL*+UI | 58TN*B045C17**12 | 23600 | 18.5 | 12.5 | 9 | 26800 | 20000 | 74.63% | 2.44 | 25000 | R-410A
215291859 | 1.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HG31930 | *92MSN0401712A* | 22600 | 15.2 | 9.5 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291860 | 1.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31924 | *92MSN0401712A* | 22600 | 15.2 | 9.5 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291875 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *92MSN0401712A* | 23600 | 16 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291877 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE34936 | *92MSN0401712A* | 23600 | 16 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291878 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HE34936 | *92MSN0401712A* | 23600 | 16 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.96 | 18200 | R-410A
215291912 | 1.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31924 | *92MSN0601412A* | 22800 | 16 | 10 | 8.5 | 24800 | 23400 | 94.35% | 1.98 | 18200 | R-410A
213785382 | 2.78 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**3717AL*+UI | 58TN*B090C17**16 | 33400 | 19 | 11.7 | 9 | 36800 | 26000 | 70.65% | 2.02 | 31400 | R-410A
213785400 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**3721AL*+UI | 58TN*B090C21**20 | 33800 | 19 | 12 | 9 | 36400 | 25600 | 70.33% | 2.04 | 30800 | R-410A
210693363 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC800604B*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
207455382 | 3.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LH42/62W9 | SL280UH080NV60C* | 46000 | 20 | 12.5 | 9.4 | 41500 | 35800 | 86.27% | 1.9 | 41000 | R-410A
207455430 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LH42/62W9 | SL297UH080NV60C* | 45500 | 20 | 12 | 9.4 | 42000 | 36000 | 85.71% | 1.88 | 41000 | R-410A
210609974 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | AMVE36CP1400A* |  | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215683912 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 935CB60080C21*** | 34400 | 17.5 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215683930 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 986TD66100C21*** | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215683996 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 987MC42060C17*** | 34200 | 17.5 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.88 | 30600 | R-454B
215684080 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 935CB60080C21*** | 34000 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
215684096 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 986TD42060C17*** | 33600 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 30800 | R-454B
214838454 | 2.9 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | L(E,G)M36E4 |  | 34800 | 17 | 10.2 | 8.1 | 34800 | 31000 | 89.08% | 1.9 | 35000 | R-410A
215941603 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN0802120A* | 44500 | 20 | 11 | 8.1 | 52000 | 38000 | 73.08% | 1.9 | 43500 | R-454B
212479917 | 2.05 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P299 | 58SP*A070V17**16 | 24600 | 17 | 10.5 | 8.5 | 23800 | 20800 | 87.39% | 1.78 | 17600 | R-410A
212479933 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 58SP*A070V17**16 | 24000 | 17 | 10 | 8.5 | 24400 | 22400 | 91.8% | 1.9 | 18000 | R-410A
212479974 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 58TP*A070V17**16 | 24000 | 17 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
212480035 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 59SC2D080E17**16 | 24200 | 17 | 10.5 | 8.1 | 24600 | 22400 | 91.06% | 1.88 | 18100 | R-410A
212480158 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P149 | 59TP6B080V17**16 | 24200 | 16 | 10.5 | 8.1 | 24600 | 22600 | 91.87% | 1.9 | 18100 | R-410A
213927956 | 3.33 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)60B44+TDR |  | 40000 | 15.55 | 11.4 | 8.5 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
214625033 | 2.82 | Yes | No | BRYANT | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)42D24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 27600 | 31600 | 114.5% | 1.85 | 27400 | R-410A
214731157 | 1.93 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG31930 | 916SA48060M17*** | 23200 | 16 | 9.5 | 9.5 | 25000 | 24400 | 97.6% | 2.04 | 18400 | R-410A
214731174 | 1.92 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG7J936 | 926TC36060V14*** | 23000 | 17 | 9.5 | 8.5 | 24600 | 23600 | 95.93% | 2 | 18100 | R-410A
213927948 | 2.43 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)30C44+TDR |  | 29200 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
213796970 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P429+CBPE3A* |  | 23600 | 16 | 10 | 8.7 | 24800 | 22600 | 91.13% | 1.86 | 18200 | R-410A
214731169 | 1.95 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG7J936 | 926TC36040V17*** | 23400 | 16 | 9.5 | 8.5 | 25400 | 25800 | 101.6% | 2.18 | 18500 | R-410A
214731176 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG81936 | 926TC36060V14*** | 23600 | 17 | 10 | 8.5 | 24600 | 23600 | 95.93% | 2 | 18100 | R-410A
214731196 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG81936 | 926TC60100V21*** | 23600 | 17 | 10.5 | 8.5 | 24600 | 24200 | 98.37% | 2.04 | 18100 | R-410A
211871491 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PE31(1,2)30+TXV | 59SC2D080E17**16 | 23800 | 17 | 10 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
215669263 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 986TD42060C17*** | 33600 | 17.5 | 9.5 | 9 | 35200 | 25400 | 72.16% | 1.88 | 30600 | R-454B
214064076 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D44+TDR | BGH96M080B3B | 41500 | 17 | 11.7 | 8.8 | 43500 | 39500 | 90.8% | 2.4 | 35000 | R-410A
215375441 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C46+TDR | BGH96M100C5B | 31200 | 18.5 | 11.9 | 9 | 25600 | 25600 | 100% | 2.98 | 32000 | R-410A
216735087 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *95CSU0601716B* | 22800 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
212507769 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | L(E,G)M48A4 |  | 45500 | 17 | 11.2 | 8.5 | 47000 | 44500 | 94.68% | 2.4 | 39000 | R-410A
215375417 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M120D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 35400 | 76.13% | 2.27 | 38500 | R-410A
216770088 | 1.98 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*C009AS3 | *UHMC100CCV4 | 23800 | 17.5 | 13 | 9 | 21400 | 16900 | 78.97% | 2.08 | 15100 | R-454B
216734472 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MSU0601716A* | 22400 | 16.5 | 11 | 8.5 | 20800 | 18600 | 89.42% | 1.96 | 17500 | R-454B
215350396 | 3.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | AE*L+DM59A44+TDR |  | 43000 | 18.2 | 11 | 9.1 | 47500 | 46000 | 96.84% | 2.5 | 40000 | R-410A
214864385 | 2.62 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE*L+CM36A34+TDR |  | 31400 | 18.3 | 10.3 | 8.4 | 33000 | 23200 | 70.3% | 2.1 | 24600 | R-410A
214595140 | 1.46 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M194+TDR |  | 17500 | 15.2 | 9.8 | 8.2 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
212851681 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | L(E,G)M48B4 |  | 45000 | 17 | 10 | 8.5 | 46500 | 41500 | 89.25% | 2.45 | 37000 | R-410A
214094152 | 3.5 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | DM59A44+TDR | BGH96M100C5A | 42000 | 17.5 | 10 | 8.1 | 47000 | 36000 | 76.6% | 2.48 | 34000 | R-410A
214094153 | 3.5 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | DM59A44+TDR | BGH96M100C5B | 42000 | 17.5 | 10 | 8.1 | 47000 | 36000 | 76.6% | 2.48 | 34000 | R-410A
215289578 | 1.43 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HE33936 | *92MSN0401712A* | 17100 | 15.2 | 10 | 8.5 | 16700 | 19000 | 113.8% | 2.32 | 11300 | R-410A
214094157 | 3.54 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | DM59A44+TDR | BGH96M120D5B | 42500 | 17.5 | 10.9 | 8.1 | 47000 | 36200 | 77.02% | 2.48 | 34200 | R-410A
215669125 | 2.78 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0451712B* | 33400 | 17.5 | 9.5 | 9 | 35200 | 25400 | 72.16% | 1.88 | 30600 | R-454B
215669225 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0602120B* | 33600 | 17.5 | 9.5 | 9 | 35200 | 25200 | 71.59% | 1.9 | 30400 | R-454B
215669255 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN1002122B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215669405 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1002122B* | 34400 | 18 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
212841205 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | AFM474+TDR |  | 46500 | 18 | 11.7 | 9 | 47500 | 45000 | 94.74% | 2.47 | 39500 | R-410A
214331689 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M060B3B | 22600 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214331693 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M080B3A | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
214331857 | 2.72 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080C4A | 32600 | 17.5 | 11 | 9 | 34200 | 26600 | 77.78% | 2.51 | 25000 | R-410A
214331866 | 2.52 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36B3G+TXV+TDR | BGH96M100C5A | 30200 | 18.5 | 11 | 8.8 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
214331941 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100D5A | 44500 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
212498514 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CE2403C+TXV |  | 23800 | 17 | 10 | 8.85 | 25600 | 25400 | 99.22% | 2.14 | 18500 | R-410A
214094154 | 3.54 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | DM59A44+TDR | BGH96M100D5A | 42500 | 17.5 | 10.9 | 8.1 | 47000 | 36200 | 77.02% | 2.48 | 34200 | R-410A
215669385 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1002122B* | 34400 | 18 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215669485 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0901716B* | 34800 | 18.5 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215375399 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M080C4B | 41000 | 17 | 11.6 | 8.7 | 44500 | 35000 | 78.65% | 2.37 | 39000 | R-410A
214723127 | 1.78 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | L(E,F)W30D4 |  | 21400 | 18 | 11.7 | 8.5 | 23600 | 17600 | 74.58% | 2 | 22400 | R-410A
214331950 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B4G+TXV+TDR | BGH96M120D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
214331759 | 3.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48A3G+TXV+TDR | BGH96M080B3B | 39500 | 17 | 11.4 | 8.5 | 43000 | 39000 | 90.7% | 2.33 | 34800 | R-410A
215375392 | 2.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M080C4B | 31600 | 17.5 | 10.9 | 8.6 | 33800 | 24800 | 73.37% | 2.42 | 26400 | R-410A
215375410 | 2.57 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)48A36+TDR | BGH96M060B3B | 30800 | 17.5 | 10.5 | 8.6 | 33600 | 24800 | 73.81% | 2.34 | 26600 | R-410A
216687219 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF80TV507521UH | 53500 | 17 | 10 | 10 | 53500 | 48500 | 90.65% | 2 | 51000 | R-454B
216687218 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF96TV507021M4 | 53500 | 16 | 10 | 10 | 53500 | 49000 | 91.59% | 2 | 51000 | R-454B
213782155 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 59MN7C120C24**22 | 32600 | 16.5 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31600 | R-410A
216735033 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80CTL0701412B* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216734716 | 1.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VSN0601716B* | 22400 | 16 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
214731175 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG9J936 | 926TC36060V14*** | 23600 | 17 | 10 | 8.5 | 24600 | 23600 | 95.93% | 2 | 18100 | R-410A
214731188 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG35936 | 926TC60080V21*** | 23800 | 17 | 10.5 | 8.5 | 24800 | 23600 | 95.16% | 1.98 | 18200 | R-410A
213278308 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+JMET16CS2N1+TDR |  | 43000 | 16 | 11.8 | 8.2 | 44000 | 31200 | 70.91% | 3.19 | 30400 | R-410A
214331768 | 3.38 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48B4G+TXV+TDR | BGH96M080C4B | 40500 | 17 | 11 | 8.8 | 44500 | 39000 | 87.64% | 2.39 | 35000 | R-410A
214331773 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)48D4G+TXV+TDR | BGH96M100C5A | 44000 | 17.5 | 11.7 | 8.8 | 46500 | 39000 | 83.87% | 2.35 | 35600 | R-410A
215375401 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M120D5B | 43500 | 17.5 | 11.6 | 8.9 | 47000 | 35600 | 75.74% | 2.29 | 38500 | R-410A
215375419 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B34+TDR | BGH96M080C4B | 41000 | 17 | 11.6 | 8.7 | 44500 | 35000 | 78.65% | 2.37 | 39000 | R-410A
214625036 | 2.35 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)30A34+TDR |  | 28200 | 15.2 | 10.3 | 9.5 | 22600 | 27000 | 119.5% | 1.85 | 22600 | R-410A
211871490 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PE31(1,2)30+TXV | 59SC2D060E17**14 | 23800 | 16 | 10 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
212614353 | 1.46 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | F,PE*G31925 |  | 17500 | 17 | 10.5 | 8.8 | 17100 | 19400 | 113.5% | 2.36 | 11500 | R-410A
212846387 | 3.92 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M15G | L(E,G)M48B4 |  | 47000 | 15.5 | 10 | 8.2 | 47000 | 41000 | 87.23% | 2.29 | 37000 | R-410A
214625061 | 2.82 | Yes | No | PAYNE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)42D24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 27600 | 31600 | 114.5% | 1.85 | 27400 | R-410A
213781075 | 2.65 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4221AL*+UI | 59TN6C100C21**22 | 31800 | 17 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.88 | 31200 | R-410A
213781225 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CAP**4321AL*+UI | 59MN7C080C17**14 | 32800 | 17 | 11 | 8.1 | 33000 | 25200 | 76.36% | 1.96 | 31800 | R-410A
213752485 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36B34+TDR | 59SC6A080M21**20 | 23800 | 16 | 9.5 | 8.1 | 25000 | 22200 | 88.8% | 2.9 | 19900 | R-410A
214595097 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M364+TDR |  | 24000 | 15.2 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213781925 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 58TN*B090C21**20 | 32400 | 16.5 | 11 | 8.1 | 32800 | 24600 | 75% | 1.94 | 31400 | R-410A
213781995 | 2.7 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4212AL*+UI | 59MN7C120C24**22 | 32400 | 16.5 | 11 | 8.1 | 32800 | 24800 | 75.61% | 1.94 | 31400 | R-410A
214064105 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)60B44+TDR | BGH96M120D5A | 44000 | 17.5 | 11.7 | 9 | 47000 | 38500 | 81.91% | 2.32 | 35600 | R-410A
215375405 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | D(A,C,E)60B36+TDR | BGH96M120D5B | 43500 | 17.5 | 11.6 | 8.9 | 47000 | 35600 | 75.74% | 2.29 | 38500 | R-410A
215669603 | 2.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6121AM*+UI | 986TD66100C21*** | 34800 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215669203 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 935CB66100C21*** | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
214595158 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24J4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212970957 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *80VTL0451412B* | 17400 | 16.5 | 11 | 8.1 | 17900 | 18600 | 103.9% | 2.24 | 12200 | R-410A
212972744 | 1.45 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *96VSN0401410B* | 17400 | 15.5 | 10.5 | 8.5 | 18500 | 19200 | 103.8% | 2.3 | 12400 | R-410A
214731212 | 2.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG35936 | 926TC60080V21*** | 35600 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.9 | 28400 | R-410A
215792888 | 2.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CDP36C15P | 926TC48060V17*** | 34600 | 15.2 | 9.5 | 8.5 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
215669555 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0801714B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215669435 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716A* | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.9 | 30000 | R-454B
215669655 | 2.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1352422B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
215668957 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CSU0601716A* | 34400 | 18 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
214731142 | 1.44 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG35936 | 926TC36040V17*** | 17300 | 16 | 10.5 | 8.5 | 16400 | 18400 | 112.2% | 2.24 | 11200 | R-410A
215683576 | 1.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2414AM*+UI | 986TD30040C14*** | 22400 | 15.5 | 9 | 8.5 | 24600 | 17300 | 70.33% | 1.82 | 20800 | R-454B
216735428 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80CSU0601716A* | 23800 | 17 | 11 | 8.5 | 21000 | 18700 | 89.05% | 1.96 | 17800 | R-454B
216735246 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VSN0601716B* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
215669029 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *95CSU0802120B* | 34400 | 17.5 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215669215 | 2.78 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0601714B* | 33400 | 17.5 | 9.5 | 9 | 35200 | 25400 | 72.16% | 1.88 | 30600 | R-454B
215669315 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0902120B* | 34400 | 18.5 | 10.5 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
212498508 | 1.48 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CE2403A+TXV |  | 17700 | 17 | 11 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
215668989 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL0702120B* | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
207172512 | 1.97 | Yes | Yes | DUCANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | 48BP**+TXV | 80G2UH090BE12 | 23600 | 19 | 12 | 8.5 | 22400 | 19100 | 85.27% | 2.22 | 13800 | R-410A
214731208 | 2.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG48936 | 926TC48080V17*** | 35600 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.98 | 28200 | R-410A
216734915 | 1.9 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80MS(N,L)0451714A* | 22800 | 15.5 | 11 | 8.1 | 20800 | 18500 | 88.94% | 1.9 | 17600 | R-454B
216734966 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80VSL0451412B* | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
215669847 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU1002122B* | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
214731189 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG7J936 | 926TC60080V21*** | 23400 | 17 | 10 | 8.5 | 24800 | 23600 | 95.16% | 1.98 | 18200 | R-410A
214063844 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36B34+TDR | BGH96M060B3B | 22600 | 18 | 11.9 | 8.8 | 23800 | 22400 | 94.12% | 2.26 | 19600 | R-410A
214094155 | 3.54 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | DM59A44+TDR | BGH96M100D5B | 42500 | 17.5 | 10.9 | 8.1 | 47000 | 36200 | 77.02% | 2.48 | 34200 | R-410A
213780338 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X60AAL+WALLCON | *80CTL0902120B* | 33000 | 16.5 | 11.5 | 8.1 | 32200 | 24800 | 77.02% | 2 | 31200 | R-410A
212978088 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L14A* | *80MS(N,L)0701412A* | 23200 | 17 | 10 | 9 | 26800 | 26800 | 100% | 2.28 | 19300 | R-410A
212979510 | 2.03 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *80MS(N,L)0702116A* | 24400 | 17 | 10.5 | 8.5 | 25200 | 24000 | 95.24% | 2 | 19200 | R-410A
212979855 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *80MS(N,L)0901714A* | 23800 | 17 | 10 | 8.5 | 26200 | 23800 | 90.84% | 1.98 | 19100 | R-410A
212981734 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *80MSU1002120A* | 23400 | 17 | 10 | 8.5 | 26000 | 24400 | 93.85% | 2.02 | 19000 | R-410A
212980705 | 2.52 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *80MS(N,L)0902420A* | 30200 | 15.2 | 9 | 8.1 | 34400 | 28400 | 82.56% | 1.96 | 32600 | R-410A
214595164 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36E4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
211912012 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CDP23H13P+TXV | 59SC2D080E17**16 | 23400 | 17 | 9.5 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
215683580 | 1.9 | No | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2417AM*+UI | 83*CA48060C17*** | 22800 | 16.5 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20400 | R-454B
214320273 | 4.21 | No | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR60HPJ1OA | D(A,C,E)60D44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
216735219 | 1.88 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VSN0401410B* | 22600 | 15.5 | 10.5 | 8.1 | 20800 | 18500 | 88.94% | 1.85 | 17600 | R-454B
216735228 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VSN0401712B* | 22800 | 16 | 10.5 | 8.5 | 20800 | 18600 | 89.42% | 1.96 | 17700 | R-454B
214731146 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG35936 | 926TC36060V14*** | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215669791 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0702120B* | 33600 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215669823 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL1352422B* | 33800 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
215669959 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0451712B* | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215669975 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0701716B* | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
215669991 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0901716B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
214385796 | 1.83 | No | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,YE21924 | *95MSU0401712A* | 22000 | 16 | 9 | 8.45 | 25400 | 25800 | 101.6% | 2.2 | 18500 | R-410A
212973064 | 1.44 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *96VSN0401712B* | 17300 | 16 | 10.5 | 8.1 | 17900 | 18600 | 103.9% | 2.22 | 12200 | R-410A
215669919 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN1002122B* | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
214064106 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | D(A,C,E)48A34+TDR | BGH96M120D5B | 42000 | 17.5 | 11.4 | 8.7 | 46500 | 38500 | 82.8% | 2.27 | 35400 | R-410A
215669113 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 83*CA60100C21*** | 33800 | 17.5 | 9.5 | 9 | 35000 | 25200 | 72% | 1.88 | 30400 | R-454B
215935307 | 2.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN0801714B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28800 | 75.79% | 2.02 | 33000 | R-454B
216734329 | 1.88 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3017AM* | OVMAAB042112 | 22600 | 15.5 | 10.5 | 8.5 | 21400 | 19100 | 89.25% | 1.96 | 18000 | R-454B
213785414 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**3721AL*+UI | 59TN6C080C17**14 | 33800 | 19 | 11.7 | 9 | 36600 | 25800 | 70.49% | 2.02 | 31000 | R-410A
213785430 | 2.68 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4221AL*+UI | 59MN7C060C17**14 | 32200 | 18.5 | 11 | 9 | 38000 | 26800 | 70.53% | 1.96 | 32400 | R-410A
215669013 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL1102120B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
207455051 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36U9 | EL296UH090XV60C* | 33600 | 21 | 13 | 8.6 | 32800 | 26200 | 79.88% | 1.8 | 29400 | R-410A
207455065 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/38X9 | EL296UH110XV60C* | 34000 | 21 | 13.5 | 8.8 | 34000 | 27000 | 79.41% | 1.82 | 31800 | R-410A
207455118 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*23/37Z9 | SL280UH080NV48B* | 34600 | 21 | 13 | 8.8 | 32600 | 25800 | 79.14% | 1.82 | 29400 | R-410A
207455150 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*23/37Z9 | SL280UH090V60C* | 34000 | 21 | 13.5 | 8.8 | 33800 | 27000 | 79.88% | 1.84 | 31800 | R-410A
207455166 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*23/37Z9 | SL280UH090XV60C* | 34000 | 21 | 13.5 | 8.8 | 33800 | 27000 | 79.88% | 1.84 | 31800 | R-410A
207455217 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/38F9 | SL297UH080NV60C* | 33600 | 21 | 13 | 8.6 | 32800 | 26200 | 79.88% | 1.8 | 29400 | R-410A
215668973 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CTL0451712B* | 34000 | 17.5 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.86 | 30800 | R-454B
215669333 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6024AM*+UI | 88*TB66135C24*** | 34400 | 18.5 | 10.5 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
215669433 | 2.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6121AM*+UI | 83*CA48060C17*** | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.9 | 30000 | R-454B
216734513 | 1.85 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3617AM* | 82*TB36045V14*** | 22200 | 16.5 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.94 | 17500 | R-454B
216734597 | 1.87 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3617AM* | 912SE42060M17*** | 22400 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
216734657 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96MSN0601412A* | 22400 | 15.5 | 10.5 | 8.1 | 20800 | 18800 | 90.38% | 1.9 | 17600 | R-454B
215941263 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CTN1202422A* | 45000 | 20.5 | 11 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
214573974 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *80CTL0702120B* | 32400 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214573754 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L21A*+WALLCON | *95CSU1002122B* | 31800 | 17.5 | 11 | 8.5 | 32800 | 24400 | 74.39% | 1.9 | 31200 | R-410A
214574004 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *97CMN0602120B* | 32200 | 17 | 11 | 8.5 | 32600 | 25200 | 77.3% | 1.96 | 31600 | R-410A
215292072 | 1.9 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32930 | *92MSN0802120A* | 22800 | 17 | 9.5 | 8.5 | 24400 | 23600 | 96.72% | 2.02 | 18000 | R-410A
212985058 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *92MSN0802120A* | 23400 | 17 | 10.5 | 8.5 | 26200 | 28600 | 109.2% | 1.96 | 32800 | R-410A
215669743 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CSU0401712A* | 33600 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
212986185 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96MSN0401410A* | 23400 | 16 | 10 | 8.5 | 26400 | 24600 | 93.18% | 2.04 | 19200 | R-410A
211206944 | 3.63 | Yes | Yes | LUXAIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HL20B4821 | XAMC48HE3N1+CC | TP9C080C16MP13 | 43500 | 18 | 11 | 8.5 | 45500 | 36800 | 80.88% | 2.14 | 41500 | R-410A
214573764 | 2.63 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L21A*+WALLCON | *97CMN0602120B* | 31600 | 17 | 10.5 | 8.1 | 33200 | 24800 | 74.7% | 1.88 | 31600 | R-410A
215375439 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C46+TDR | BGH96M060B3B | 23400 | 18.5 | 12 | 9 | 20000 | 20000 | 100% | 2.86 | 25000 | R-410A
215669799 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0901716B* | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215669999 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0902120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215670015 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL1352422B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
213206122 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59SC5B080E21**20 | 23800 | 15.5 | 9.5 | 8.5 | 26000 | 22600 | 86.92% | 2.88 | 20400 | R-410A
215942549 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN1002122B* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215942579 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *95CSU0802120B* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
212987818 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *96MSN0802120A* | 24200 | 17.5 | 10 | 8.5 | 25200 | 24200 | 96.03% | 2.02 | 19100 | R-410A
212988659 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X25L17A* | *95MSU0401712A* | 24200 | 16.5 | 10 | 8.5 | 25200 | 21800 | 86.51% | 1.82 | 18700 | R-410A
212989163 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *95MSU0601716A* | 23600 | 17 | 10 | 8.5 | 26400 | 24600 | 93.18% | 2.04 | 19100 | R-410A
212989631 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *95MSU0802120A* | 23400 | 17 | 10.5 | 8.5 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
216734365 | 1.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0451412A* | 22400 | 16 | 11 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
213782325 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*6012AL*+UI | 59TN6C060C17**14 | 32800 | 16.5 | 11 | 8.1 | 32400 | 25000 | 77.16% | 1.96 | 31400 | R-410A
216734749 | 1.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *95MSU0601716A* | 22400 | 16.5 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
216735749 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *97CMN1002122B* | 23400 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
216734798 | 1.85 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VTN0401712B* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216679531 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3621AL* | 927TA48060V17*** | 23600 | 16.5 | 10 | 9 | 25800 | 23600 | 91.47% | 1.76 | 18900 | R-410A
215670087 | 2.72 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0401410B* | 32600 | 15.2 | 9 | 8.5 | 36000 | 25600 | 71.11% | 1.76 | 31000 | R-454B
215670189 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0702120B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
212973364 | 1.46 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L14** | *96VSN0601412B* | 17500 | 16 | 10.5 | 8.5 | 18500 | 19200 | 103.8% | 2.3 | 12400 | R-410A
216735410 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | OMV112K14A | 23400 | 15.5 | 10.5 | 8.5 | 21400 | 18900 | 88.32% | 1.96 | 18000 | R-454B
216735530 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80VSL0901716B* | 22800 | 16 | 11 | 8.5 | 20400 | 18300 | 89.71% | 1.98 | 17400 | R-454B
215669283 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 986TD66100C21*** | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
216735539 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80VSL0902120B* | 23400 | 16 | 11 | 8.5 | 20800 | 18600 | 89.42% | 1.98 | 17700 | R-454B
215940943 | 3.63 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0802120B* | 43500 | 20.5 | 10.5 | 9.5 | 48000 | 36600 | 76.25% | 2 | 39500 | R-454B
215375387 | 1.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M080B3B | 22200 | 18 | 11.8 | 8.4 | 23600 | 19500 | 82.63% | 2.17 | 22200 | R-410A
216687202 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF80TV407517UH | 45500 | 19 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
207455219 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36S9 | SL297UH080NV60C* | 33600 | 21 | 13 | 8.6 | 32800 | 26200 | 79.88% | 1.8 | 29400 | R-410A
207455250 | 2.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*35/36S9 | SLP99UH090XV36C* | 34000 | 22 | 13 | 8.8 | 34000 | 27200 | 80% | 1.82 | 32000 | R-410A
216735348 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VTN0601716B* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
215683582 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2417AM*+UI | 88*TB36045C17*** | 22600 | 16.5 | 9.5 | 9 | 24200 | 17000 | 70.25% | 1.94 | 20400 | R-454B
215683616 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2517AM*+UI | 986TD42080C17*** | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
215683718 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 986TD66100C21*** | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
213369388 | 1.41 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG7J936 | 59TP6C040V17**12 | 16900 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
213780438 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X60AAL+WALLCON | *96CTN1002122B* | 33000 | 16.5 | 11.5 | 8.1 | 32200 | 24800 | 77.02% | 2 | 31200 | R-410A
212978256 | 1.47 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *80MS(N,L)0701412A* | 17600 | 16.5 | 10.5 | 8.5 | 18500 | 19400 | 104.9% | 2.34 | 12400 | R-410A
210693394 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC961205DNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212980696 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L24A* | *80MS(N,L)0902420A* | 36000 | 16.5 | 10 | 8.5 | 37800 | 34800 | 92.06% | 2.02 | 29200 | R-410A
212982166 | 2.5 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L21A* | *80MSU0401712A* | 30000 | 15.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 1.78 | 23200 | R-410A
215935494 | 2.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA6124XMA*+UI | 59MN7C060C21**20 | 35800 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.06 | 32800 | R-454B
215674057 | 3.71 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0902120B* | 44500 | 18 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.06 | 42500 | R-454B
213785514 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4824AL*+UI | 59TN6C100C21**22 | 33200 | 19.5 | 12 | 9 | 36400 | 25800 | 70.88% | 2.04 | 31000 | R-410A
213785532 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**6121AL*+UI | 58TN*B045C17**12 | 33800 | 19 | 11.7 | 9 | 36200 | 25400 | 70.17% | 1.98 | 30400 | R-410A
214320264 | 1.92 | Yes | No | BOREAL | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | ENVBR36HPJ1OA | D(A,C,E)24C34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215674107 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0801714B* | 44000 | 17 | 9 | 9 | 49000 | 34600 | 70.61% | 2.04 | 43000 | R-454B
216643546 | 1.53 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X25M17A* | *80MSU0401712A* | 18300 | 15.5 | 11 | 9.5 | 20000 | 17600 | 88% | 2 | 14900 | R-454B
212982274 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *80MSU0401712A* | 23800 | 16.5 | 10 | 8.5 | 25800 | 24000 | 93.02% | 2 | 18900 | R-410A
212982706 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *80MSU0601716A* | 23800 | 17.5 | 10 | 8.5 | 25600 | 23400 | 91.41% | 1.96 | 18800 | R-410A
213205871 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)36C34+TDR | 58S(B,C)*A070E21**16 | 23800 | 16 | 9.5 | 8.1 | 25400 | 22600 | 88.98% | 2.97 | 20200 | R-410A
212983193 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *92MSN0401712A* | 23800 | 16 | 10 | 8.5 | 25800 | 22600 | 87.6% | 1.86 | 19000 | R-410A
212986149 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L17A* | *96MSN0401410A* | 23200 | 16 | 9.5 | 8.5 | 27000 | 26400 | 97.78% | 2.2 | 19500 | R-410A
212986582 | 1.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *96MSN0401712A* | 23400 | 16 | 9.5 | 8.5 | 26200 | 22200 | 84.73% | 1.82 | 19000 | R-410A
212987421 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *96MSN0801716A* | 23400 | 17 | 10 | 8.5 | 26000 | 24200 | 93.08% | 2.02 | 19000 | R-410A
212988755 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *95MSU0401712A* | 23600 | 16.5 | 10 | 8.1 | 26400 | 24200 | 91.67% | 2.02 | 19200 | R-410A
215683658 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3617AM*+UI | 987MC42080C17*** | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
216681769 | 3.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3721AL* | 59TP7A100V21**20 | 36200 | 16.5 | 10 | 9 | 38000 | 34400 | 90.53% | 1.96 | 29000 | R-410A
215674047 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0901716B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.06 | 42500 | R-454B
214331862 | 2.72 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36C4G+TXV+TDR | BGH96M080C4B | 32600 | 17.5 | 11 | 9 | 34200 | 26600 | 77.78% | 2.51 | 25000 | R-410A
215674067 | 3.71 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL1102120B* | 44500 | 18 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.06 | 42500 | R-454B
215674147 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN1002122B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.04 | 42500 | R-454B
215674177 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0702120B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
216734826 | 1.85 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96VTN0801716B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17500 | R-454B
216734876 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | OMV112K14A | 22800 | 16 | 10.5 | 8.5 | 21200 | 19000 | 89.62% | 1.96 | 17900 | R-454B
215683932 | 2.75 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4221AM*+UI | 83*CA36040C17*** | 33000 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215674347 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0702120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
213206206 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30C44+TDR | 59TP6B100V21**20 | 23800 | 16 | 9.5 | 8.1 | 25000 | 22400 | 89.6% | 2.96 | 20000 | R-410A
216687214 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF97MV510021DH | 53500 | 17 | 10 | 10 | 53500 | 48500 | 90.65% | 2 | 51000 | R-454B
216687221 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF98MV510021UP | 53500 | 17 | 10 | 10 | 53500 | 49000 | 91.59% | 2 | 51000 | R-454B
214574054 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X60L24A*+WALLCON | *95CSU1002122B* | 32800 | 17.5 | 11.5 | 8.5 | 31600 | 24800 | 78.48% | 2 | 31000 | R-410A
214595163 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36D4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212984767 | 1.45 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *92MSN0801716A* | 17400 | 16.5 | 11 | 8.1 | 17900 | 18600 | 103.9% | 2.24 | 12100 | R-410A
212986389 | 1.47 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *96MSN0401410A* | 17600 | 16 | 11 | 8.1 | 18200 | 18700 | 102.7% | 2.24 | 12300 | R-410A
212988779 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *95MSU0401712A* | 17700 | 16.5 | 10.5 | 8.1 | 17700 | 17900 | 101.1% | 2.16 | 12100 | R-410A
212988827 | 1.47 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *95MSU0401712A* | 17600 | 16 | 10.5 | 8.5 | 18700 | 19100 | 102.1% | 2.3 | 12500 | R-410A
212984599 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *92MSN0801716A* | 23400 | 17.5 | 10 | 8.5 | 26200 | 24800 | 94.66% | 2.08 | 19100 | R-410A
212984683 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *92MSN0801716A* | 23600 | 17.5 | 10.5 | 8.5 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
215942439 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X61M24A*+WALLCON | *80CTL0702120B* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215942589 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M24A*+WALLCON | *97CMN0802120B* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215673997 | 3.71 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0802120A* | 44500 | 18 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.06 | 42500 | R-454B
215674267 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1202422B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215674367 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0902120B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215683872 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3717AM*+UI | 88*TB36045C17*** | 33600 | 17 | 9 | 9 | 36000 | 25800 | 71.67% | 1.86 | 31200 | R-454B
215683904 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 88*TB48090C17*** | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215683920 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 987MC42080C17*** | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
214570654 | 2.03 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X43L21A*+WALLCON | *97CMN0802120B* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
214570704 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X48L21A*+WALLCON | *97CMN0602120B* | 24000 | 16.5 | 10.5 | 8.5 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
207455369 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LD42/61Z9 | SL280DF090V60C* | 45500 | 20 | 12 | 9.1 | 41500 | 34800 | 83.86% | 1.86 | 39500 | R-410A
215683622 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3017AM*+UI | 83*CA36040C17*** | 23000 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214571104 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D)4X36L21**+WALLCON | *95CSU0802120B* | 23400 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
212989547 | 2.5 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L21A* | *95MSU0802120A* | 30000 | 15.2 | 9 | 8.1 | 34200 | 27600 | 80.7% | 1.8 | 23600 | R-410A
215683708 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 987MC60060C21*** | 24000 | 17 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
212983292 | 1.44 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *92MSN0401712A* | 17300 | 15.5 | 10.5 | 8.5 | 18100 | 18800 | 103.9% | 2.24 | 12200 | R-410A
215684004 | 2.87 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 986TD42080C17*** | 34400 | 18 | 10 | 8.1 | 35400 | 25200 | 71.19% | 1.9 | 30600 | R-454B
215684040 | 2.78 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 987MC42080C17*** | 33400 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
207683537 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LP42/62W9 | EL296UH110XV48C* | 45500 | 20 | 12 | 9.4 | 42000 | 36000 | 85.71% | 1.88 | 41000 | R-410A
215674037 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0702120B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.06 | 42500 | R-454B
216735866 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96VSN0401712B* | 23000 | 16 | 10.5 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216736016 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96VTN0801716B* | 23200 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216736351 | 1.88 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80MSU0601716A* | 22600 | 16 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.85 | 17800 | R-454B
216736870 | 1.85 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *96VTN0802120B* | 22200 | 15.2 | 10.5 | 8.1 | 21000 | 19000 | 90.48% | 1.9 | 17700 | R-454B
215674337 | 3.79 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0701716B* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34000 | 70.83% | 2.06 | 42500 | R-454B
215674437 | 3.79 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0801714B* | 45500 | 17.5 | 9.5 | 9 | 48000 | 33600 | 70% | 2.08 | 41500 | R-454B
212982154 | 2.53 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X37L21A* | *80MSU0401712A* | 30400 | 15.2 | 9 | 8.1 | 33400 | 26200 | 78.44% | 1.86 | 23200 | R-410A
212982958 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L21A* | *80MSU0802120A* | 29600 | 15.5 | 9 | 8.5 | 33600 | 27600 | 82.14% | 1.78 | 23200 | R-410A
213785650 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*3612AL*+UI | 59MN7C060C17**14 | 32800 | 17.5 | 11 | 8.5 | 37400 | 26400 | 70.59% | 1.98 | 31800 | R-410A
215684074 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 88*TB60110C21*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215683606 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2517AM*+UI | 88*TB48090C17*** | 24000 | 17.5 | 10.5 | 9 | 23200 | 16400 | 70.69% | 2 | 19700 | R-454B
215683672 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3717AM*+UI | 88*TB36070C14*** | 23800 | 17.5 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
213785009 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**2417AL*+UI | 58TN*B045C17**12 | 22800 | 19 | 12 | 9.5 | 27200 | 20400 | 75% | 2.26 | 25400 | R-410A
215941093 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN1002122A* | 45500 | 21 | 11 | 9.5 | 48500 | 36800 | 75.88% | 2 | 40000 | R-454B
215941593 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X48M24A*+WALLCON | *96CTN0802120B* | 44500 | 20 | 11 | 8.1 | 52000 | 38000 | 73.08% | 1.9 | 43500 | R-454B
213782095 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*4812AL*+UI | 58TN*B110C21**20 | 32600 | 16.5 | 11 | 8.1 | 32800 | 24800 | 75.61% | 1.96 | 31400 | R-410A
214573624 | 2.62 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X36L21A*+WALLCON | *95CSU0802120B* | 31400 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.86 | 31200 | R-410A
214573674 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X37L21A*+WALLCON | *80CTL0702120B* | 32800 | 17.5 | 11 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
215666930 | 1.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M14A*+WALLCON | *80CTL0701412B* | 22800 | 17 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215666946 | 1.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M14A*+WALLCON | *96CTN0401410B* | 22400 | 15.5 | 9 | 8.5 | 24600 | 17300 | 70.33% | 1.82 | 20800 | R-454B
213785043 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**2517AL*+UI | 59TN6C080C17**14 | 24000 | 20 | 13 | 10.5 | 26600 | 19800 | 74.44% | 2.5 | 24800 | R-410A
215667254 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *97CMN0801714B* | 23800 | 17 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19800 | R-454B
215464925 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP44(1,2)36+TXV | A96DS2V070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
215683688 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 83*CA36040C17*** | 24000 | 18 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215684056 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 83*CA36040C17*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215792884 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PE32936 | 926TC48060V17*** | 33600 | 15.2 | 9.5 | 8.5 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
216687199 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF98MV510021UP | 34200 | 21 | 12 | 10 | 34200 | 29400 | 85.96% | 2 | 30000 | R-454B
216687184 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80TV407517UH | 22800 | 21 | 13 | 10 | 22800 | 18400 | 80.7% | 1.8 | 21200 | R-454B
215941203 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1202422A* | 44500 | 20 | 10.5 | 9 | 48500 | 36400 | 75.05% | 1.82 | 39500 | R-454B
215941753 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *97CTN1002122A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.9 | 43500 | R-454B
215674017 | 3.63 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0451712B* | 43500 | 17 | 9 | 9 | 49000 | 35000 | 71.43% | 2.02 | 43500 | R-454B
214573964 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L21A*+WALLCON | *96CTN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32400 | 24800 | 76.54% | 2 | 31400 | R-410A
214574014 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *97CMN0802120B* | 32400 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214573874 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *95CSU1002122B* | 33000 | 17.5 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 2 | 31600 | R-410A
214573994 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *95CSU1002122B* | 32400 | 17.5 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 2 | 31400 | R-410A
213785075 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3617AL*+UI | 59MN7C060C17**14 | 23200 | 19.5 | 12.5 | 10 | 26800 | 20000 | 74.63% | 2.38 | 25000 | R-410A
213785095 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**3621AL*+UI | 59MN7C060C17**14 | 23200 | 19.5 | 12.5 | 10 | 26800 | 20000 | 74.63% | 2.38 | 25000 | R-410A
210693330 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC960603BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693335 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC961205DNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693385 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC800805C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
207683112 | 1.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LP36/37R9 | EL296UH045XV36B* | 22800 | 22 | 14.5 | 10 | 19600 | 19600 | 100% | 1.96 | 22400 | R-410A
213785386 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**3717AL*+UI | 59MN7C060C17**14 | 33200 | 18.5 | 11 | 9 | 37200 | 26400 | 70.97% | 1.98 | 31600 | R-410A
213785434 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4221AL*+UI | 59MN7C100C21**22 | 32600 | 19 | 11.7 | 9 | 37800 | 26600 | 70.37% | 1.98 | 32000 | R-410A
213785452 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CAP**4224AL*+UI | 59TN6C100C21**22 | 32600 | 19 | 11.7 | 9 | 37800 | 26600 | 70.37% | 1.98 | 32000 | R-410A
215292341 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE33936 | *96MSN0601412A* | 23400 | 16 | 10 | 8.5 | 25400 | 26000 | 102.4% | 2.22 | 18400 | R-410A
215669123 | 2.78 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 88*TB36045C17*** | 33400 | 17.5 | 9.5 | 9 | 35200 | 25400 | 72.16% | 1.88 | 30600 | R-454B
213785159 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CAP**4224AL*+UI | 59TN6C100C21**22 | 23200 | 20 | 13 | 10 | 26600 | 19700 | 74.06% | 2.46 | 24800 | R-410A
213785193 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*3012AL*+UI | 58TN*B090C21**20 | 23400 | 18.5 | 12.5 | 10 | 26800 | 19900 | 74.25% | 2.44 | 25000 | R-410A
215667074 | 1.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *97CMN0601714B* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215667451 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CTL0901716B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
214574294 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X42AAL+WALLCON | *95CSU1002122B* | 32600 | 17 | 11 | 8.5 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
214574344 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EHD4X48AAL+WALLCON | *95CSU0802120B* | 32600 | 17.5 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
215464919 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP15(1,2)36+TXV | A96DS2V045B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
214574104 | 2.77 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X61L21A*+WALLCON | *95CSU0802120B* | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 25000 | 78.12% | 2 | 31200 | R-410A
214574624 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D,W)4X48L21**+WALLCON | *96CTN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31400 | R-410A
212985932 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *96MSN0261410A* | 17500 | 16 | 10.5 | 8.5 | 18100 | 19800 | 109.4% | 2.38 | 12500 | R-410A
212986666 | 1.47 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96MSN0401712A* | 17600 | 15.5 | 10.5 | 8.1 | 17800 | 19400 | 109% | 2.32 | 12300 | R-410A
215683886 | 2.72 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3717AM*+UI | 986TD30040C14*** | 32600 | 16 | 9.5 | 8.5 | 36200 | 25600 | 70.72% | 1.76 | 31000 | R-454B
215667853 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0901716B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215667869 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL1102120B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
216687169 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF95SV304017UH | 22800 | 21 | 13 | 10 | 22800 | 18700 | 82.02% | 1.8 | 21200 | R-454B
212987806 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L21A* | *96MSN0802120A* | 23800 | 17 | 10 | 8.5 | 26200 | 21600 | 82.44% | 1.82 | 18700 | R-410A
212989175 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *95MSU0601716A* | 23600 | 17 | 10 | 8.5 | 26200 | 24000 | 91.6% | 1.98 | 19100 | R-410A
212988339 | 2.5 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *96MSN1202422A* | 30000 | 15.2 | 9 | 8.1 | 34200 | 27600 | 80.7% | 1.8 | 23400 | R-410A
216687164 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF92SV304017M4 | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
215670217 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 88*TB60110C21*** | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215670267 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 987MC42060C17*** | 33800 | 16.5 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
215670367 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 986TD66120C24*** | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
213206524 | 1.98 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36C34+TDR | 59SC5B060E14**12 | 23800 | 16 | 9.9 | 8.1 | 26000 | 20400 | 78.46% | 2.7 | 19100 | R-410A
212989295 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *95MSU0601716A* | 17800 | 16.5 | 10.5 | 8.1 | 17700 | 17700 | 100% | 2.14 | 12000 | R-410A
215465007 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP15(1,2)36+TXV | A97DSMV070B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
215464996 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP15(1,2)36+TXV | A97DS2V070B16 | 23400 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
215464784 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP14(1,2)36+TXV | A80DS2V090B16 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.16 | 15800 | R-410A
215683874 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3717AM*+UI | 88*TB36070C14*** | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 30800 | R-454B
215683876 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3717AM*+UI | 88*TB48070C17*** | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.88 | 30800 | R-454B
215683908 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 88*TB60110C21*** | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215684042 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 987MC60080C21*** | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215939823 | 2.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CTN1202422A* | 34000 | 20.5 | 12 | 9.5 | 34000 | 26000 | 76.47% | 2.06 | 29800 | R-454B
216056025 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Z8ES130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
214731156 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG9J936 | 926TC48080V17*** | 17700 | 16 | 11 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
215670257 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 935CB66100C21*** | 34200 | 16.5 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215670337 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 986TD42060C17*** | 33800 | 16 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
213785734 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*6012AL*+UI | 58TN*B070C17**16 | 33800 | 18.5 | 11.7 | 8.5 | 36200 | 25400 | 70.17% | 2.02 | 30400 | R-410A
215670159 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL0451712B* | 33800 | 16.5 | 9 | 8.5 | 35600 | 25600 | 71.91% | 1.78 | 30800 | R-454B
215670309 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN1002122B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
216734627 | 1.85 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96MSN0261410A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
216734870 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | OMV098J12* | 22400 | 15.2 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
216735138 | 1.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *92MSN0601412A* | 23000 | 15.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
216735370 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *97VTN0601716A* | 22800 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216735477 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)0701716A* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
215684044 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 987MC66100C21*** | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215464918 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP14(1,2)36+TXV | A96DS2V045B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
215669205 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU1002122B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215669325 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1102120B* | 34400 | 18.5 | 10.5 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
215464922 | 1.93 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP42(1,2)36+TXV | A96DS2V070B16 | 23200 | 18 | 12 | 8.35 | 22400 | 16200 | 72.32% | 2.12 | 15900 | R-410A
214595214 | 1.5 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M304+TDR |  | 18000 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
215942429 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X61M24A*+WALLCON | *80CSU1002120A* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215464786 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP44(1,2)36+TXV | A80DS2V090B16 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.16 | 15800 | R-410A
215464995 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP14(1,2)36+TXV | A97DS2V070B16 | 23400 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
215464997 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP44(1,2)36+TXV | A97DS2V070B16 | 23400 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
216735719 | 1.95 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *97CMN0602120B* | 23400 | 15.5 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.98 | 17700 | R-454B
215464924 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP15(1,2)36+TXV | A96DS2V070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
215464991 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP15(1,2)36+TXV | A97DS2V045B12 | 23400 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
213782315 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | CSPH*6012AL*+UI | 59MN7C120C24**22 | 33000 | 16.5 | 11 | 8.1 | 32200 | 24800 | 77.02% | 2 | 31200 | R-410A
215292083 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG34936 | *92MSN0802120A* | 23200 | 17 | 10.5 | 8.5 | 24600 | 24400 | 99.19% | 2.08 | 18000 | R-410A
215818598 | 2.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | BV**B9*37+TXV |  | 34000 | 19 | 11.7 | 9 | 30800 | 24800 | 80.52% | 2.1 | 25600 | R-454B
213076396 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*2417AL* | GG96VTAB48060B** | 23200 | 16.5 | 10 | 8.5 | 26800 | 25400 | 94.78% | 2.12 | 19400 | R-410A
213613484 | 2 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M36L4 |  | 24000 | 15.5 | 9 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213613468 | 1.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24B4 |  | 22800 | 15.5 | 9.4 | 8.8 | 25400 | 22600 | 88.98% | 2.84 | 20200 | R-410A
213613470 | 1.98 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24D4 |  | 23800 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
215674327 | 3.79 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0451712B* | 45500 | 17 | 9.5 | 9 | 48500 | 34600 | 71.34% | 2.06 | 43000 | R-454B
215674447 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN1002122B* | 46000 | 18 | 10 | 9 | 47500 | 33800 | 71.16% | 2.08 | 42000 | R-454B
216687217 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF96TV510021M4 | 53500 | 16 | 10 | 10 | 53500 | 49000 | 91.59% | 2 | 51000 | R-454B
214061531 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | A36VDA+TXV | A97DF2E070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16900 | 75.45% | 2.22 | 16100 | R-410A
215935544 | 2.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAVA3117XMA*+UI | 59MN7C060C17**14 | 34800 | 20.5 | 11.5 | 8.5 | 38000 | 27800 | 73.16% | 2.08 | 31800 | R-454B
215935744 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAVA3621XMA*+UI | 59MN7C100C21**22 | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
215292108 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE1K936 | *92MSN0802120A* | 23400 | 17 | 10.5 | 8.5 | 24600 | 24400 | 99.19% | 2.08 | 18000 | R-410A
210597924 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L24A*+WALLCON | *97CMN1002122A* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
210598024 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *95CSU0802120A* | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
210598176 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *80CTL0701716A* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
214595213 | 1.46 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M254+TDR |  | 17500 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
204456536 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X30L17A*+WALLCON | *96CTN0601714A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.9 | 20800 | R-410A
205750727 | 2.05 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *80CTL0901716A* | 24600 | 17.5 | 11.7 | 8.5 | 21000 | 16500 | 78.57% | 2.04 | 20400 | R-410A
212987086 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *96MSN0601412A* | 17500 | 16 | 11 | 8.1 | 18000 | 16200 | 90% | 1.86 | 20200 | R-410A
212987505 | 1.52 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96MSN0801716A* | 18200 | 16.5 | 11 | 8.5 | 18100 | 17700 | 97.79% | 2.14 | 12300 | R-410A
215670239 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU0601716B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215674417 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0802120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
214254925 | 2.98 | No | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | C(A,C,D,E)36B44+TDR | WPV080T3AA | 35800 | 17 | 9.9 | 8.5 | 36600 | 32800 | 89.62% | 1.8 | 25600 | R-410A
212984695 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *92MSN0801716A* | 23600 | 17.5 | 10.5 | 8.5 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
216488051 | 2.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | A36VDA*+TXV | Z8ES100C20SMPS1 | 34600 | 18 | 11 | 8.5 | 30600 | 25800 | 84.31% | 2 | 27600 | R-454B
210597852 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L21A*+WALLCON | *80CTL0901716A* | 23800 | 17.5 | 11 | 8.1 | 21400 | 16500 | 77.1% | 1.98 | 20600 | R-410A
210598000 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *80CSU0601716A* | 24000 | 17 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2.02 | 20400 | R-410A
214331848 | 1.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)24B3G+TXV+TDR | BGH96M080B3B | 21800 | 18 | 11 | 8.5 | 23800 | 22200 | 93.28% | 2.19 | 19500 | R-410A
215291944 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | HE7J936 | *92MSN0601412A* | 23400 | 17 | 10 | 8.5 | 24800 | 23400 | 94.35% | 1.98 | 18200 | R-410A
215464923 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP14(1,2)36+TXV | A96DS2V070B16 | 23600 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
216735176 | 1.9 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96MSN0401410A* | 22800 | 15.2 | 10.5 | 8.1 | 20800 | 18500 | 88.94% | 1.9 | 17600 | R-454B
215941393 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVM5X60M21A*+WALLCON | *96CTN0802120B* | 45500 | 20.5 | 11 | 8.1 | 53000 | 38500 | 72.64% | 1.95 | 43500 | R-454B
215941613 | 3.71 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X48M24A*+WALLCON | *97CTN1002122A* | 44500 | 20 | 11 | 8.1 | 52000 | 38000 | 73.08% | 1.9 | 43500 | R-454B
215941663 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X49M24A*+WALLCON | *97CTN1202422A* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.95 | 43000 | R-454B
215464998 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP13(1,2)36+TXV | A97DS2V070B16 | 23400 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
213927964 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)37D34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
215683592 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2417AM*+UI | 987MC42080C17*** | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
213613471 | 1.93 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24E4 |  | 23200 | 15.5 | 9.5 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
214303313 | 3 | No | No | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | D(A,C,E)48B34+TDR | WPV070T3AA | 36000 | 17 | 9.9 | 8.3 | 36400 | 32800 | 90.11% | 1.8 | 25600 | R-410A
216055789 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C080B12MP13 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216055798 | 2.63 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C100C20MP13 | 31600 | 18 | 9.8 | 8.5 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
215942649 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN1002122A* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
216980139 | 1.95 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RXB-M15S | L(E,G)M36FJ |  | 23400 | 17 | 10.4 | 8.1 | 24000 | 17600 | 73.33% | 1.88 | 21000 | R-454B
213286685 | 1.45 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CE2301C+TXV |  | 17400 | 17 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
213286687 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CE2403A+TXV |  | 17700 | 17 | 11 | 8.7 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
213206192 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | D(A,C,E)30B34+TDR | 59TP6B080V21**20 | 23400 | 16 | 9.5 | 8.1 | 24800 | 22200 | 89.52% | 2.88 | 19800 | R-410A
214254932 | 2.98 | No | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | C(A,C,D,E)36B44+TDR | WUV080T3AA | 35800 | 17 | 9.9 | 8.5 | 36600 | 32800 | 89.62% | 1.8 | 25600 | R-410A
214303314 | 3 | No | No | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | D(A,C,E)48B34+TDR | WUV070T3AA | 36000 | 17 | 9.9 | 8.3 | 36400 | 32800 | 90.11% | 1.8 | 25600 | R-410A
214254928 | 2.98 | No | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | C(A,C,D,E)36B44+TDR | WUV070T3AA | 35800 | 17 | 9.9 | 8.5 | 36600 | 32800 | 89.62% | 1.8 | 25600 | R-410A
215866274 | 1.97 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96MSAA48060B** | 23600 | 16.5 | 9.8 | 9.5 | 26600 | 20800 | 78.2% | 3.05 | 19400 | R-410A
214056978 | 1.9 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX36HP230V1AO | L(E,G)M24C4 |  | 22800 | 17 | 11.9 | 8.7 | 23800 | 22000 | 92.44% | 1.8 | 15900 | R-410A
213785263 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*4212AL*+UI | 59MN7C100C21**22 | 23600 | 19 | 13 | 10 | 26400 | 19700 | 74.62% | 2.52 | 24600 | R-410A
215667488 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *97CMN0801714B* | 23000 | 17 | 10 | 8.5 | 23800 | 16700 | 70.17% | 1.86 | 20200 | R-454B
216687165 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF95SV306017UH | 22800 | 21 | 13 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
215667925 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0801714B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
216682321 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CSPH*2412AL* | 59TP7A100V21**20 | 23800 | 16 | 10 | 9 | 26200 | 23400 | 89.31% | 1.8 | 19200 | R-410A
214595221 | 1.85 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M254+TDR |  | 22200 | 15.2 | 9.8 | 8.5 | 26200 | 23400 | 89.31% | 1.92 | 19200 | R-410A
215866298 | 1.92 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96VTAB30040A** | 23000 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.88 | 19500 | R-410A
215866303 | 1.95 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96MSAA48080B** | 23400 | 16.5 | 9.8 | 8.5 | 27000 | 20600 | 76.3% | 3.08 | 19400 | R-410A
216734347 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3617AM* | 83*CA48060C17*** | 23000 | 17 | 11 | 8.5 | 21200 | 19000 | 89.62% | 1.94 | 17900 | R-454B
216735082 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3717AM* | 935CB48060C17*** | 22800 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
215866284 | 1.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96VTAB30040A** | 22800 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.84 | 19500 | R-410A
215866300 | 1.88 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96VTAB60100C** | 22600 | 17.5 | 9.8 | 8.5 | 26200 | 20000 | 76.34% | 2.91 | 19000 | R-410A
215464990 | 1.95 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP14(1,2)36+TXV | A97DS2V045B12 | 23400 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
215465006 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP14(1,2)36+TXV | A97DSMV070B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
215866277 | 1.92 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96VTAB30040A** | 23000 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.97 | 19500 | R-410A
215866291 | 1.92 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | PG96VTAB30040A** | 23000 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.98 | 19500 | R-410A
215866304 | 1.93 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96MSAA60080C** | 23200 | 17 | 9.8 | 8.5 | 26200 | 20400 | 77.86% | 3.03 | 19100 | R-410A
215866306 | 1.93 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96VTAB48060B** | 23200 | 16.5 | 9.8 | 8.5 | 26800 | 20600 | 76.87% | 3.06 | 19400 | R-410A
215669175 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL1102120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215464920 | 1.97 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DP44(1,2)36+TXV | A96DS2V045B12 | 23600 | 19 | 12 | 8.5 | 22400 | 16100 | 71.88% | 2.18 | 15800 | R-410A
215942539 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CMN1002122B* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
215942639 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X61M21A*+WALLCON | *97CTN0802120A* | 35800 | 22 | 12.5 | 8.5 | 37400 | 28400 | 75.94% | 2.04 | 32400 | R-454B
215683598 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**2517AM*+UI | 83*CA36040C17*** | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215683666 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3717AM*+UI | 83*CA36040C17*** | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
215683668 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3717AM*+UI | 83*CA48060C17*** | 23800 | 17 | 10 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
211168144 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV0X24A1 | 4PXFH003AZ3+TDR | *DHMB060BCV3 | 23200 | 18 | 12 | 8.5 | 20200 | 19300 | 95.54% | 2.48 | 16800 | R-410A
212983715 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *92MSN0601412A* | 17500 | 16 | 11 | 8.5 | 18500 | 18600 | 100.5% | 2.24 | 12200 | R-410A
214625038 | 2.33 | Yes | No | MIDEA | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ30AB3 | D(A,C,E)30B34+TDR |  | 28000 | 15.4 | 10.3 | 9 | 32400 | 27000 | 83.33% | 1.85 | 22400 | R-410A
215669927 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *96CTN1202422B* | 33800 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215670007 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL1102120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
211263814 | 1.52 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L14** | *92ESN0601412A* | 18200 | 16 | 11 | 8.5 | 18700 | 18300 | 97.86% | 2.22 | 12500 | R-410A
213613504 | 2 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36L4 |  | 24000 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212626914 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C36+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
214056983 | 2.77 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX36HP230V1AO | L(E,G)M36C4 |  | 33200 | 16 | 10 | 9 | 35000 | 28000 | 80% | 1.8 | 24000 | R-410A
211168166 | 4 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL9048A1 | 4PXFH009AZ3+TDR | *UD2C080ACV4 | 48000 | 19 | 11.7 | 8.7 | 42500 | 34000 | 80% | 2.73 | 31600 | R-410A
215866309 | 2.85 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36A34+TDR | PG96MSAA48080B** | 34200 | 15.2 | 9 | 8.1 | 39000 | 32200 | 82.56% | 2.56 | 29600 | R-410A
210597904 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L24A*+WALLCON | *95CSU0802120A* | 23800 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
210598088 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L24A*+WALLCON | *97CMN1002122A* | 24200 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
210598156 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *80CSU0401712A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
210598487 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EN(A,D,W)4X48L21**+WALLCON | *80CTL0901716A* | 24200 | 17.5 | 11.7 | 8.1 | 21200 | 16500 | 77.83% | 2.02 | 20600 | R-410A
215669775 | 2.78 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0701412B* | 33400 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215669807 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0902120B* | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
215669425 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0401712A* | 34800 | 18.5 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
212983879 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *92MSN0601714A* | 35600 | 16 | 10 | 8.5 | 37800 | 34800 | 92.06% | 2.02 | 29000 | R-410A
212986137 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L14A* | *96MSN0401410A* | 23200 | 16 | 9.5 | 8.5 | 27000 | 26600 | 98.52% | 2.22 | 19500 | R-410A
212986221 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L14** | *96MSN0401410A* | 23200 | 16 | 10 | 8.5 | 27000 | 25200 | 93.33% | 2.1 | 19500 | R-410A
214588328 | 2.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P299 | 926TC48080V17*** | 35600 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.98 | 28200 | R-410A
215684016 | 2.78 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 88*TB36070C14*** | 33400 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
215684018 | 2.8 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*3612AM*+UI | 88*TB48070C17*** | 33600 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.78 | 31000 | R-454B
215684068 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 88*TB60070C21*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215684102 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 986TD66120C24*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215866317 | 2.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | PG96MSAA60080C** | 34800 | 16 | 9 | 8.1 | 39000 | 32400 | 83.08% | 2.63 | 29600 | R-410A
210597984 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X43L21A*+WALLCON | *97CMN0602120A* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
210598036 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *96CTN0801714A* | 24000 | 16.5 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
210598300 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *97CMN0602120A* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20600 | R-410A
213927951 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)36C44+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
210598236 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *80CSU0401712A* | 24200 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
215939923 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CTN1002122A* | 34400 | 20.5 | 12 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 29800 | R-454B
215940073 | 2.8 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CTN0802120A* | 33600 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215940273 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *80CSU0401712B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215866318 | 2.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | PG96MSAA60100C** | 34800 | 16 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.61 | 29400 | R-410A
215866316 | 2.88 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | PG96MSAA48080B** | 34600 | 15.2 | 9 | 8.1 | 39000 | 32400 | 83.08% | 2.62 | 29600 | R-410A
215375438 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | D(A,C,E)36C44+TDR | BGH96M100C5B | 31200 | 18.5 | 11.9 | 9 | 25600 | 25600 | 100% | 2.98 | 32000 | R-410A
214056975 | 2.67 | No | No | American Standard | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 4TXD2036A10NU** | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 15000 | R-410A
215669153 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 88*TB48090C17*** | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
212925899 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | D(A,C,E)60C44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215866280 | 1.92 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96MSAA30040A** | 23000 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.89 | 19500 | R-410A
215866287 | 1.93 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | PG96MSAA30040A** | 23200 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.99 | 19500 | R-410A
215866289 | 1.95 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | PG96MSAA48080B** | 23400 | 16.5 | 9.8 | 8.5 | 27000 | 20400 | 75.56% | 3.02 | 19400 | R-410A
216687182 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80SV405017UHN | 22800 | 20 | 12 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
214263948 | 2 | Yes | Yes | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | H,A,DG9J936 | A96DF1E045B12 | 24000 | 18 | 12 | 8.5 | 22400 | 16200 | 72.32% | 2.16 | 15900 | R-410A
215866311 | 2.87 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36A34+TDR | PG96MSAA60100C** | 34400 | 16 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
215866312 | 2.83 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36A34+TDR | PG96VTAB48060B** | 34000 | 15.2 | 9 | 8.1 | 38500 | 32400 | 84.16% | 2.54 | 29600 | R-410A
216687196 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF98MV307017UP | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
210693371 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC960803BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212861170 | 3.92 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | C(A,C,D,E)48C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
214056987 | 4.5 | Yes | No | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX60HP230V1AO | L(E,G)M60E4 |  | 54000 | 15.8 | 10.4 | 9 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
213772746 | 2.03 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CAP**2517AL*+UI | 88*TB48090C17*** | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
213773566 | 2.02 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CAP**4321AL*+UI | 88*TB36045C17*** | 24200 | 16.5 | 10.5 | 8.1 | 21200 | 16700 | 78.77% | 2 | 20600 | R-410A
215866282 | 1.93 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96MSAA48080B** | 23200 | 16.5 | 9.8 | 8.5 | 27000 | 20400 | 75.56% | 2.93 | 19400 | R-410A
215670111 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN1002122B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215670259 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU1002122B* | 34200 | 16.5 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215670459 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL1102120B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
211871492 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PE32(1,2)36+TXV | 59SC2D080E17**16 | 24000 | 17 | 10 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
215866272 | 1.83 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24A34+TDR | PG96VTAB60100C** | 22000 | 17.5 | 9.8 | 8.1 | 26200 | 20000 | 76.34% | 2.88 | 19000 | R-410A
215866313 | 2.87 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36A34+TDR | PG96VTAB60100C** | 34400 | 16 | 9.8 | 8.1 | 38500 | 32200 | 83.64% | 2.59 | 29400 | R-410A
215866320 | 2.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | PG96VTAB60100C** | 34800 | 16 | 9.8 | 8.1 | 38500 | 32200 | 83.64% | 2.64 | 29400 | R-410A
212925907 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
212984958 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L24A* | *92MSN0802120A* | 35800 | 16.5 | 10 | 8.5 | 37800 | 35400 | 93.65% | 1.8 | 29600 | R-410A
212925905 | 3.92 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | C(A,C,D,E)48D44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
212986966 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *96MSN0601412A* | 23600 | 16.5 | 10 | 8.1 | 26400 | 24200 | 91.67% | 2.02 | 19200 | R-410A
212987409 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *96MSN0801716A* | 23800 | 17 | 10 | 8.5 | 26400 | 23600 | 89.39% | 1.96 | 19100 | R-410A
214440887 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | V,C36H175P159 | 88*TB36045C17*** | 32800 | 19 | 11.7 | 9 | 35200 | 27400 | 77.84% | 2.02 | 31800 | R-410A
214440901 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | V,C36H175P459 | 88*TB48090C17*** | 33800 | 20 | 12.5 | 9 | 34800 | 27200 | 78.16% | 2.06 | 31400 | R-410A
215670437 | 2.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 88*TB48090C17*** | 34600 | 17 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
215670269 | 2.82 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0601714B* | 33800 | 16.5 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
212925904 | 3.92 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | C(A,C,D,E)48C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
212925906 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | C(A,C,D,E)60A44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215670419 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0701716B* | 34400 | 17 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.8 | 30000 | R-454B
211618663 | 2.92 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | LEM48A4 |  | 35000 | 18 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
215866269 | 1.85 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24A34+TDR | PG96MSAA60080C** | 22200 | 17 | 9.8 | 8.1 | 26200 | 20200 | 77.1% | 2.87 | 19100 | R-410A
215866319 | 2.87 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | PG96VTAB48060B** | 34400 | 15.2 | 9 | 8.1 | 38500 | 32600 | 84.68% | 2.57 | 29600 | R-410A
216687201 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF96TV307017M4 | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
215866314 | 2.82 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36A34+TDR | PG96VTAB66120D** | 33800 | 16 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.63 | 29400 | R-410A
215866321 | 2.87 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36B34+TDR | PG96VTAB66120D** | 34400 | 16 | 9 | 8.1 | 38500 | 32400 | 84.16% | 2.64 | 29400 | R-410A
215866292 | 1.93 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | PG96VTAB48060B** | 23200 | 16.5 | 9.8 | 8.5 | 26800 | 20600 | 76.87% | 3.03 | 19400 | R-410A
212925913 | 3.92 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | D(A,C,E)61C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
215684058 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 83*CA48060C17*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
215669303 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6024AM*+UI | 88*TB60070C21*** | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
212861171 | 3.92 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | C(A,C,D,E)48D44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
215670149 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU1002120A* | 34200 | 16.5 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30600 | R-454B
214588271 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P299 | 926TC36040V17*** | 24200 | 16 | 10 | 8.5 | 23800 | 21200 | 89.08% | 1.8 | 17900 | R-410A
214588276 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 926TC36040V17*** | 23400 | 16 | 10 | 8.5 | 24600 | 23800 | 96.75% | 2 | 18100 | R-410A
212984948 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *92MSN0802120A* | 35600 | 16.5 | 10 | 8.5 | 37800 | 34600 | 91.53% | 2.02 | 28800 | R-410A
212924871 | 1.92 | Yes | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | D(A,C,E)24A44+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215866297 | 1.9 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96MSAA60080C** | 22800 | 17 | 9.8 | 8.5 | 26200 | 20200 | 77.1% | 2.9 | 19100 | R-410A
214254922 | 2.98 | No | Yes | NAPOLEON | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | WSEHV2436RA1-N | C(A,C,D,E)36B44+TDR | WPV070T3AA | 35800 | 17 | 9.9 | 8.5 | 36600 | 32800 | 89.62% | 1.8 | 25600 | R-410A
215866281 | 1.95 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96MSAA48060B** | 23400 | 16.5 | 9.8 | 9.5 | 26600 | 20600 | 77.44% | 2.93 | 19400 | R-410A
212984215 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *92MSN0601714A* | 17500 | 16 | 10.5 | 8.5 | 18500 | 19200 | 103.8% | 2.3 | 12400 | R-410A
213613491 | 1.88 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24E4 |  | 22600 | 15.2 | 9.5 | 8.1 | 26200 | 23400 | 89.31% | 1.92 | 19200 | R-410A
213613496 | 2 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24J4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214056989 | 4.5 | Yes | No | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX60HP230V1AO | L(E,G)M60J4 |  | 54000 | 15.8 | 10.4 | 9 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
212925912 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | D(A,C,E)25B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215375408 | 2.58 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | D(A,C,E)36A36+TDR | BGH96M080C4B | 31000 | 17.5 | 10.7 | 8.6 | 33800 | 24800 | 73.37% | 2.41 | 26400 | R-410A
214588331 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H175P149 | 926TC48080V17*** | 34400 | 16 | 9.5 | 8.1 | 36200 | 34400 | 95.03% | 2 | 28000 | R-410A
211168146 | 1.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X24A1 | 4PXFH003AZ3+TDR | *DHMB080ACV3 | 23200 | 18 | 12 | 8.5 | 20200 | 19300 | 95.54% | 2.48 | 16800 | R-410A
210598368 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EN(A,D)4X48L24**+WALLCON | *95CSU1002122A* | 24200 | 17 | 11.5 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
212924872 | 1.92 | Yes | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | D(A,C,E)24C34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
210597840 | 1.98 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L21A*+WALLCON | *80CSU1002120A* | 23800 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
210597876 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L21A*+WALLCON | *96CTN1002122A* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
216734880 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3717AM* | 83*CA36040C17*** | 23600 | 17 | 11 | 8.5 | 21200 | 18700 | 88.21% | 1.94 | 17800 | R-454B
214377805 | 1.83 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | AE(D,N,U)+CM24B34+TDR |  | 22000 | 16.8 | 11 | 8.5 | 24000 | 22000 | 91.67% | 1.8 | 16000 | R-410A
213613450 | 1.46 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | AFM234+TDR |  | 17500 | 15.2 | 9.8 | 8.2 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
212861174 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | C(A,C,D,E)60C44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
214056985 | 4 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX60HP230V1AO | L(E,G)M48J4 |  | 48000 | 17 | 11 | 9 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
215866275 | 1.95 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96MSAA48080B** | 23400 | 16.5 | 9.8 | 8.5 | 27000 | 20600 | 76.3% | 3.06 | 19400 | R-410A
215940523 | 2.88 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *80CSU0401712B* | 34600 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
214595223 | 2 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M364+TDR |  | 24000 | 15.2 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214588262 | 1.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P039 | 926TC30040V14*** | 22400 | 15.2 | 9.5 | 8.5 | 25400 | 24600 | 96.85% | 2.06 | 18600 | R-410A
215866283 | 1.87 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96MSAA60080C** | 22400 | 17 | 9.8 | 8.1 | 26200 | 20200 | 77.1% | 2.86 | 19100 | R-410A
213613492 | 1.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24F4 |  | 22800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213613493 | 1.95 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24G4 |  | 23400 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213613494 | 1.98 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24H4 |  | 23800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
215669943 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CSU0601716A* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
215670609 | 2.78 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | FCMA5B36L0C*+WALLCON |  | 33400 | 18.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
213613498 | 1.9 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36A4 |  | 22800 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212986353 | 1.45 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L14** | *96MSN0401410A* | 17400 | 15.5 | 10.5 | 8.5 | 18500 | 19200 | 103.8% | 2.3 | 12400 | R-410A
214377810 | 2.65 | No | No | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | AE(D,N,U)+DM48E34+TDR |  | 31800 | 15.9 | 9.8 | 8.5 | 34600 | 28000 | 80.92% | 1.8 | 24000 | R-410A
216441213 | 1.92 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | SM6*31+TXV |  | 23000 | 19 | 12 | 9.5 | 22400 | 16600 | 74.11% | 2.1 | 17400 | R-454B
212861165 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | D(A,C,E)60C44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
212861166 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | D(A,C,E)60D44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
212925910 | 2.67 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
212925909 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | C(A,C,D,E)24B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
212924874 | 1.92 | Yes | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | D(A,C,E)25B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
214377806 | 1.85 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | AE(D,N,U)+CM30A34+TDR |  | 22200 | 16.8 | 11 | 8.5 | 23800 | 22000 | 92.44% | 1.8 | 16000 | R-410A
215296855 | 2.82 | No | No | Wells | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WUCA-36HFMO | H,A,DE32936+TD |  | 33800 | 15.2 | 9.5 | 8.2 | 36200 | 31200 | 86.19% | 1.78 | 26400 | R-410A
214588265 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 926TC30040V14*** | 23200 | 16 | 10 | 8.5 | 24800 | 24400 | 98.39% | 2.06 | 18200 | R-410A
212924876 | 2.67 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
216776732 | 3.71 | Yes | Yes | KENMORE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | (C,H,T)5H3V48*K*AAA* | H,GG35*48+TXV | *96CTN0802120B* | 44500 | 20 | 11 | 8.1 | 50000 | 37600 | 75.2% | 1.9 | 42500 | R-454B
215866302 | 1.97 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96MSAA48060B** | 23600 | 16.5 | 9.8 | 9.5 | 26600 | 20800 | 78.2% | 3.09 | 19400 | R-410A
210597944 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X43L21A*+WALLCON | *80CTL0451712A* | 24200 | 16.5 | 11 | 8.1 | 21600 | 16800 | 77.78% | 2 | 20800 | R-410A
210597960 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X43L21A*+WALLCON | *95CSU0802120A* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
215037833 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL17XP1-048-230A** | CH60B34+TDR | ML193UH110XE48C* | 45000 | 15.5 | 12.4 | 8.1 | 44500 | 32000 | 71.91% | 2.8 | 31000 | R-410A
212924870 | 1.83 | Yes | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | C(A,C,D,E)24B34+TDR |  | 22000 | 15.2 | 10 | 8.1 | 22400 | 21200 | 94.64% | 1.78 | 14000 | R-410A
214588269 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P219 | 926TC30040V14*** | 23400 | 16 | 10 | 8.5 | 24800 | 24400 | 98.39% | 2.06 | 18200 | R-410A
213356136 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV+CBPE4B* |  | 24200 | 18 | 10.5 | 8.85 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
212925900 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | D(A,C,E)60D44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215683642 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3017AM*+UI | 986TD42080C17*** | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20200 | R-454B
215683674 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3717AM*+UI | 88*TB48070C17*** | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
212973914 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D,W)4X36L17** | *96VSN0801716B* | 23400 | 16.5 | 10 | 8.1 | 25800 | 24200 | 93.8% | 2 | 18900 | R-410A
214056982 | 2.73 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX36HP230V1AO | L(E,G)M36B4 |  | 32800 | 16 | 10 | 8.9 | 35000 | 28000 | 80% | 1.8 | 24000 | R-410A
214588332 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | V,C36H175P149 | 926TC48080V17*** | 34400 | 16 | 9.5 | 8.1 | 36200 | 34400 | 95.03% | 2 | 28000 | R-410A
214588282 | 1.92 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P429 | 926TC36060V14*** | 23000 | 17 | 9.5 | 8.5 | 24600 | 23600 | 95.93% | 2 | 18100 | R-410A
211755736 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TL8E060A12UH11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
210597976 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X43L21A*+WALLCON | *96CTN1002122A* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
215670469 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL1352422B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
215670519 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0801714B* | 34400 | 16.5 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
215866278 | 1.93 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96VTAB48060B** | 23200 | 16.5 | 9.8 | 8.5 | 26800 | 20600 | 76.87% | 3.02 | 19400 | R-410A
212861172 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | C(A,C,D,E)60A44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
212861173 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
210598172 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *80CTL0701412A* | 24200 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
211755877 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE080B12MP11 | 31000 | 17.8 | 9.2 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
211755895 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLV100C16MP12 | 31000 | 17.3 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211290760 | 2.65 | Yes | No | ARMSTRONG AIR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4SHP18LX136P | C(A,C,D,E)36A34+TDR | A97USMV090C16 | 31800 | 17.9 | 10.7 | 8.2 | 34200 | 24200 | 70.76% | 2.18 | 23600 | R-410A
215670537 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 987MC66100C21*** | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 30000 | R-454B
215866273 | 1.93 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96MSAA30040A** | 23200 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.98 | 19500 | R-410A
215866296 | 1.95 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96MSAA48080B** | 23400 | 16.5 | 9.8 | 8.5 | 27000 | 20400 | 75.56% | 2.96 | 19400 | R-410A
215866276 | 1.92 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96MSAA60080C** | 23000 | 17 | 9.8 | 8.5 | 26200 | 20400 | 77.86% | 3 | 19100 | R-410A
215866310 | 2.87 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | D(A,C,E)36A34+TDR | PG96MSAA60080C** | 34400 | 16 | 9 | 8.1 | 39000 | 32600 | 83.59% | 2.58 | 29600 | R-410A
214588339 | 3.05 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P299 | 926TC60080V21*** | 36600 | 16 | 10 | 8.5 | 36400 | 34400 | 94.51% | 2.06 | 28200 | R-410A
213613502 | 2 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36E4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213613503 | 2 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36F4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212925902 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | D(A,C,E)24C34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
206417164 | 2.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL9036A1 | 4PXFH005AZ3+TDR | *UD2B060ACV3 | 35600 | 17 | 11 | 8.5 | 33800 | 24400 | 72.19% | 2.69 | 23600 | R-410A
213885882 | 1.83 | Yes | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | C(A,C,D,E)36C24+TDR |  | 22000 | 15.2 | 10 | 8.1 | 24000 | 21400 | 89.17% | 1.8 | 15000 | R-410A
215669553 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6121AM*+UI | 987MC42080C17*** | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215674257 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1002122B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 41500 | R-454B
215866267 | 1.92 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24A34+TDR | PG96MSAA48060B** | 23000 | 16.5 | 9.8 | 9.5 | 26600 | 20600 | 77.44% | 2.96 | 19400 | R-410A
215866285 | 1.92 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96VTAB48060B** | 23000 | 16.5 | 9.8 | 8.5 | 26800 | 20400 | 76.12% | 2.9 | 19400 | R-410A
215866286 | 1.85 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30A34+TDR | PG96VTAB60100C** | 22200 | 17.5 | 9.8 | 8.1 | 26200 | 20000 | 76.34% | 2.87 | 19000 | R-410A
215292124 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GG32930 | *92MSN1002120A* | 23000 | 17 | 10 | 8.5 | 24800 | 23800 | 95.97% | 2.02 | 18100 | R-410A
215292158 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE9J936 | *92MSN1002120A* | 23600 | 17 | 10.5 | 8.5 | 24800 | 23800 | 95.97% | 2.02 | 18100 | R-410A
214056984 | 4 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX60HP230V1AO | L(E,G)M48I4 |  | 48000 | 17 | 11 | 9 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
212925903 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | D(A,C,E)24D34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215289594 | 1.43 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | HG8J936 | *92MSN0401712A* | 17100 | 15.2 | 10.5 | 8.1 | 16700 | 18900 | 113.2% | 2.3 | 11400 | R-410A
215683692 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 88*TB36045C17*** | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
212925901 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | D(A,C,E)24A44+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
211755912 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211755926 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211755962 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211755979 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TL9E060B12UH11 | 32000 | 18 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.46 | 25600 | R-410A
211756028 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.46 | 25800 | R-410A
211756079 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211756095 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
214588283 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 926TC36060V14*** | 23200 | 16 | 10 | 8.5 | 25200 | 26400 | 104.8% | 2.28 | 18400 | R-410A
212861167 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | D(A,C,E)24A44+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
214312491 | 4.5 | Yes | No | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH4860ZGDA* | L(E,G)M60E4 |  | 54000 | 15.2 | 10 | 8.5 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
216735232 | 1.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3717AM* | 926SB36060V14*** | 22600 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
213785652 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*3612AL*+UI | 59MN7C080C17**14 | 33000 | 18 | 11 | 8.5 | 37200 | 26400 | 70.97% | 2 | 31800 | R-410A
213286686 | 1.45 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | CE1801C+TXV |  | 17400 | 17 | 10.5 | 8.6 | 17000 | 19300 | 113.5% | 2.3 | 11500 | R-410A
216980140 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | L(E,G)M48AJ |  | 43500 | 17.9 | 11 | 8.1 | 48500 | 48500 | 100% | 2.1 | 37600 | R-454B
212861168 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | D(A,C,E)24C34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
216687190 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF98MV306017UP | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
214056979 | 1.93 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX36HP230V1AO | L(E,G)M24D4 |  | 23200 | 17 | 12 | 8.8 | 24000 | 22000 | 91.67% | 1.8 | 16000 | R-410A
212924877 | 3.92 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | C(A,C,D,E)48C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
215670317 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 987MC66120C24*** | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
211467474 | 3.54 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YH2F48TB21 | D(A,C,E)48B44+TDR | YPLC100C16MP13 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
212868091 | 3.92 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX60HP230V1AO | D(A,C,E)61C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
212986996 | 1.44 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L14A* | *96MSN0601412A* | 17300 | 16 | 10.5 | 8.5 | 18200 | 19400 | 106.6% | 2.34 | 12300 | R-410A
216051832 | 2.78 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | FE*G34*36+TXV |  | 33400 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
206417166 | 2.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL9036A1 | 4PXFH005AZ3+TDR | *UD2C080ACV4 | 35600 | 17 | 11.5 | 8.7 | 33200 | 24000 | 72.29% | 2.81 | 23200 | R-410A
211755755 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8E040A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.5 | 25200 | R-410A
211755825 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9E080C16MP12 | 32200 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
211755873 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TMLE040A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.5 | 25200 | R-410A
211755889 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLE120C16MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
216687223 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF96TV508521M4 | 53500 | 16 | 10 | 10 | 53500 | 49000 | 91.59% | 2 | 51000 | R-454B
214056981 | 1.93 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX36HP230V1AO | L(E,G)M24H4 |  | 23200 | 17 | 12 | 8.8 | 24000 | 22000 | 91.67% | 1.8 | 16000 | R-410A
216760255 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,RG48*60+TXV+AEFE5* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
211467458 | 3.54 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YH2F48TB21 | D(A,C,E)48B44+TDR | TM8V100C16MP12 | 42500 | 15.9 | 11.5 | 8.2 | 44000 | 30800 | 70% | 3.13 | 30200 | R-410A
216687216 | 4.5 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF80TV507521DZ | 54000 | 17 | 10 | 10 | 54000 | 48500 | 89.81% | 2 | 51000 | R-454B
213312008 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V36H***P219+CBPE3A* |  | 24000 | 18 | 10.5 | 8.9 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
216735468 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3721AM* | 8(0,1)*SB48070M17*** | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
214056991 | 1.93 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | L(E,G)M24D4 |  | 23200 | 17 | 12 | 8.8 | 24000 | 22000 | 91.67% | 1.8 | 16000 | R-410A
214056992 | 1.9 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | L(E,G)M24G4 |  | 22800 | 17 | 11.9 | 8.7 | 23800 | 22000 | 92.44% | 1.8 | 15900 | R-410A
216735582 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3721AM* | 83*SB60100M21*** | 23200 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216735850 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3721AM* | 916SA66100M21*** | 23400 | 16 | 11 | 8.5 | 20800 | 18600 | 89.42% | 1.98 | 17600 | R-454B
214056993 | 1.93 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | L(E,G)M24H4 |  | 23200 | 17 | 12 | 8.8 | 24000 | 22000 | 91.67% | 1.8 | 16000 | R-410A
215866294 | 1.93 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96MSAA30040A** | 23200 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.9 | 19500 | R-410A
212985882 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96MSN0261410A* | 17800 | 16.5 | 10.5 | 8.1 | 17800 | 19400 | 109% | 2.34 | 12300 | R-410A
211756025 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM9E060A10MP12 | 31800 | 17.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.48 | 25400 | R-410A
211756032 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9E080C16MP12 | 32200 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
211756066 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLE060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211756107 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
213613463 | 1.5 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M36B4 |  | 18000 | 15.2 | 9.8 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
211627558 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TL8E080C16UH11 | 32000 | 17.5 | 9.9 | 8.5 | 25600 | 32000 | 125% | 2.88 | 25600 | R-410A
215683926 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**3721AM*+UI | 986TD42060C17*** | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215683944 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4221AM*+UI | 88*TB48090C17*** | 33200 | 18 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215683978 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 88*TB36045C17*** | 34000 | 17.5 | 9.5 | 9 | 35600 | 25400 | 71.35% | 1.86 | 30800 | R-454B
212861175 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | C(A,C,D,E)24B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
216093480 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG35*48+TXV+AEFE5* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
215670187 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 88*TB60070C21*** | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215670407 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 88*TB36070C14*** | 34400 | 16.5 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
211755837 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
211755853 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9Y060B12MP11 | 32200 | 17.5 | 9.5 | 8.1 | 34000 | 29400 | 86.47% | 2.5 | 26600 | R-410A
211755904 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TP9C080B12MP13 | 32200 | 17 | 9.5 | 8.1 | 33600 | 29600 | 88.1% | 2.51 | 26600 | R-410A
216762914 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG48*48+TXV+AEFE4B* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
211628381 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TPLC100C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
216762905 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | A48VGC*+TXV+AEFE5* |  | 45500 | 17 | 11.5 | 8.35 | 45000 | 33200 | 73.78% | 1.84 | 37000 | R-454B
211755758 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
215866299 | 1.93 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96VTAB48060B** | 23200 | 16.5 | 9.8 | 8.5 | 26800 | 20600 | 76.87% | 2.93 | 19400 | R-410A
216093483 | 4.04 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG84*60+TXV+AEFE5* |  | 48500 | 19 | 12 | 10 | 46500 | 48000 | 103.2% | 2.1 | 47500 | R-454B
215828422 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | FE*TT9*60+TXV |  | 51500 | 18.5 | 11.3 | 9.7 | 53000 | 54500 | 102.8% | 2.06 | 54000 | R-454B
215866279 | 1.9 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)24B44+TDR | PG96VTAB60100C** | 22800 | 17.5 | 9.8 | 8.5 | 26200 | 20200 | 77.1% | 3.02 | 19000 | R-410A
212925908 | 4.21 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD60W/A-D(U) | C(A,C,D,E)60C44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
215683992 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 935CB60080C21*** | 34400 | 17.5 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
211627762 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A36+TDR | TM8V100C20MP12 | 31600 | 16.5 | 8.9 | 8.1 | 32400 | 27400 | 84.57% | 2.49 | 25000 | R-410A
215683994 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 935CB66100C21*** | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
215684076 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 88*TB66135C24*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215670557 | 2.75 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 986TD30040C14*** | 33000 | 15.5 | 9 | 8.5 | 35000 | 25200 | 72% | 1.78 | 30200 | R-454B
215670387 | 2.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 83*CA48060C17*** | 34600 | 17 | 9.5 | 8.5 | 34600 | 25000 | 72.25% | 1.8 | 30000 | R-454B
215866305 | 1.92 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96VTAB30040A** | 23000 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.98 | 19500 | R-410A
214588278 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P749 | 926TC36040V17*** | 23200 | 16 | 10 | 8.5 | 24600 | 24000 | 97.56% | 2.02 | 18100 | R-410A
214588285 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 926TC36060V14*** | 23600 | 17 | 10 | 8.5 | 24600 | 23600 | 95.93% | 2 | 18100 | R-410A
214056990 | 1.9 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | L(E,G)M24C4 |  | 22800 | 17 | 11.9 | 8.7 | 23800 | 22000 | 92.44% | 1.8 | 15900 | R-410A
214377809 | 1.88 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | AE(D,N,U)+DM36A34+TDR |  | 22600 | 17 | 11.8 | 8.5 | 23800 | 22000 | 92.44% | 1.8 | 16000 | R-410A
210598260 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *80CTL0901716A* | 24400 | 17 | 11 | 8.1 | 21200 | 16500 | 77.83% | 2.04 | 20600 | R-410A
211755936 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755938 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | YP9C060B12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
211755955 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | YPLC060A12MP13 | 31000 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211755988 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211756038 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TM9V040A10MP12 | 31600 | 17 | 9.4 | 8.1 | 33200 | 27400 | 82.53% | 2.49 | 25200 | R-410A
211756087 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TP9C080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
213773866 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CAP**4824AL*+UI | 986TD66120C24*** | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
216093489 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG36*36+TXV+AEFE4B* |  | 34200 | 17 | 11.7 | 8.5 | 32600 | 33800 | 103.7% | 1.8 | 33200 | R-454B
216093492 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG84*60+TXV+AEFE5* |  | 46000 | 17 | 11.7 | 8.5 | 45000 | 33200 | 73.78% | 1.86 | 37000 | R-454B
207455316 | 1.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*23/37Z9 | SL280UH090V36B* | 22800 | 23 | 15 | 9.7 | 19800 | 19500 | 98.48% | 1.98 | 22200 | R-410A
215684094 | 2.72 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4212AM*+UI | 986TD30040C14*** | 32600 | 15.2 | 9 | 8.5 | 36000 | 25600 | 71.11% | 1.76 | 31000 | R-454B
211628026 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9V100C20MP12 | 32000 | 17.5 | 9.4 | 8.5 | 26000 | 32400 | 124.6% | 2.88 | 26000 | R-410A
211628078 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9Y080C16MP11 | 32000 | 18.5 | 9.4 | 8.5 | 25800 | 32200 | 124.8% | 2.85 | 25800 | R-410A
211755892 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TMLV060A12MP12 | 31000 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211756065 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
211756099 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211756108 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | YP9C060B12MP13 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
214056980 | 1.9 | Yes | Yes | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX36HP230V1AO | L(E,G)M24G4 |  | 22800 | 17 | 11.9 | 8.7 | 23800 | 22000 | 92.44% | 1.8 | 15900 | R-410A
212924884 | 4.21 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | D(A,C,E)60D44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
216093470 | 2.7 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*G32*36+TXV |  | 32400 | 18 | 11 | 9.05 | 32200 | 24000 | 74.53% | 1.92 | 27000 | R-454B
215942599 | 3.71 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVD5X61M21A*+WALLCON | *96CTN0801714B* | 44500 | 20 | 11.5 | 8.1 | 54000 | 37800 | 70% | 1.95 | 43000 | R-454B
212925911 | 2.67 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | GUD36W/A-D(U) | C(A,C,E)37C24+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
212924873 | 1.92 | Yes | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | D(A,C,E)24D34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215866301 | 1.93 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96MSAA30040A** | 23200 | 16 | 9 | 8.5 | 27000 | 20600 | 76.3% | 2.99 | 19500 | R-410A
214588264 | 1.92 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L129 | 926TC30040V14*** | 23000 | 16 | 9.5 | 8.5 | 25400 | 26800 | 105.5% | 2.3 | 18500 | R-410A
214588266 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P149 | 926TC30040V14*** | 23400 | 16 | 10 | 8.5 | 24800 | 24400 | 98.39% | 2.06 | 18200 | R-410A
214588280 | 1.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H175P139 | 926TC36040V17*** | 23000 | 16 | 10 | 8.5 | 24800 | 24800 | 100% | 2.08 | 18200 | R-410A
214056994 | 4 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH4860ZGDA* | L(E,G)M48I4 |  | 48000 | 17 | 11 | 9 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
214588347 | 2.92 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L159 | 926TC66100V21*** | 35000 | 17 | 10 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
214588281 | 1.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P039 | 926TC36060V14*** | 22400 | 16 | 9.5 | 8.5 | 25200 | 25000 | 99.21% | 2.12 | 18500 | R-410A
213613495 | 2 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24I4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
212863956 | 2.67 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | D(A,C,E)36B34+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
216776728 | 2.83 | Yes | Yes | KENMORE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | (C,H,T)5H3V36*K*AAA* | H,GG8J*36+TXV | *96CTN0801714B* | 34000 | 21 | 11.5 | 8.5 | 36400 | 28400 | 78.02% | 2.02 | 32000 | R-454B
216093488 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG35*48+TXV+AEFE5* |  | 44000 | 17 | 11 | 8.1 | 44500 | 33200 | 74.61% | 1.8 | 36800 | R-454B
216093491 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | FE*TT4*60+TXV |  | 46000 | 17 | 11.7 | 8.5 | 45000 | 33200 | 73.78% | 1.87 | 37000 | R-454B
212924875 | 2.67 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH2436ZGDA* | C(A,C,E)37C24+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
213205543 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80ES(N,L)0902420A* | 35400 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
212924881 | 4.21 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | C(A,C,D,E)60B44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
212924883 | 3.92 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | D(A,C,E)60C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
213613501 | 2 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36D4 |  | 24000 | 16 | 10 | 9 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
213613485 | 1.92 | Yes | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M244+TDR |  | 23000 | 16 | 10 | 8.5 | 25800 | 20200 | 78.29% | 2.92 | 19000 | R-410A
215674227 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU1002122B* | 45000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
215674277 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1002122B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 41500 | R-454B
213355361 | 2.92 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M36E6 |  | 35000 | 18 | 9 | 8.1 | 35400 | 26000 | 73.45% | 2.82 | 25000 | R-410A
215669253 | 2.82 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 987MC66100C21*** | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
206417165 | 2.93 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL9036A1 | 4PXFH005AZ3+TDR | *UD2B080ACV3 | 35200 | 17 | 11 | 8.5 | 33600 | 24400 | 72.62% | 2.71 | 23600 | R-410A
213613487 | 1.83 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24A4 |  | 22000 | 15.8 | 9.7 | 9 | 26400 | 20400 | 77.27% | 2.88 | 19200 | R-410A
213927963 | 2.47 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM36SZA21S | D(A,C,E)43C34+TDR |  | 29600 | 15.5 | 11.3 | 9.4 | 30000 | 24200 | 80.67% | 2.08 | 23000 | R-410A
211593683 | 2.97 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG48936 | 926TB60080V21*** | 35600 | 15.2 | 10 | 8.1 | 37400 | 34400 | 91.98% | 2 | 28200 | R-410A
215250406 | 4 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH4860ZGDA* | L(E,G)M60M4 |  | 48000 | 17 | 11 | 9 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
216761997 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HE48*60+TXV+AEFE5* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
216762898 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HE35*48+TXV+AEFE5* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
211628260 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TP9C060B12MP13 | 32200 | 17.5 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.82 | 25600 | R-410A
211628377 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TPLC100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 25400 | 31600 | 124.4% | 2.87 | 25400 | R-410A
215683690 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CAA**3721AM*+UI | 83*CA48060C17*** | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215669353 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6024AM*+UI | 935CB66100C21*** | 34400 | 18 | 10 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
215669453 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6121AM*+UI | 88*TB36045C17*** | 34400 | 17.5 | 9.5 | 9 | 34600 | 25200 | 72.83% | 1.9 | 30200 | R-454B
211628446 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | YP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.53 | 25400 | R-410A
211755793 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8Y060A12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33400 | 27400 | 82.04% | 2.5 | 25200 | R-410A
211756113 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YP9C100C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 34000 | 27400 | 80.59% | 2.54 | 25400 | R-410A
211756127 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YPLC100C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211756129 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.49 | 25200 | R-410A
211755811 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM9E040A10MP12 | 32000 | 17 | 9.5 | 8.1 | 33400 | 28400 | 85.03% | 2.51 | 25800 | R-410A
215683976 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4321AM*+UI | 83*CA60100C21*** | 34400 | 17.5 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215669103 | 2.82 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**4821AM*+UI | 83*CA48060C17*** | 33800 | 18 | 9.5 | 9 | 35000 | 25200 | 72% | 1.88 | 30400 | R-454B
211755893 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLV060A12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
211755963 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | YPLC080C16MP13 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
211756011 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.5 | 25200 | R-410A
213205642 | 2.95 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *95ESN0802120A* | 35400 | 15.5 | 9.5 | 8.1 | 39500 | 32000 | 81.01% | 2.52 | 29600 | R-410A
213205658 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *95ESN1002122A* | 35400 | 15.5 | 10 | 8.5 | 39500 | 31600 | 80% | 2.71 | 29400 | R-410A
215670347 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 986TD42080C17*** | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
213205691 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96VTN1002122A* | 35200 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
213613460 | 1.5 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24J4 |  | 18000 | 15.2 | 10 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214588215 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PL36H210P299 | 926TC36040V17*** | 17400 | 16 | 10.5 | 8.5 | 16400 | 18400 | 112.2% | 2.24 | 11200 | R-410A
214588210 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PL36H175P149 | 926TC30040V14*** | 17200 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
214588217 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L139 | 926TC36040V17*** | 17100 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
214588221 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H175P159 | 926TC36040V17*** | 17400 | 16 | 10.5 | 8.5 | 16400 | 18400 | 112.2% | 2.24 | 11200 | R-410A
214588228 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L139 | 926TC36060V14*** | 17400 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215821307 | 3.63 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | FE*BB9*48+TXV |  | 43500 | 16 | 11 | 8.1 | 44500 | 33200 | 74.61% | 1.8 | 37000 | R-454B
214588213 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P219 | 926TC30040V14*** | 17200 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
214588233 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PL36H***P449 | 926TC36060V14*** | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
215939685 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CAA**4221AM*+UI | 987TA42080C17*** | 32400 | 19.5 | 11 | 9.5 | 35200 | 27200 | 77.27% | 2 | 31000 | R-454B
215939935 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CSAH*3612AM*+UI | 986TD60080C21*** | 33200 | 19 | 11 | 9 | 35000 | 26800 | 76.57% | 1.92 | 30800 | R-454B
213613459 | 1.5 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24I4 |  | 18000 | 15.2 | 10 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
212436971 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | F,PE*G22924 |  | 17400 | 17 | 10.5 | 8.65 | 17000 | 19400 | 114.1% | 2.32 | 11500 | R-410A
215669077 | 2.87 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *96CTN0801714B* | 34400 | 18 | 10 | 8.1 | 35400 | 25200 | 71.19% | 1.9 | 30600 | R-454B
214588207 | 1.42 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P429 | 926TC30040V14*** | 17000 | 16 | 9.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
214588223 | 1.44 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L159 | 926TC36040V17*** | 17300 | 16 | 10.5 | 8.5 | 16400 | 18400 | 112.2% | 2.24 | 11200 | R-410A
214588212 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L159 | 926TC30040V14*** | 17200 | 16 | 10.5 | 8.5 | 16500 | 18500 | 112.1% | 2.26 | 11200 | R-410A
215654048 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | TM8V100C20MP12 | 41500 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215654055 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | Y81E120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
213613464 | 1.5 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M36C4 |  | 18000 | 15.2 | 10 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
212863957 | 2.67 | No | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | C(A,C,E)37C24+TDR |  | 32000 | 15.2 | 9.5 | 8.5 | 34000 | 24000 | 70.59% | 1.8 | 22000 | R-410A
215670479 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU0601716B* | 34400 | 16.5 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
215670549 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN1202422B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
216054316 | 4.54 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG86*60+TXV+AEFE5* |  | 54500 | 16 | 10 | 8.45 | 54000 | 39000 | 72.22% | 1.86 | 39000 | R-454B
213613449 | 1.47 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M244+TDR |  | 17600 | 15.2 | 9.8 | 8.2 | 19200 | 18300 | 95.31% | 2.2 | 12800 | R-410A
214588219 | 1.43 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H175P149 | 926TC36040V17*** | 17200 | 16 | 10.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
214377808 | 3.79 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH4860ZGDA* | AE(D,N,U)+CM60A44+TDR |  | 45500 | 17 | 10.8 | 8.5 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
216056758 | 3.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C120D20MP13 | 40000 | 17.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216056805 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8V100C20MP12 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
216056838 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y100C20MP11 | 41000 | 17 | 10.5 | 8.5 | 46000 | 34800 | 75.65% | 2 | 34600 | R-454B
216056840 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9Y120D20MP11 | 41000 | 17.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32000 | R-454B
215654052 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | Y81E100C16SMPS1 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
214569545 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CAP**4224AL*+UI | 987MC60080C21*** | 33200 | 19 | 11.5 | 9.5 | 37800 | 26600 | 70.37% | 2 | 32000 | R-410A
214569599 | 2.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CAP**6121AL*+UI | 935CB60080C21*** | 34800 | 19.5 | 12 | 9 | 35800 | 25200 | 70.39% | 2.02 | 30000 | R-410A
211756063 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | TMLE040A12MP11 | 32000 | 18 | 9.9 | 8.1 | 33600 | 27200 | 80.95% | 2.5 | 25200 | R-410A
211756080 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | TMLV100C16MP12 | 32000 | 17.5 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.54 | 25400 | R-410A
213356129 | 1.48 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A36VCA+TXV+CBPE3A* |  | 17800 | 15.5 | 10.5 | 9 | 17100 | 19400 | 113.5% | 2.4 | 11500 | R-410A
214377813 | 3.75 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | CM48C44+TDR |  | 45000 | 15.2 | 9.9 | 8.3 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
216687191 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF98MV508521UP | 34200 | 21 | 12 | 10 | 34200 | 29400 | 85.96% | 2 | 30000 | R-454B
214588208 | 1.4 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L129 | 926TC30040V14*** | 16800 | 16 | 9.5 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
216675659 | 1.97 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X30M14A* | *80MS(N,L)0451412A* | 23600 | 15.2 | 9.8 | 8.5 | 24200 | 19400 | 80.17% | 1.9 | 18900 | R-454B
216675745 | 2.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X25M17A* | *80MS(N,L)0451714A* | 24200 | 15.2 | 10 | 8.5 | 23200 | 19100 | 82.33% | 1.96 | 18500 | R-454B
215828423 | 4.42 | No | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | FE*TT9*60+TXV |  | 53000 | 16 | 9.5 | 8.3 | 54000 | 39000 | 72.22% | 1.84 | 39000 | R-454B
215674117 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0802120B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.06 | 42500 | R-454B
216762899 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HE2K*60+TXV+AEFE5* |  | 47000 | 18 | 11.7 | 9.7 | 46500 | 48000 | 103.2% | 2.04 | 47500 | R-454B
215940343 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU0401712B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 33000 | R-454B
215940423 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0601716B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
215940643 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M21A*+WALLCON | *80CSU0601716B* | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.04 | 32000 | R-454B
215940693 | 2.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVD5X42M24A*+WALLCON | *96CTN0802120B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
214056995 | 4 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH4860ZGDA* | L(E,G)M48J4 |  | 48000 | 17 | 11 | 9 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
215866307 | 1.92 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36B34+TDR | PG96VTAB60100C** | 23000 | 17.5 | 9.8 | 8.5 | 26200 | 20200 | 77.1% | 3.04 | 19000 | R-410A
213613499 | 1.95 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M36B4 |  | 23400 | 15.2 | 9.8 | 8.5 | 26400 | 23400 | 88.64% | 1.92 | 19200 | R-410A
214056988 | 4.5 | Yes | No | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX60HP230V1AO | L(E,G)M60I4 |  | 54000 | 15.8 | 10.3 | 9 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
215942379 | 2.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *96CTN0601714B* | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
212861169 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | D(A,C,E)24D34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215670487 | 2.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 935CB66100C21*** | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.92 | 29800 | R-454B
215670517 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 987MC42080C17*** | 34400 | 16.5 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
213613488 | 1.9 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | L(E,G)M24B4 |  | 22800 | 16 | 9.9 | 8.8 | 26400 | 20400 | 77.27% | 2.84 | 19200 | R-410A
215670567 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 986TD42060C17*** | 34200 | 16.5 | 9.5 | 8.5 | 34800 | 25200 | 72.41% | 1.78 | 30200 | R-454B
215866288 | 1.97 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)30B34+TDR | PG96MSAA48060B** | 23600 | 16.5 | 9.8 | 9.5 | 26600 | 20600 | 77.44% | 3.02 | 19400 | R-410A
215866295 | 1.97 | No | Yes | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | D(A,C,E)36A34+TDR | PG96MSAA48060B** | 23600 | 16.5 | 9.8 | 9 | 26600 | 20600 | 77.44% | 2.97 | 19400 | R-410A
215670607 | 2.78 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | FE5BN(B,X)C36L*+UI |  | 33400 | 18.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215667398 | 1.92 | No | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CTL0451712B* | 23000 | 16.5 | 10 | 8.5 | 24000 | 16800 | 70% | 1.86 | 20200 | R-454B
215667364 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CSU0401712A* | 23000 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215667381 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CSU0601716A* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
214588226 | 1.44 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P429 | 926TC36060V14*** | 17300 | 16 | 10.5 | 8.5 | 16900 | 19400 | 114.8% | 2.38 | 11400 | R-410A
215654050 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | Y81E080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
215654057 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | TM8V080C16MP12 | 41000 | 17 | 11.7 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215669703 | 2.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CAA**6124AM*+UI | 987MC66100C21*** | 35000 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215670287 | 2.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 987MC42080C17*** | 34000 | 16.5 | 9 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
215667164 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CTL0451712B* | 23800 | 17 | 10 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
215667181 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CTL0701412B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16400 | 70.69% | 2 | 19700 | R-454B
215667330 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M14A*+WALLCON | *80CTL0701412B* | 23000 | 17 | 10 | 8.5 | 23800 | 16700 | 70.17% | 1.86 | 20200 | R-454B
215667414 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CTL0701412B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
215667597 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0451712B* | 23000 | 16.5 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20200 | R-454B
215667699 | 1.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *96CTN0401410B* | 22600 | 16 | 9.5 | 8.5 | 24200 | 17000 | 70.25% | 1.84 | 20400 | R-454B
215667580 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0601716A* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
206417167 | 3 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWL9036A1 | 4PXFH005AZ3+TDR | *UD2C100ACV5 | 36000 | 17 | 11.5 | 8.7 | 33400 | 24200 | 72.46% | 2.8 | 23400 | R-410A
215670227 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*4812AM*+UI | 88*TB66135C24*** | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215670477 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 935CB48060C17*** | 34400 | 16.5 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
214279022 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214574514 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D,W)4X42L21**+WALLCON | *80CTL0702120B* | 31800 | 17 | 11 | 8.1 | 33000 | 24600 | 74.55% | 1.88 | 31400 | R-410A
214574614 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D,W)4X48L21**+WALLCON | *97CMN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
214574684 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D)4X48L24**+WALLCON | *96CTN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31400 | R-410A
216687208 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF96TV507021M4 | 45500 | 18 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
215666964 | 1.9 | No | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CSU0401712A* | 22800 | 16.5 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20200 | R-454B
215667347 | 1.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M14A*+WALLCON | *96CTN0401410B* | 22600 | 15.5 | 9 | 8.5 | 24200 | 17100 | 70.66% | 1.84 | 20600 | R-454B
215667614 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701412B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215667681 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *97CMN0801714B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
215670429 | 2.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0702120B* | 34600 | 17 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
214279016 | 2.78 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | F,PE*G34936 |  | 33400 | 18 | 11.7 | 9.3 | 32600 | 23600 | 72.39% | 1.88 | 27000 | R-410A
214279019 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*G32930 |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
215667649 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0901716B* | 23200 | 17 | 10.5 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
211627792 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM8Y060A12MP11 | 32000 | 18 | 9.9 | 8.1 | 25200 | 31400 | 124.6% | 2.83 | 25200 | R-410A
211627829 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM8Y100C16MP11 | 31400 | 18.3 | 9.8 | 8.2 | 25200 | 31800 | 126.2% | 2.82 | 25400 | R-410A
211627926 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TM9E080C16MP12 | 33000 | 18 | 10 | 8.1 | 33600 | 27200 | 80.95% | 2.53 | 25200 | R-410A
210597868 | 1.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L21A*+WALLCON | *96CTN0601714A* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.94 | 20800 | R-410A
210597900 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L24A*+WALLCON | *80CTL1352422A* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
210597916 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X42L24A*+WALLCON | *96CTN1202422A* | 23800 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
215662864 | 3.79 | No | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | FCMA5B48L0C*+WALLCON |  | 45500 | 19 | 10.5 | 9 | 48000 | 33600 | 70% | 2.1 | 42000 | R-454B
216960325 | 1.51 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A3J+TDR | S9V2B040D3PSC+LRP | 18100 | 18.9 | 11.2 | 8.5 | 22800 | 26400 | 115.8% | 2.6 | 21600 | R-454B
215667765 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *80CTL0901716B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
215667781 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0801714B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19900 | R-454B
215654064 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | Y81E100C20SMPS1 | 41000 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215654066 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | Y81E120C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
215821297 | 1.87 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | FE*E31*24+TXV |  | 22400 | 16 | 11 | 8.1 | 22200 | 16800 | 75.68% | 1.78 | 17900 | R-454B
215670507 | 2.87 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 987MC60060C21*** | 34400 | 16 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
211628076 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM9Y080C16MP11 | 31200 | 18.3 | 9.3 | 8.3 | 25600 | 32200 | 125.8% | 2.78 | 25800 | R-410A
214588345 | 3 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P299 | 926TC66100V21*** | 36000 | 17 | 10.5 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
215821300 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*G32*24+TXV |  | 22600 | 18 | 12 | 9.2 | 22400 | 17000 | 75.89% | 1.94 | 21400 | R-454B
210597932 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X43L21A*+WALLCON | *80CSU0401712A* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
211780575 | 1.98 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE31930 | *92ESN0801716A* | 23800 | 17 | 10 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
215413747 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG8J936+AEFE4B* |  | 23600 | 20 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215413749 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | PL36H175P459+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212380857 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG82936 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380858 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P149 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380859 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P159 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214440919 | 1.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | BV**B1925 |  | 22000 | 17 | 12 | 9 | 22200 | 17200 | 77.48% | 1.92 | 21400 | R-410A
213258364 | 1.97 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32936 | *96VTN0601714A* | 23600 | 16 | 10 | 8.5 | 25200 | 24000 | 95.24% | 2.02 | 18400 | R-410A
213258948 | 1.9 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE7J936 | *96VTN0401410A* | 22800 | 16 | 9.5 | 8.5 | 24200 | 23800 | 98.35% | 2.02 | 18000 | R-410A
215667933 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN1002122B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215402575 | 1.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | BV**B1725 |  | 22000 | 17 | 12 | 9 | 22200 | 17200 | 77.48% | 1.92 | 21400 | R-410A
216776727 | 2.8 | Yes | Yes | KENMORE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | (C,H,T)5H3V36*K*AAA* | H,GG8J*36+TXV | *96CTN0601714B* | 33600 | 21 | 11 | 8.5 | 36000 | 27800 | 77.22% | 2 | 31000 | R-454B
212480260 | 2.55 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | PL36H210P749 | 59SC2D100E21**20 | 30600 | 15.2 | 9 | 8.1 | 32600 | 26600 | 81.6% | 1.82 | 22400 | R-410A
215296853 | 2.82 | No | No | Wells | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WUCA-36HFMO | H,A,DE32(1,2)36+TXV+TD |  | 33800 | 15.2 | 9.5 | 8.2 | 36200 | 31200 | 86.19% | 1.78 | 26400 | R-410A
215670377 | 2.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CSAH*6012AM*+UI | 83*CA36040C17*** | 34600 | 17 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
215667000 | 1.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CTL0451712B* | 22600 | 16.5 | 9.5 | 9 | 24200 | 17000 | 70.25% | 1.94 | 20400 | R-454B
215869163 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG33936+AEFE3A* |  | 23400 | 19 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
216687205 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF80TV510021UH | 45500 | 19 | 12 | 10 | 45500 | 41500 | 91.21% | 2.1 | 42000 | R-454B
213147356 | 2.5 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | C36A***L139+AEFE4B* |  | 30000 | 15.2 | 8.5 | 8.3 | 33400 | 27000 | 80.84% | 1.78 | 22600 | R-410A
216687203 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF80TV507521DZ | 45500 | 19 | 12 | 10 | 45500 | 41500 | 91.21% | 2.1 | 42000 | R-454B
216687171 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF97MV508521DH | 22800 | 21 | 13 | 10 | 22800 | 18400 | 80.7% | 1.8 | 21200 | R-454B
216687173 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF98MV508521UP | 22800 | 21 | 13 | 10 | 22800 | 18400 | 80.7% | 1.8 | 21200 | R-454B
212380735 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P149 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214595215 | 1.5 | No | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A(E,F)M364+TDR |  | 18000 | 15.2 | 9.8 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214588220 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PL36H175P159 | 926TC36040V17*** | 17400 | 16 | 10.5 | 8.5 | 16400 | 18400 | 112.2% | 2.24 | 11200 | R-410A
213785195 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | CSPH*3012AL*+UI | 58TN*B110C21**20 | 23400 | 18.5 | 12.5 | 10 | 26800 | 19900 | 74.25% | 2.44 | 25000 | R-410A
215654058 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | TM8V100C16MP12 | 41000 | 17 | 11.7 | 8.5 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
215821299 | 1.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | FE*G32*24+TXV |  | 22600 | 16 | 11 | 8.25 | 22400 | 16800 | 75% | 1.8 | 18000 | R-454B
211756118 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B36+TDR | YP9C120D20MP13 | 31600 | 17 | 9.3 | 8.1 | 32400 | 28200 | 87.04% | 2.57 | 25400 | R-410A
215654030 | 2.55 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E100B12SMPS1 | 30600 | 17.5 | 11.2 | 8.1 | 30200 | 24800 | 82.12% | 2 | 26600 | R-454B
215821306 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | FE*BB9*48+TXV |  | 44500 | 17 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
215667291 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *96CTN0601714B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2.02 | 19800 | R-454B
215667829 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0451712B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
211467574 | 3.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YZT48B21 | D(A,C,E)48D44+TDR | TM9Y080C16MP11 | 44000 | 16.2 | 12 | 8.4 | 47500 | 34200 | 72% | 3.02 | 33200 | R-410A
214279014 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | F,PE*G32930 |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
214279023 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V36H175P459+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
215669145 | 2.82 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0702120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.88 | 30200 | R-454B
215669345 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU0802120B* | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215669395 | 2.87 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1202422B* | 34400 | 18.5 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
216732358 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | CE3005C*+TXV |  | 23200 | 19 | 12.5 | 9.25 | 22400 | 17000 | 75.89% | 1.96 | 21400 | R-454B
216093472 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG36*36+TXV+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
213310740 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H142P429+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
213088361 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213088362 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213088363 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212868090 | 1.92 | Yes | No | GREE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | FLEXX36HP230V1AO | D(A,C,E)25B34+TDR |  | 23000 | 15.2 | 11 | 8.5 | 24000 | 21600 | 90% | 1.8 | 15000 | R-410A
215397418 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG36936+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 23600 | 72.39% | 1.9 | 27000 | R-410A
212380736 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P159 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380868 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG80936 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380870 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P149 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216093481 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG35*48+TXV+AEFE4B* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
212984479 | 2.58 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X37L21A* | *92MSN0801716A* | 31000 | 15.2 | 9 | 8.5 | 33400 | 26200 | 78.44% | 1.86 | 23200 | R-410A
212984978 | 2.55 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X37L21A* | *92MSN0802120A* | 30600 | 15.2 | 9 | 8.1 | 33200 | 27600 | 83.13% | 1.8 | 23400 | R-410A
216687176 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF97MV510021DH | 22800 | 20 | 12 | 10 | 22800 | 18400 | 80.7% | 1.8 | 21200 | R-454B
212380732 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P459 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380749 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG8J936 | BGH96M080B3B | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380864 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P149 | BGH96M080B3A | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380729 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P149 | BGH96M060B3A | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213281572 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Y81E100C20LMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213927831 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.49 | 25200 | R-410A
213927829 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9E100C20MP12 | 32800 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.5 | 25000 | R-410A
214091946 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TL8E100C20UH11 | 31600 | 17.5 | 9.8 | 8.5 | 33800 | 27400 | 81.07% | 2.68 | 25400 | R-410A
214091982 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8V080B12MP12 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29000 | 86.31% | 2.59 | 26200 | R-410A
214092015 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9E040A10MP12 | 32200 | 17 | 9 | 8.1 | 33400 | 28000 | 83.83% | 2.53 | 25600 | R-410A
214092031 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9E100C16MP12 | 32800 | 18 | 10 | 8.1 | 33600 | 27200 | 80.95% | 2.65 | 25200 | R-410A
214092045 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9V080C16MP12 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
214588230 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PL36H175P159 | 926TC36060V14*** | 17400 | 16 | 11 | 8.1 | 16400 | 18300 | 111.6% | 2.24 | 11200 | R-410A
214588231 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L159 | 926TC36060V14*** | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
214588232 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | V,C36H***P219 | 926TC36060V14*** | 17500 | 16 | 10.5 | 8.5 | 16900 | 18800 | 111.2% | 2.3 | 11400 | R-410A
213205694 | 2.87 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96VTN1202422A* | 34400 | 16 | 9.9 | 8.5 | 38500 | 31400 | 81.56% | 2.74 | 29000 | R-410A
216776731 | 2.85 | Yes | Yes | KENMORE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | (C,H,T)5H3V36*K*AAA* | H,GG8J*36+TXV | *97CMN0802120B* | 34200 | 21 | 12 | 8.5 | 36400 | 28200 | 77.47% | 2.02 | 31800 | R-454B
215667861 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0902120B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
216093484 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG35*48+TXV+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
216093486 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | FE*TT4*60+TXV |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-454B
213367717 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YP9C100C16MP13 | 29800 | 16.9 | 9.5 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
215654031 | 2.6 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E100C16SMPS1 | 31200 | 17.5 | 11.2 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
213307060 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H142P429+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
212380856 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG80936 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380874 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG80936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215654027 | 2.53 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E080B12SMPS1 | 30400 | 17.5 | 11.2 | 8.1 | 29800 | 24800 | 83.22% | 2 | 26400 | R-454B
214279018 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | V36H175P459+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214571154 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X42L21**+WALLCON | *80CTL0702120B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
215654042 | 2.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E100C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31400 | 25200 | 80.25% | 2 | 27600 | R-454B
212985912 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *96MSN0261410A* | 17800 | 16.5 | 10.5 | 8.1 | 17700 | 18800 | 106.2% | 2.26 | 12200 | R-410A
214574024 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *96CTN0802120B* | 32400 | 17.5 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 2 | 31400 | R-410A
214574044 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X60L24A*+WALLCON | *95CSU0802120B* | 32800 | 17.5 | 11.5 | 8.5 | 31600 | 24800 | 78.48% | 1.98 | 31000 | R-410A
212380867 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P459 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380748 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P159 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213894998 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,YG34936 | BGH96M080B3A | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213145612 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | PL36H175P459+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212380730 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P159 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216735432 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CAA**3721AM* | 83*CA60080C21*** | 24000 | 16 | 11 | 8.5 | 21200 | 18700 | 88.21% | 1.98 | 17800 | R-454B
216736686 | 1.87 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CSAH*2412AM* | 926SB48060V17*** | 22400 | 15.2 | 10.5 | 8.1 | 21200 | 19100 | 90.09% | 1.85 | 17900 | R-454B
216737069 | 1.87 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CSAH*3012AM* | 8(0,1)*SB42090M17*** | 22400 | 15.5 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.9 | 17600 | R-454B
214092046 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TM9V080C16MP12 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
214092063 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM9Y080C16MP11 | 32400 | 18.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.65 | 25800 | R-410A
214092112 | 2.73 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TP9C080C16MP13 | 32800 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
214092113 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TP9C100C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
214092115 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | TP9C100C16MP13 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
216761999 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HE48*60+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
216760242 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,GE35*48+TXV+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
216760243 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,GE35*48+TXV+AEFE4B* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
216762915 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG48*60+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
212380741 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P149 | BGH96M080B3A | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215654026 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215654044 | 2.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E120C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
211756119 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A46+TDR | YPLC060A12MP13 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.5 | 25600 | R-410A
215675864 | 3.96 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAMA6024XMA*+UI | 88*TB60070C21*** | 47500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215675914 | 4 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAMA6024XMA*+UI | 935CB66100C21*** | 48000 | 19 | 10 | 9 | 50000 | 36400 | 72.8% | 2.02 | 46000 | R-454B
215675744 | 4 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAMA6021XMA*+UI | 88*TB60110C21*** | 48000 | 19 | 10.5 | 9 | 50000 | 36600 | 73.2% | 2 | 46500 | R-454B
215675764 | 4 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAMA6021XMA*+UI | 935CB60080C21*** | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215676064 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAMA6124XMA*+UI | 987MC66120C24*** | 48500 | 19.5 | 10.5 | 9.5 | 50000 | 36800 | 73.6% | 2.12 | 46500 | R-454B
213145609 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | PL36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
212361448 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE32936 | BGH96M080B3A | 23000 | 18 | 11.5 | 8.8 | 22400 | 17000 | 75.89% | 1.86 | 19000 | R-410A
212361566 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HE33(1,2)36+TXV | BGH96M080B3A | 23400 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.9 | 18400 | R-410A
216737119 | 1.88 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 37MUHAQ24AA3 | CSAH*3012AM* | 8(0,1)*SB60110M24*** | 22600 | 15.5 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.85 | 17700 | R-454B
212380747 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H175P149 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213769872 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG33936+AEFE3A* |  | 23400 | 19 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
214569397 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | CAP**4821AL*+UI | 88*TB60070C21*** | 43500 | 20.5 | 11 | 9.5 | 46500 | 36600 | 78.71% | 2.26 | 43500 | R-410A
214569429 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | CAP**6024AL*+UI | 987MC60080C21*** | 44500 | 21 | 11.5 | 10 | 46000 | 36400 | 79.13% | 2.34 | 43500 | R-410A
214569481 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV048*0**B* | CNPV*4821AL*+UI | 88*TB60070C21*** | 43500 | 21 | 11.5 | 9 | 46500 | 36600 | 78.71% | 2.16 | 44000 | R-410A
213350123 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E080B12SMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.68 | 26200 | R-410A
213350140 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E080C20SMPS1 | 32000 | 18 | 9.9 | 8.5 | 33400 | 28400 | 85.03% | 2.71 | 25800 | R-410A
213350172 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E120C16SMPS1 | 33600 | 18 | 9.5 | 8.3 | 32800 | 30000 | 91.46% | 2.76 | 26600 | R-410A
213350189 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y82E080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.2 | 32800 | 29800 | 90.85% | 2.79 | 26400 | R-410A
213350190 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y82E100C16LMPS1 | 32000 | 18 | 9.4 | 8.5 | 33400 | 28000 | 83.83% | 2.7 | 25600 | R-410A
215667237 | 1.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *97CMN0601714B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
213367719 | 2.45 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YP9C120D20MP13 | 29400 | 16.3 | 9 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
215397415 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG32924+AEFE4B* |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
215397416 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG32924+AEFE3A* |  | 23000 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
215654034 | 2.6 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E120C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
215654037 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
215667789 | 1.95 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *96CTN0401410B* | 23400 | 16 | 9.5 | 9 | 24000 | 16900 | 70.42% | 1.98 | 20200 | R-454B
215654018 | 1.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH24B3J+TDR | Y81E100B12SMPS1 | 20400 | 18.6 | 11.2 | 9 | 22400 | 18000 | 80.36% | 2 | 18200 | R-454B
215654021 | 1.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH36A3J+TDR | Y81E060A12SMPS1 | 21000 | 17.5 | 11.7 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215413743 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | V36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213205459 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *96VTN1002122A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.63 | 23400 | R-410A
216796395 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | *UHMC100CCV4 | 31800 | 15.5 | 12 | 8.5 | 31200 | 22200 | 71.15% | 3.01 | 21600 | R-454B
215676164 | 3.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAVA4821XMA*+UI | 986TD66100C21*** | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215675964 | 4.04 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CVAMA6124XMA*+UI | 83*CA60100C21*** | 48500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
213774401 | 2.02 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EHD4X42AAL+WALLCON | *80CTL0701412B* | 24200 | 16 | 10.5 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
213821578 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0901714A* | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
213821633 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *92MSN1202420A* | 35400 | 16 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.7 | 29200 | R-410A
213821644 | 2.85 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96MSN1002120A* | 34200 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.75 | 29000 | R-410A
215654025 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
213821544 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30B34+TDR | *96VTN1002120B* | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
215674077 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0601716B* | 44000 | 17 | 9 | 9 | 49000 | 34600 | 70.61% | 2.04 | 43000 | R-454B
215674247 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
211755757 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TM8E060A12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.51 | 25400 | R-410A
215654041 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E100B12SMPS1 | 31000 | 18 | 11.2 | 8.1 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
212380897 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG84960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380902 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P199 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381036 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M100D5B | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212381038 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M120D5A | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212381052 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960 | BGH96M100C5A | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212381086 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG2K948 | BGH96M100C5A | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
215674377 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL1102120B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215674397 | 3.83 | No | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU1002122B* | 46000 | 18 | 10 | 9 | 48000 | 33600 | 70% | 2.08 | 42000 | R-454B
212380873 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P459 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214056986 | 4.5 | Yes | No | GREE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FLEXX60HP230V1AO | L(E,G)M60D4 |  | 54000 | 15.8 | 10.3 | 9 | 54000 | 41000 | 75.93% | 1.8 | 36000 | R-410A
215472295 | 1.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X24A1 | D(A,C,E)36A34+TDR | S9V2B060U4PSB+RP | 21800 | 17.8 | 12.2 | 8.1 | 20800 | 16800 | 80.77% | 2.41 | 19000 | R-410A
215472297 | 1.87 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X24A1 | D(A,C,E)36C34+TDR | S9V2B060U4PSB+RP | 22400 | 18 | 12.4 | 8.2 | 20800 | 16900 | 81.25% | 2.51 | 19200 | R-410A
213916462 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,YG84960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212988743 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *95MSU0401712A* | 23600 | 16.5 | 10 | 8.1 | 26400 | 24200 | 91.67% | 2.02 | 19200 | R-410A
213307131 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V48H175P469+AEFE4B* |  | 46500 | 18 | 11.7 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
213147358 | 2.52 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | V,C36H***P219+AEFE3A* |  | 30200 | 15.2 | 9 | 8.4 | 33400 | 27000 | 80.84% | 1.8 | 22600 | R-410A
213088746 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
214588274 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P149 | 926TC36040V17*** | 23200 | 16 | 10 | 8.5 | 24800 | 24800 | 100% | 2.08 | 18200 | R-410A
216951562 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | *UHMB080CCV3 | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
216951571 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8V2B060M4PDB | 31800 | 16 | 12 | 8.1 | 28400 | 20600 | 72.54% | 2.91 | 20000 | R-454B
216951578 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8V2C080M5PCA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
216951594 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8X1C080M5PTC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
214377807 | 3.88 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH4860ZGDA* | AE(D,N,U)+CM48C44+TDR |  | 46500 | 17 | 11 | 8.5 | 48000 | 39000 | 81.25% | 1.8 | 31400 | R-410A
216732356 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | CE2403C*+TXV |  | 22800 | 19 | 12 | 9.15 | 22200 | 17000 | 76.58% | 1.94 | 21400 | R-454B
214332162 | 2.73 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | AUH2436ZGDA* | L(E,G)M36B4 |  | 32800 | 16 | 10 | 8.9 | 35000 | 28000 | 80% | 1.8 | 24000 | R-410A
213613893 | 1.93 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | *E9J936 |  | 23200 | 15.2 | 12 | 9 | 22400 | 16500 | 73.66% | 1.88 | 18400 | R-410A
213088389 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213088390 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216951584 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8V2C100M5PCB | 32200 | 16.5 | 12 | 8.1 | 29000 | 21000 | 72.41% | 2.95 | 20400 | R-454B
216951585 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8V2C100M5PDA | 32000 | 16 | 12 | 8.1 | 28800 | 20400 | 70.83% | 2.9 | 20000 | R-454B
215669695 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0802120B* | 34800 | 18 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215670063 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *97CMN0802120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215039706 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ML17XP1-048-230A** | CH60B34+TDR | ML196UH110XE60C* | 45000 | 15.5 | 12.4 | 8.1 | 44500 | 31600 | 71.01% | 2.75 | 30800 | R-410A
215654067 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | Y81E130D20SMPS1 | 41500 | 17.5 | 11.7 | 8.5 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
216951603 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8X2B080M4PSC | 31800 | 16 | 12 | 8.1 | 28600 | 20800 | 72.73% | 2.94 | 20200 | R-454B
216951605 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8X2C080M5PSC | 32200 | 16.5 | 12 | 8.1 | 29000 | 20400 | 70.34% | 2.93 | 20000 | R-454B
216951612 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S9V2B040D3PSC | 31400 | 16 | 11.7 | 8.1 | 29200 | 21000 | 71.92% | 2.79 | 20400 | R-454B
216951628 | 2.62 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S9V2B080D4VSB | 31400 | 16 | 11.7 | 8.1 | 29000 | 20600 | 71.03% | 2.8 | 20200 | R-454B
216951653 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S9X2B040U3PSB | 31800 | 16 | 12 | 8.1 | 28800 | 20800 | 72.22% | 2.94 | 20200 | R-454B
212927486 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | CE2505C+TXV |  | 23200 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
216732351 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | CE3005A*+TXV |  | 23200 | 17 | 11 | 8.3 | 22400 | 16800 | 75% | 1.8 | 18000 | R-454B
212381040 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M120D5B | 45500 | 17 | 11.7 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212381093 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG2K948 | BGH96M080C4B | 42000 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
206135684 | 2.65 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L21A*+WALLCON | *80CSU0601716A* | 31800 | 17 | 11 | 8.1 | 33200 | 24400 | 73.49% | 1.86 | 31200 | R-410A
214279017 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | V36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213612172 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,TG33936+AEFE3A* |  | 23400 | 19 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
213894999 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,YG8J936 | BGH96M080B3A | 23600 | 18 | 11.7 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214572944 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X60L24A*+WALLCON | *96CTN0802120B* | 32800 | 18 | 11.5 | 8.5 | 31600 | 24600 | 77.85% | 2 | 31000 | R-410A
212986630 | 1.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *96MSN0401712A* | 23200 | 15.5 | 10 | 8.1 | 26000 | 24400 | 93.85% | 2.02 | 19100 | R-410A
212380711 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P179 | BGH96M100C5A | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212380754 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG50960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
214269146 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84960 | BGH96M100D5A | 51500 | 18 | 11.7 | 8.5 | 52000 | 37400 | 71.92% | 1.85 | 37400 | R-410A
212924878 | 3.92 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | C(A,C,D,E)48D44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
216732353 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | PL36H175P15*+TXV+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
215670379 | 2.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *80CSU0401712A* | 34600 | 17 | 9.5 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
213769871 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG33936+AEFE4B* |  | 23400 | 20 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
212381034 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M100D5A | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
213088391 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
214269152 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84960 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
214572584 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X37L21A*+WALLCON | *96CTN0802120B* | 33000 | 17.5 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 2 | 31600 | R-410A
213613892 | 1.93 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | *G9J936 |  | 23200 | 15.2 | 12 | 9 | 22400 | 16500 | 73.66% | 1.88 | 18400 | R-410A
214440917 | 2.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | BV**B9937 |  | 34000 | 19 | 12 | 9.4 | 32600 | 23600 | 72.39% | 1.88 | 27000 | R-410A
213088739 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
213253171 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
215940955 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CAA**4821AM*+UI | 83*CB48060C17*** | 43500 | 21 | 11 | 9.5 | 48000 | 36600 | 76.25% | 1.9 | 39500 | R-454B
214569649 | 2.85 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CSPH*4812AL*+UI | 935CB66100C21*** | 34200 | 19 | 12 | 9 | 36400 | 25800 | 70.88% | 2.06 | 31000 | R-410A
212380901 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG50960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381031 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M080C4B | 42000 | 17 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
215397419 | 2.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | HG36936+AEFE3A* |  | 34000 | 18 | 12 | 9.5 | 32600 | 23600 | 72.39% | 1.9 | 27000 | R-410A
213612270 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,TG33936+AEFE4B* |  | 23400 | 20 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
215940355 | 2.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAMA4921XMA*+UI | 987TA42060C17*** | 35200 | 21 | 11.7 | 8.5 | 38500 | 29400 | 76.36% | 2.02 | 33800 | R-454B
215940855 | 2.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAVA6021XMA*+UI | 987TA60080C21*** | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
216736348 | 1.88 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80MSU0601716A* | 22600 | 16 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.85 | 17800 | R-454B
216734433 | 1.88 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80VSL0701412B* | 22600 | 16.5 | 11 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
213307059 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H142P429+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
212924880 | 4.21 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | C(A,C,D,E)60A44+TDR |  | 50500 | 15.2 | 9.5 | 8.5 | 53000 | 37200 | 70.19% | 1.8 | 35200 | R-410A
213356195 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | A48VGA+TXV+AEFE5* |  | 46000 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
216732355 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | CE2903C*+TXV |  | 22800 | 19 | 12 | 9.15 | 22200 | 17000 | 76.58% | 1.94 | 21400 | R-454B
215413741 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | A36VDA+TXV+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216768267 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*BB9*31+TXV |  | 24000 | 20 | 13 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
213307135 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V48H175P389+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
216762051 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HE8J*36+TXV+AEFE3A* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
216760238 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V,G60H210P16*+TXV+AEFE5* |  | 44500 | 16 | 11 | 8.2 | 45000 | 33200 | 73.78% | 1.82 | 37000 | R-454B
216760247 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,GE8J*36+TXV+AEFE4B* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
212380688 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P179 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380709 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P179 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381095 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG2K948 | BGH96M100C5B | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213088742 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG2K948+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213253156 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84948+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
213356128 | 1.48 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | A24VBA+TXV+CBPE3A* |  | 17800 | 15.5 | 10.5 | 9 | 17100 | 19400 | 113.5% | 2.4 | 11500 | R-410A
213310739 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V,R36H142P429+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
213252931 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG32924+AEFE3A* |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
215941333 | 3.79 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V48*K*AAA* | EVM5X49M21A*+WALLCON | *96CTN0802120B* | 45500 | 20.5 | 11 | 8.1 | 53000 | 38500 | 72.64% | 1.95 | 43500 | R-454B
216760249 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | H,RG33*36+TXV+AEFE4B* |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17000 | 75.89% | 1.98 | 21400 | R-454B
213088741 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R48H175P469+AEFE4B* |  | 46500 | 18 | 11.7 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
213307136 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V48H175P469+AEFE4B* |  | 46500 | 18 | 11.7 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
212380691 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL60H210P179 | BGH96M100C5B | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213088729 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG2K948+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213088730 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960+AEFE5* |  | 45500 | 18 | 11.7 | 9.25 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
213088731 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG50960+AEFE5* |  | 47000 | 18 | 12 | 9.45 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213088747 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG84960+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
214862791 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG7J(1,2)36+TXV | BGH96M060B3B | 23200 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.88 | 19000 | R-410A
213088749 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG86960+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
214092132 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TPLC100C16MP13 | 32400 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214092147 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | Y81E080B12SMPS1 | 33000 | 18 | 9.5 | 8.2 | 32800 | 29400 | 89.63% | 2.71 | 26200 | R-410A
214862792 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG7J(1,2)36+TXV | BGH96M080B3B | 23200 | 18 | 11.7 | 8.95 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216762918 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG48*60+TXV+AEFE5* |  | 45500 | 17 | 11.5 | 8.35 | 45000 | 33200 | 73.78% | 1.84 | 37000 | R-454B
215931654 | 4.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA360A*030* | CAA**6121AM*+UI | 58TN*B070C17**16 | 56000 | 18 | 11 | 8.5 | 61000 | 45500 | 74.59% | 2.1 | 46500 | R-454B
214092162 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E100C16SMPS1 | 32400 | 18 | 9.5 | 8.5 | 33400 | 28400 | 85.03% | 2.7 | 25800 | R-410A
216737114 | 1.9 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MS(N,L)1102120A* | 22800 | 15.2 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.9 | 17800 | R-454B
213821572 | 2.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0701716A* | 35000 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213821573 | 2.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80MS(N,L)0701716A* | 35000 | 16.5 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213821574 | 2.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0702116A* | 34800 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.6 | 29400 | R-410A
213821623 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *92MSN0802120A* | 35000 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
213253160 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
213253162 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG88960+AEFE5* |  | 51500 | 17 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213253167 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84948+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
213769867 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG33936+AEFE4B* |  | 23400 | 20 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
215869162 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG33936+AEFE4B* |  | 23400 | 20 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
215674237 | 3.75 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0602120B* | 45000 | 17.5 | 9.5 | 9 | 47500 | 34000 | 71.58% | 2.06 | 42000 | R-454B
213307139 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG3K960+AEFE5* |  | 45500 | 18 | 11.7 | 9.25 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
213088724 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213088738 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213088740 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R48H175P389+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
216762044 | 2.77 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG33*36+TXV+AEFE3A* |  | 33200 | 16 | 11 | 8.25 | 32400 | 33800 | 104.3% | 1.76 | 33200 | R-454B
216760245 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,GE35*48+TXV+AEFE5* |  | 44000 | 16 | 11 | 8.1 | 44500 | 33200 | 74.61% | 1.8 | 36800 | R-454B
216762919 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HE8J*36+TXV+AEFE4B* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
215940905 | 2.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAVA6024XMA*+UI | 987TA66120C24*** | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215942391 | 2.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAMA4921XMA*+UI | 986TD42060C17*** | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2.06 | 32000 | R-454B
215942461 | 2.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAVA6021XMA*+UI | 986TD42060C17*** | 35200 | 21 | 11.7 | 8.5 | 37400 | 28000 | 74.87% | 2 | 32000 | R-454B
216705986 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*G33*25+TXV |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17000 | 75.89% | 1.98 | 21400 | R-454B
213821196 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)24B44+TDR | *80MS(N,L)0702116A* | 23600 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213821198 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80MS(N,L)0702116A* | 23800 | 17.5 | 10 | 8.5 | 26400 | 20200 | 76.52% | 2.92 | 19100 | R-410A
213927974 | 3.38 | Yes | No | WESTINGHOUSE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | WHM48SZA21S | D(A,C,E)61B44+TDR |  | 40500 | 15.55 | 11.4 | 8.55 | 42000 | 34600 | 82.38% | 1.94 | 31200 | R-410A
212361473 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M100C5B | 44000 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212361482 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M100D5B | 45000 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
212361491 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE37960 | BGH96M120D5B | 45000 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361584 | 3.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M080C4B | 41000 | 16 | 11 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 33400 | R-410A
212361593 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M100D5B | 45500 | 17 | 11.7 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34000 | R-410A
215670229 | 2.85 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CTL1352422B* | 34200 | 17 | 9.5 | 8.5 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215670279 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0602120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
213613894 | 1.93 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | *G34936 |  | 23200 | 15.2 | 12 | 9 | 22400 | 16500 | 73.66% | 1.88 | 18400 | R-410A
216760234 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V,G60H210P16*+TXV+AEFE5* |  | 46500 | 18 | 11.5 | 9.65 | 46500 | 48000 | 103.2% | 2.04 | 47500 | R-454B
216762039 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG33*36+TXV+AEFE4B* |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17000 | 75.89% | 1.98 | 21400 | R-454B
214092197 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | YP9C100C16MP13 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
216732366 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | PL60H210P16*+TXV+AEFE5* |  | 46500 | 18 | 11.5 | 9.65 | 46500 | 48000 | 103.2% | 2.04 | 47500 | R-454B
216788568 | 4.04 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,RG84*48+TXV+AEFE5* |  | 48500 | 19 | 12 | 10 | 46500 | 48000 | 103.2% | 2.1 | 47500 | R-454B
213258896 | 2.9 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36D36+JMET12BS2N1+TDR |  | 34800 | 18 | 9 | 8.1 | 36000 | 26000 | 72.22% | 2.8 | 25200 | R-410A
210693348 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC801005C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214092212 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | YPLC080C16MP13 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214092831 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | Y81E040A12SMPS1 | 33200 | 18 | 10 | 8.2 | 32800 | 29800 | 90.85% | 2.73 | 26400 | R-410A
213307138 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG2K948+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
214394752 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R962V0705A21M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
213612289 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,T60H210P169+AEFE5* |  | 45000 | 18 | 11.5 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-410A
210693324 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC800804C*A* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214394796 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U98MV1155A24UPS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
216762897 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | A48VGC*+TXV+AEFE5* |  | 47500 | 18 | 11.7 | 9.85 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
216762920 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V60H210P16*+TXV+AEFE5* |  | 46500 | 18 | 11.5 | 9.65 | 46500 | 48000 | 103.2% | 2.04 | 47500 | R-454B
214092898 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | YP9C080B12MP13 | 32800 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.66 | 26400 | R-410A
214092914 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | YPLC100C16MP13 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214092916 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | YPLC100C20MP13 | 32000 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214091962 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8E060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
214091964 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E080B12MP11 | 31600 | 17.9 | 9.3 | 8.1 | 34000 | 28000 | 82.35% | 2.62 | 25800 | R-410A
214092732 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8Y080B12MP11 | 32600 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
213296198 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8E080C16MP11 | 31400 | 18 | 9.9 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
214092784 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE060A12MP11 | 32600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.63 | 25400 | R-410A
213821624 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *92MSN0802120A* | 35000 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.55 | 29400 | R-410A
216737144 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80MS(N,L)1552420A* | 22400 | 15.2 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.9 | 17700 | R-454B
216737161 | 1.88 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80VSL0701412B* | 22600 | 16 | 10.5 | 8.1 | 21000 | 18800 | 89.52% | 1.85 | 17700 | R-454B
214269147 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84960 | BGH96M120D5A | 51500 | 18 | 11.7 | 8.5 | 52000 | 37400 | 71.92% | 1.85 | 37400 | R-410A
213253166 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213088726 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R48H175P389+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213088744 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG3K960+AEFE5* |  | 45500 | 18 | 11.7 | 9.25 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
216732370 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | PL36H175P14*+TXV+AEFE4B* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
216762043 | 2.77 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG33*36+TXV+AEFE4B* |  | 33200 | 16 | 11 | 8.25 | 32400 | 33800 | 104.3% | 1.76 | 33200 | R-454B
213307132 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG2K948+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
216762022 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HE48*60+TXV+AEFE5* |  | 45500 | 17 | 11.5 | 8.35 | 45000 | 33200 | 73.78% | 1.84 | 37000 | R-454B
215654051 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | Y81E080C20SMPS1 | 41000 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32200 | R-454B
216624563 | 2 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H24HA5*** | FE*G34*30+TXV |  | 24000 | 18 | 11.7 | 9.95 | 22400 | 22600 | 100.9% | 1.8 | 17000 | R-454B
216736788 | 1.87 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *96CTN0601714B* | 22400 | 15.5 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.85 | 17800 | R-454B
214391676 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R921V0703A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.88 | 15900 | R-410A
216772268 | 4 | Yes | No | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H60HA5*** | FC*CC4*60+TXV+TD |  | 48000 | 15.2 | 10 | 8.5 | 45500 | 39000 | 85.71% | 1.85 | 39000 | R-454B
214392761 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R801V0504A17UHS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214392861 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R801V0754A17DZ | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
212986896 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L14A* | *96MSN0601412A* | 23400 | 16.5 | 10 | 8.5 | 26400 | 24200 | 91.67% | 2 | 19100 | R-410A
212989211 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L21A* | *95MSU0601716A* | 24200 | 17.5 | 10.5 | 8.5 | 25200 | 21600 | 85.71% | 1.82 | 18700 | R-410A
213088733 | 4.25 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG84960+AEFE5* |  | 51000 | 17 | 11.5 | 9.4 | 53000 | 38000 | 71.7% | 2 | 42500 | R-410A
213088728 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG2K948+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
214573244 | 2.72 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X48AAL+WALLCON | *96CTN0802120B* | 32600 | 17.5 | 11 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31600 | R-410A
214573294 | 2.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X60AAL+WALLCON | *97CMN0802120B* | 33000 | 17 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 2 | 31400 | R-410A
212927475 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CP3005A+TXV+TD |  | 22800 | 17 | 12 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213821570 | 2.82 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80MS(N,L)0701712A* | 33800 | 16.5 | 9.9 | 8.1 | 37800 | 31800 | 84.13% | 2.73 | 29000 | R-410A
212380746 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG82936 | BGH96M080B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212380855 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,R36H175P459 | BGH96M060B3A | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215654039 | 2.62 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E080C16SMPS1 | 31400 | 18 | 11.2 | 8.1 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
214279021 | 2.78 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | F,PE*G34936 |  | 33400 | 18 | 11.7 | 9.3 | 32600 | 23600 | 72.39% | 1.88 | 27000 | R-410A
213769868 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG33936+AEFE3A* |  | 23400 | 19 | 12.5 | 9.45 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
216687187 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80SV405017UHU | 22800 | 20 | 12 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
212924879 | 3.92 | No | No | GE Appliances | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | AUH4860ZGDA* | D(A,C,E)61C44+TDR |  | 47000 | 15.2 | 10 | 8.5 | 48000 | 33600 | 70% | 1.8 | 31200 | R-410A
216732352 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | PL36H175P14*+TXV+AEFE4B* |  | 23800 | 20 | 13 | 9.45 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
213612277 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG36960+AEFE5* |  | 45000 | 18 | 11.5 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-410A
213612279 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG2K948+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213088745 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG50960+AEFE5* |  | 47000 | 18 | 12 | 9.45 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213088734 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG84948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
215942619 | 3 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H3V36*K*AAA* | EVM5X61M24A*+WALLCON | *97CTN0802120A* | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
213612282 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG48948+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213612283 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG50960+AEFE5* |  | 47000 | 18 | 12 | 9.45 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213307130 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V48H175P389+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
215654059 | 3.54 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | TM8V100C20MP12 | 42500 | 18 | 11 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215654060 | 3.54 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | TM8V120C20MP12 | 42500 | 18 | 11 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215674467 | 3.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU1002120A* | 46000 | 18 | 9.5 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
216788585 | 4.58 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V,R60H210P19*+TXV+AEFE5* |  | 55000 | 16 | 10 | 8.4 | 54000 | 39000 | 72.22% | 1.85 | 38000 | R-454B
214394368 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | U97MV0603A17DHS | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394435 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | U97MV0855A21DHS | 33000 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
215654023 | 1.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH36A3J+TDR | Y81E100B12SMPS1 | 20800 | 18.9 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
215674027 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0701716B* | 44000 | 17.5 | 9.5 | 9 | 49000 | 34400 | 70.2% | 2.04 | 43000 | R-454B
215674127 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN1002122B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.04 | 42500 | R-454B
215670529 | 2.88 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0802120B* | 34600 | 17 | 10 | 8.5 | 34600 | 24800 | 71.68% | 1.8 | 30000 | R-454B
216762040 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG33*36+TXV+AEFE3A* |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17000 | 75.89% | 1.98 | 21400 | R-454B
216760250 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | H,RG33*36+TXV+AEFE3A* |  | 23400 | 20 | 12.5 | 9.35 | 22400 | 17000 | 75.89% | 1.98 | 21400 | R-454B
215588105 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6024AM*+UI | 59MN7C100C21**22 | 49000 | 19 | 11 | 10.5 | 52500 | 53500 | 101.9% | 1.96 | 50500 | R-454B
216760248 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,GE8J*36+TXV+AEFE3A* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
214243996 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CNPV*3017AL*+UI | 987MC42060C17*** | 22800 | 19 | 12.5 | 9.5 | 26800 | 20200 | 75.37% | 2.34 | 25200 | R-410A
212361436 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M100C5B | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212361437 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M100D5A | 45000 | 17 | 11.5 | 9 | 45000 | 32800 | 72.89% | 1.9 | 34600 | R-410A
213821595 | 2.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)1352420A* | 34800 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821602 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80VTL0451412B* | 35200 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.64 | 29400 | R-410A
215654022 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH36A3J+TDR | Y81E080B12SMPS1 | 22400 | 18 | 12 | 8.5 | 22600 | 18500 | 81.86% | 2 | 18400 | R-454B
215674287 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *96CTN1202422B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 41500 | R-454B
212380710 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | PL60H210P179 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380753 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P179 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380760 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG50960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380762 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG84960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381030 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG3K960 | BGH96M080C4A | 42000 | 17 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213350114 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y81E040A12SMPS1 | 33200 | 18 | 10 | 8.2 | 32800 | 29800 | 90.85% | 2.72 | 26400 | R-410A
213350115 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E040A12SMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.71 | 26400 | R-410A
213350147 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E100B12SMPS1 | 31600 | 18.4 | 9.3 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
213350196 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y82E100C20LMPS1 | 32000 | 18.5 | 9.4 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213307345 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM8E100B12MP11 | 31400 | 17.8 | 9.8 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
216687198 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF96TV508521M4 | 34200 | 19 | 12 | 10 | 34200 | 29400 | 85.96% | 2 | 30000 | R-454B
216732354 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | PL36H***P44*+TXV+AEFE3A* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
215674297 | 3.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716A* | 46000 | 18 | 9.5 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
216732372 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | PL60H210P16*+TXV+AEFE5* |  | 44500 | 16 | 11 | 8.2 | 45000 | 33200 | 73.78% | 1.82 | 37000 | R-454B
212381087 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG2K948 | BGH96M100C5B | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
213253154 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213252934 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG32924+AEFE3A* |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
216734606 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *92MSN0601714A* | 22400 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.9 | 17600 | R-454B
216734671 | 1.85 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *96MSN0601716A* | 22200 | 15.5 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216734840 | 1.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *97VTN0601716A* | 22400 | 16 | 10.5 | 8.5 | 20800 | 18700 | 89.9% | 1.96 | 17600 | R-454B
216735222 | 1.88 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VSN0401410B* | 22600 | 15.5 | 10.5 | 8.1 | 20800 | 18500 | 88.94% | 1.85 | 17600 | R-454B
212380756 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG84960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212380758 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG88960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212381092 | 3.5 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG2K948 | BGH96M080C4A | 42000 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213253164 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
216788566 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V,R48H175P38*+TXV+AEFE4B* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
216788589 | 2.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | H,RG36*36+TXV+AEFE3A* |  | 34000 | 18 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
216687188 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF80TV510021UH | 34200 | 20 | 12 | 10 | 34200 | 29200 | 85.38% | 2 | 30000 | R-454B
213281363 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H***P449+AEFE3A* |  | 23800 | 19 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
210693380 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+MBVC1601**-1A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214396125 | 2.9 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36C5CDS1 | TMLE080C20MP11 | 34800 | 17 | 11 | 8.5 | 32800 | 27000 | 82.32% | 2 | 29400 | R-454B
214396127 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TMLE080C16MP11 | 33400 | 19 | 11 | 9 | 31400 | 25400 | 80.89% | 2 | 26000 | R-454B
215674197 | 3.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1102120B* | 45000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
215674506 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1352422B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
215674597 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1002122B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
214588216 | 1.41 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | C36A***L129 | 926TC36040V17*** | 16900 | 16 | 10 | 8.5 | 16600 | 19000 | 114.5% | 2.34 | 11300 | R-410A
213088736 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG88960+AEFE5* |  | 51500 | 17 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213088743 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG2K948+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
215821308 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | FE*BB9*48+TXV |  | 46000 | 17 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
216760239 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,GE35*48+TXV+AEFE5* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
216494135 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)4824G1K*+TXV | 987MC60060C21*** | 44000 | 17 | 9.5 | 9 | 47000 | 34200 | 72.77% | 2.04 | 42000 | R-454B
215654047 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | TM8V100C16MP12 | 41000 | 17 | 11.5 | 8.5 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
214609889 | 2.82 | Yes | No | CARRIER | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 38MURAQ36AB3 | D(A,C,E)42D24+TDR |  | 33800 | 15.2 | 10 | 8.6 | 38500 | 31600 | 82.08% | 1.85 | 27400 | R-410A
214569697 | 2.85 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV036*0**B* | CNPV*6024AL*+UI | 88*TB60070C21*** | 34200 | 20 | 12.5 | 9 | 36200 | 25600 | 70.72% | 2.02 | 30600 | R-410A
216093490 | 2.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HG36*36+TXV+AEFE3A* |  | 34000 | 16 | 11.7 | 8.5 | 32600 | 33800 | 103.7% | 1.8 | 33200 | R-454B
216612229 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | 5PX*B004AS3 | S9V2B060D3PSC+LRP | 32200 | 17.6 | 11.2 | 9.7 | 31200 | 24400 | 78.21% | 2 | 30600 | R-454B
214394451 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | U97MV0855A21DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
214394452 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | U97MV0855A21DHS | 33800 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
214396020 | 2.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM36C5CDS1 | TM8E080C20MP11 | 34400 | 17 | 11 | 8.5 | 32400 | 26400 | 81.48% | 2 | 28600 | R-454B
214395619 | 2.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TMLE080C20MP11 | 34600 | 18 | 11 | 8.5 | 32800 | 25800 | 78.66% | 2 | 26400 | R-454B
216763682 | 2.7 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C005AS3 |  | 32400 | 15.2 | 11 | 8.7 | 33200 | 24800 | 74.7% | 2.1 | 22000 | R-454B
216763871 | 2.77 | Yes | Yes | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB006AS3 |  | 33200 | 16 | 11.5 | 8.7 | 33000 | 24600 | 74.55% | 2.1 | 21800 | R-454B
212380898 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG86960 | BGH96M080C4A | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
213612174 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,T36H175P139+AEFE4B* |  | 23600 | 20 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213612173 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V,T36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213253158 | 4.25 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84960+AEFE5* |  | 51000 | 17 | 11.5 | 9.4 | 53000 | 38000 | 71.7% | 2 | 42500 | R-410A
213612280 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG2K948+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
213612284 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,T60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213281156 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H175P159+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213281360 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | V36H***P429+AEFE3A* |  | 23200 | 19 | 12.5 | 9.35 | 22400 | 17200 | 76.79% | 1.98 | 21400 | R-410A
215402574 | 2.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | BV**B9737 |  | 34000 | 19 | 12 | 9.4 | 32600 | 23600 | 72.39% | 1.88 | 27000 | R-410A
213145626 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | PL36H175P459+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
211799913 | 1.95 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG37936+TD |  | 23400 | 15.2 | 12 | 9 | 22400 | 15900 | 70.98% | 1.82 | 17800 | R-410A
212927492 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CE2903C+TXV |  | 22800 | 19 | 12 | 9.2 | 22200 | 17200 | 77.48% | 1.94 | 21400 | R-410A
212927494 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CE3005A+TXV |  | 23200 | 19 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
213821592 | 2.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)1102420A* | 35000 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
215588121 | 4.08 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CAA**6121AM*+UI | 59MN7C080C17**14 | 49000 | 18 | 11.5 | 9.5 | 52000 | 51000 | 98.08% | 1.98 | 50000 | R-454B
215588139 | 3.96 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CSAH*4812AM*+UI | 59CU5B060C17**16 | 47500 | 17 | 11 | 12.5 | 51500 | 50500 | 98.06% | 1.94 | 49500 | R-454B
213281151 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | PL36H***P219+AEFE3A* |  | 23600 | 19 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216558398 | 2.88 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*L+CM48C36+TDR |  | 34600 | 18 | 9 | 8.5 | 35000 | 25200 | 72% | 2.81 | 24000 | R-410A
214391693 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R962V0703A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.88 | 15900 | R-410A
214393816 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V0603A17M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393948 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R951V1005A21M4S | 33200 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216494183 | 3.92 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | CE(P,V)4824G1K*+TXV | 986TD42080C17*** | 47000 | 18 | 11.7 | 9 | 48500 | 49500 | 102.1% | 1.96 | 48000 | R-454B
216788587 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG84*48+TXV+AEFE4B* |  | 46000 | 17 | 11.7 | 8.5 | 45000 | 33200 | 73.78% | 1.86 | 37000 | R-454B
216643941 | 1.54 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X19M17A* | *92MSN0801716A* | 18500 | 15.2 | 11.5 | 10.5 | 20000 | 17800 | 89% | 2 | 14900 | R-454B
212983525 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L17A* | *92MSN0601412A* | 23600 | 16.5 | 10 | 9 | 27000 | 21600 | 80% | 1.8 | 18800 | R-410A
212986233 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *96MSN0401410A* | 23200 | 16 | 10 | 8.5 | 27000 | 25200 | 93.33% | 2.1 | 19500 | R-410A
216760259 | 2.77 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG33*36+TXV+AEFE4B* |  | 33200 | 16 | 11 | 8.25 | 32400 | 33800 | 104.3% | 1.76 | 33200 | R-454B
216760261 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG37*36+TXV+AEFE4B* |  | 44500 | 16 | 11 | 8.25 | 45000 | 33200 | 73.78% | 1.82 | 37000 | R-454B
212985249 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L24A* | *92MSN1002120A* | 35800 | 16.5 | 10 | 8.5 | 37800 | 34600 | 91.53% | 2.02 | 28800 | R-410A
210693355 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC961005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693360 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+MBVC1201**-1A*+TXV |  | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213281155 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H175P149+AEFE4B* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213771324 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X42L21A*+WALLCON | *97CMN0801714B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
213771354 | 1.97 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X42L21A*+WALLCON | *96CTN0801714B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
213367714 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YP9C060B12MP13 | 29800 | 16.9 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.63 | 25600 | R-410A
216624574 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | L*18/36V*+TXV+LEFE4B* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
216624576 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | L*18/36T*+TXV+LEFE4B* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
210693396 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VM970803BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215654038 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E080B12SMPS1 | 30800 | 18 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
215654015 | 1.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH24B3J+TDR | Y81E040A12SMPS1 | 20400 | 17.5 | 11.2 | 9 | 22400 | 18100 | 80.8% | 2 | 18200 | R-454B
213253173 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG88960+AEFE5* |  | 51500 | 17 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
216732373 | 2.82 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | PL36H***P44*+TXV+AEFE3A* |  | 33800 | 16 | 11.5 | 8.45 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
216762907 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HE35*48+TXV+AEFE5* |  | 44000 | 17 | 11 | 8.1 | 44500 | 33200 | 74.61% | 1.8 | 36800 | R-454B
216732357 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | CE3005A*+TXV |  | 23200 | 19 | 12.5 | 9.25 | 22400 | 17000 | 75.89% | 1.96 | 21400 | R-454B
213821594 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80MS(N,L)1102420A* | 35400 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213821603 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80VTL0451412B* | 35200 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.64 | 29400 | R-410A
213821610 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80VTL1102122B* | 34000 | 16.4 | 9.8 | 8.5 | 38000 | 31600 | 83.16% | 2.73 | 29000 | R-410A
213821651 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96MSN1202422A* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
214271897 | 2 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | PL36H175P159 | 58TN*B070C14**12 | 24000 | 17 | 10.5 | 8.1 | 19600 | 16200 | 82.65% | 2.02 | 19600 | R-410A
216624564 | 2 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H24HA5*** | FE*G34*25+TXV |  | 24000 | 18 | 11.7 | 9.95 | 22400 | 22600 | 100.9% | 1.8 | 17000 | R-454B
215654043 | 2.6 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E100C20SMPS1 | 31200 | 17.5 | 10.5 | 8.1 | 31600 | 25400 | 80.38% | 2 | 27600 | R-454B
213613465 | 1.5 | Yes | No | PAYNE HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M36D4 |  | 18000 | 15.2 | 10 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
212986305 | 1.45 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *96MSN0401410A* | 17400 | 16 | 10.5 | 8.5 | 18500 | 19500 | 105.4% | 2.34 | 12400 | R-410A
212986678 | 1.43 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *96MSN0401712A* | 17200 | 15.5 | 10 | 8.5 | 18300 | 17800 | 97.27% | 2.14 | 12100 | R-410A
216624582 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | LP18/37R*+TXV+LEFE3A* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
216624593 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | L*42/49K*+TXV+LEFE4B* |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
212361486 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M120D5A | 45000 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361489 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35948 | BGH96M120D5B | 44500 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
212361587 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE48(1,2)60+TXV | BGH96M100C5A | 45000 | 17 | 11.7 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34000 | R-410A
212367487 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG84948 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212367488 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG88960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212367505 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG84948 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
216794351 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | *UHMC100CCV4+LRP | 32600 | 20.5 | 12.5 | 9 | 32200 | 30800 | 95.65% | 2.76 | 37800 | R-454B
213367723 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | YPLC100C16MP13 | 29800 | 16.9 | 9.5 | 8.5 | 33800 | 27400 | 81.07% | 2.67 | 25400 | R-410A
216624567 | 3.96 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H60HA5*** | FE*TT4*60+TXV |  | 47500 | 18 | 11.7 | 9.5 | 46000 | 41500 | 90.22% | 1.75 | 38000 | R-454B
216768259 | 2 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H24HA5*** | FC*E33*25+TXV+TD |  | 24000 | 16 | 11.7 | 8.95 | 22400 | 22200 | 99.11% | 1.8 | 18600 | R-454B
215935284 | 2.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA6021XMA*+UI | 59MN7C080C21**20 | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
210693344 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC800604B*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693364 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC800804C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213821575 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0702116A* | 35000 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.6 | 29400 | R-410A
213821586 | 2.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0902420A* | 34800 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821593 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)1102420A* | 35400 | 17 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213821625 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *92MSN1002120A* | 35000 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
216760251 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | H,RG37*36+TXV+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
213088723 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R48H175P159+AEFE4B* |  | 44500 | 18 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213088737 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,R48H175P159+AEFE4B* |  | 44500 | 18 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
216762056 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V36H***D12*+TXV+AEFE3A* |  | 23000 | 19 | 12.5 | 9.2 | 22400 | 17000 | 75.89% | 1.96 | 21400 | R-454B
216788580 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V,R36H***P44*+TXV+AEFE3A* |  | 23800 | 20 | 13 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
215654053 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | Y81E100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216687215 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF98MV508521UP | 53500 | 17 | 10 | 10 | 53500 | 48500 | 90.65% | 2 | 51000 | R-454B
215674387 | 3.79 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0601716B* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34200 | 71.25% | 2.06 | 42500 | R-454B
214396385 | 2.82 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TM8Y080C16MP11 | 33800 | 19 | 11 | 9 | 31800 | 25400 | 79.87% | 2 | 26200 | R-454B
214396462 | 2.8 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36C5CDS1 | TM8Y120C20MP11 | 33600 | 18 | 11.7 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
214396512 | 2.88 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TM8Y120C20MP11 | 34600 | 19 | 11 | 9 | 32600 | 25800 | 79.14% | 2 | 26400 | R-454B
214396542 | 2.75 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TPLC100C16MP13 | 33000 | 19 | 11 | 9 | 31200 | 25200 | 80.77% | 2 | 25800 | R-454B
214396794 | 2.8 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM36C5CDS1 | TM8Y080C16MP11 | 33600 | 18 | 11 | 8.5 | 31400 | 25200 | 80.25% | 2 | 27200 | R-454B
214396935 | 2.77 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF48C5CFS1 | TM8E080C16MP11 | 33200 | 19 | 11 | 9 | 31200 | 25400 | 81.41% | 2 | 26000 | R-454B
215935354 | 2.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA336A*030* | CVAMA6024XMA*+UI | 58TN*B110C21**20 | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32800 | R-454B
215683603 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**2517AM*+UI | 58TN*B070C17**16 | 24000 | 17.5 | 10.5 | 9 | 23200 | 16400 | 70.69% | 2 | 19700 | R-454B
215683619 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3014AM*+UI | 59TN6C040C14**10 | 22600 | 15.5 | 9 | 8.5 | 24200 | 17100 | 70.66% | 1.84 | 20600 | R-454B
215683671 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3717AM*+UI | 58TN*B070C14**12 | 23800 | 17.5 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
214568836 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | H,PE7J936 | 59TN6B080C17**14 | 23600 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.94 | 19800 | R-410A
216794419 | 2.52 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B080D4PSC+LRP | 30200 | 17.5 | 11 | 9 | 31800 | 30000 | 94.34% | 2.77 | 36600 | R-454B
216794451 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | *DHMC100CCV4+LRP | 42000 | 19.6 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.67 | 51000 | R-454B
216794471 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | L8V1B080U4VSB+LRP | 41500 | 19 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.81 | 51000 | R-454B
216794535 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2B060U4VSB+LRP | 41500 | 19.2 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.81 | 51000 | R-454B
216794537 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S9V2B060U4VSB+LRP | 41500 | 19.2 | 11.7 | 9 | 46500 | 42500 | 91.4% | 2.76 | 51000 | R-454B
216794603 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2D120U5VSB+LRP | 41500 | 20.2 | 11.7 | 9.5 | 46000 | 41500 | 90.22% | 2.81 | 49500 | R-454B
214393753 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R951V0403A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393862 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R951V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214391679 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R951V0403A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.9 | 16000 | R-410A
216457601 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG80936+AEFE3A* |  | 34200 | 18 | 12 | 9.5 | 32600 | 23600 | 72.39% | 1.9 | 27000 | R-410A
216487876 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)6021G48*+TXV | 986TD66100C21*** | 45000 | 18 | 10 | 9 | 45500 | 33200 | 72.97% | 2.06 | 40500 | R-454B
216558395 | 2.62 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE*S+CM36B36+TDR |  | 31400 | 17 | 10 | 8.1 | 32200 | 26400 | 81.99% | 2.75 | 24000 | R-410A
214394188 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | U802VA050317M | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394195 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | U802VA050317M | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394067 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R962V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213821580 | 2.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0902116A* | 34800 | 16.5 | 9 | 8.1 | 38500 | 32200 | 83.64% | 2.52 | 29400 | R-410A
213821582 | 2.9 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80MS(N,L)0902116A* | 34800 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.52 | 29400 | R-410A
213821596 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)1352420A* | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821629 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *92MSN1002122A* | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821630 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *92MSN1002122A* | 35200 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.72 | 29200 | R-410A
213821664 | 2.78 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *96VTN0802120B* | 33400 | 16.4 | 9.8 | 8.1 | 37800 | 31400 | 83.07% | 2.72 | 28800 | R-410A
215037829 | 3.71 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL17XP1-048-230A** | CH60B34+TDR | ML193UH090XE48C* | 44500 | 15.3 | 12.4 | 8.1 | 44500 | 32000 | 71.91% | 2.77 | 31000 | R-410A
212977820 | 1.48 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L14** | *80MS(N,L)0451412A* | 17700 | 16.5 | 11 | 8.1 | 18200 | 18600 | 102.2% | 2.24 | 12300 | R-410A
216762908 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | HE2K*60+TXV+AEFE5* |  | 44500 | 17 | 11 | 8.2 | 45000 | 33200 | 73.78% | 1.82 | 37000 | R-454B
214392750 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R801V0504A17UHN | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214392800 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R801V0504A17UHU | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392825 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R801V0704A17UHU | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215673987 | 3.67 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716A* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.04 | 42500 | R-454B
216735797 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *92MSN1002120A* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17400 | R-454B
215674217 | 3.75 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU0802120B* | 45000 | 17.5 | 9.5 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
216788586 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG84*48+TXV+AEFE5* |  | 46000 | 17 | 11.7 | 8.5 | 45000 | 33200 | 73.78% | 1.86 | 37000 | R-454B
216732367 | 4.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | PL60H210P19*+TXV+AEFE5* |  | 53000 | 19 | 11.7 | 9.5 | 53000 | 53000 | 100% | 2 | 53000 | R-454B
216788570 | 4.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,RG88*60+TXV+AEFE5* |  | 53000 | 19 | 11.7 | 9.5 | 53000 | 53000 | 100% | 2 | 53000 | R-454B
216734355 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80CSU0601716A* | 23000 | 17 | 11 | 8.5 | 21200 | 19000 | 89.62% | 1.94 | 17900 | R-454B
212984998 | 2.52 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *92MSN0802120A* | 30200 | 15.2 | 9 | 8.1 | 34200 | 26400 | 77.19% | 1.86 | 23200 | R-410A
213821665 | 2.82 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96VTN0802120B* | 33800 | 16.5 | 9.9 | 8.1 | 37800 | 31400 | 83.07% | 2.72 | 28800 | R-410A
215654017 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH24B3J+TDR | Y81E080B12SMPS1 | 21800 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
215912361 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TL9E060B12UH11 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215912362 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TL9E060B12UH11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
215912375 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y080B12MP11 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
215912427 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Y91E060B12SMPS1 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18600 | 82.3% | 2 | 18600 | R-454B
215912429 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Y91E080B12SMPS1 | 21600 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
215674357 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0901716B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
216054315 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG86*60+TXV+AEFE5* |  | 51500 | 17.75 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 1.98 | 43000 | R-454B
215674427 | 3.83 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN1002122B* | 46000 | 18 | 10 | 9 | 47500 | 33800 | 71.16% | 2.08 | 42000 | R-454B
214394371 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | U97MV0603A17DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216794286 | 1.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B040D3VSB+LRP | 18600 | 19.2 | 11 | 9 | 23000 | 21800 | 94.78% | 2.71 | 26600 | R-454B
216794304 | 1.57 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)36C3J+TDR | S9V2B060U3VSB+LRP | 18800 | 19.8 | 11.7 | 9 | 22200 | 21200 | 95.5% | 2.64 | 26000 | R-454B
212577448 | 3.79 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA848A*031* | C60A***L189 | 58TN*A090C21**20 | 45500 | 17 | 10 | 8.5 | 43500 | 32200 | 74.02% | 2.24 | 36200 | R-410A
214243998 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CNPV*3017AL*+UI | 987MC42080C17*** | 23200 | 19.5 | 13 | 9.5 | 26800 | 20000 | 74.63% | 2.36 | 25000 | R-410A
216764932 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 | S8X2B060M4PSC | 32200 | 17.1 | 11.7 | 8.7 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216764945 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*BD04AS3 | S8X1A040M3PTC | 32400 | 17.1 | 11.5 | 8.2 | 33600 | 24600 | 73.21% | 1.9 | 21800 | R-454B
216764962 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S8X2C100M5PSC | 33000 | 17.1 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
216764963 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S8X2C080M5PSC | 32600 | 17.1 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216764964 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*C005AS3 | S8X1C080M5PTC | 32600 | 17.1 | 11.7 | 8.7 | 32400 | 24000 | 74.07% | 2.1 | 21200 | R-454B
216764999 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCB004AS3 | S8X1B060M4PTC | 32200 | 17.1 | 11.7 | 8.7 | 32200 | 23800 | 73.91% | 2.1 | 21000 | R-454B
216765014 | 2.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7036A1 | 5TXCC005AS3 | S8X1C100M5PTC | 33000 | 17.1 | 11.5 | 8.7 | 32800 | 24400 | 74.39% | 2.1 | 21600 | R-454B
216765079 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7048A1 | 5TXCD010AS3 | S8X2C100M5PSC | 43500 | 17.1 | 12 | 9 | 44000 | 32200 | 73.18% | 2.2 | 29400 | R-454B
216734557 | 1.85 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *97CMN0601714B* | 22200 | 16 | 10.5 | 8.1 | 20800 | 18700 | 89.9% | 1.85 | 17600 | R-454B
216736392 | 1.85 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80CTL0701412B* | 22200 | 16 | 10.5 | 8.1 | 21000 | 18900 | 90% | 1.85 | 17700 | R-454B
216736980 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X30M12A* | *80CSU0401712A* | 23000 | 17 | 11 | 8.5 | 21400 | 19100 | 89.25% | 1.94 | 18000 | R-454B
216735258 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *96VSN0801716B* | 23000 | 16.5 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216735458 | 1.92 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)0451714A* | 23000 | 15.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.98 | 17500 | R-454B
216735524 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80VSL0701716B* | 23000 | 16.5 | 11 | 8.5 | 20600 | 18300 | 88.83% | 1.96 | 17400 | R-454B
216735542 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80VSL0902120B* | 23400 | 16 | 11 | 8.5 | 20800 | 18600 | 89.42% | 1.98 | 17700 | R-454B
215675215 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL1102120B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33600 | 70% | 2.06 | 42000 | R-454B
215675515 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU1002120A* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
215675415 | 3.92 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *95CSU0802120B* | 47000 | 18 | 9.5 | 9 | 50000 | 36600 | 73.2% | 1.98 | 46000 | R-454B
216762909 | 4.25 | Yes | No | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H60HA5*** | FC*CC9*60+TXV+TD |  | 51000 | 15.2 | 10 | 8.5 | 52000 | 41000 | 78.85% | 1.95 | 42500 | R-454B
216624566 | 3.96 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H60HA5*** | FE*TT9*60+TXV |  | 47500 | 18 | 11.7 | 9.5 | 46000 | 41500 | 90.22% | 1.75 | 38000 | R-454B
212983963 | 2.53 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X43L21A* | *92MSN0601714A* | 30400 | 15.2 | 9 | 8.1 | 33400 | 26400 | 79.04% | 1.84 | 23200 | R-410A
216056094 | 1.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM9E060A10MP12 | 20000 | 16.5 | 9.8 | 8.5 | 22600 | 18100 | 80.09% | 2 | 18400 | R-454B
216056162 | 1.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TL9E060B12UH11 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216056228 | 1.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TP9C060B12MP13 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216056248 | 1.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Y82E060A12LMPS1 | 19500 | 18 | 11.2 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
216056295 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TM8V080B12MP12 | 22000 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216056395 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | YP9C080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
213927847 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9Y080B12MP11 | 32800 | 18 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.47 | 25800 | R-410A
216056548 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TPLC080C16MP13 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216056598 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y100C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
214244064 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CNPV*4221AL*+UI | 88*TB36045C17*** | 23400 | 19.5 | 13 | 9.5 | 26800 | 20000 | 74.63% | 2.4 | 25000 | R-410A
216765081 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*D008AS3 | S8X2C100M5PSC | 51000 | 16.5 | 10 | 8.7 | 52000 | 39000 | 75% | 2.1 | 34400 | R-454B
215654020 | 1.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CH36A3J+TDR | Y81E040A12SMPS1 | 20800 | 17.5 | 11.2 | 9.5 | 22800 | 18100 | 79.39% | 2 | 18400 | R-454B
213360248 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LH35/36F9 | EL297UH045XV36B* | 33400 | 21 | 12.5 | 8.8 | 33200 | 25800 | 77.71% | 1.82 | 30200 | R-410A
216765099 | 4.25 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5PX*DD10AS3 | S8X1C100M5PTC | 51000 | 16 | 10 | 8.7 | 51000 | 38500 | 75.49% | 2.1 | 34000 | R-454B
216056682 | 2.58 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM9Y100C16MP11 | 31000 | 18 | 10.5 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
215912454 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Y81E080C16SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216056714 | 3.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 40000 | 16.5 | 11.2 | 8.1 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216056733 | 3.33 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E080C16MP12 | 40000 | 17.5 | 10.5 | 8.1 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216056749 | 3.42 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE100C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216056780 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E100C20UH11 | 41500 | 18 | 11.5 | 8.5 | 45000 | 34000 | 75.56% | 2 | 33600 | R-454B
216056816 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9E080C16MP12 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34400 | 76.44% | 2 | 33800 | R-454B
216056832 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM9V120D20MP12 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216765115 | 4.33 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TXCD010AS3 | S8X2D120M5PSC | 52000 | 16.5 | 11.2 | 8.7 | 51000 | 38500 | 75.49% | 2.2 | 33800 | R-454B
216766018 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B004AS3 | S8V2B080M4PCB | 32200 | 16 | 12 | 8.7 | 32200 | 24000 | 74.53% | 2.11 | 21200 | R-454B
216766034 | 2.62 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*B006AS3 | S9X2B060D3PSB | 31400 | 15.2 | 11 | 8.7 | 32000 | 24000 | 75% | 2.15 | 21200 | R-454B
216766098 | 2.7 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*BD06AS3+P0V0A000M30SD |  | 32400 | 16 | 12 | 8.5 | 33000 | 24200 | 73.33% | 2.05 | 21400 | R-454B
216766132 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*C005AS3 | S8V2C100M5PDB | 32600 | 16 | 12 | 8.7 | 32400 | 24000 | 74.07% | 2.13 | 21200 | R-454B
216766216 | 2.78 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5PX*CD07AS3 | S9V2C100D5VSB | 33400 | 16.5 | 12 | 8.7 | 33200 | 24400 | 73.49% | 2.11 | 21600 | R-454B
216056865 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216056482 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216056580 | 1.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Y81E100B12SMPS1 | 21000 | 19 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
216687224 | 4.46 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF97MV508521DH | 53500 | 17 | 10 | 10 | 53500 | 48500 | 90.65% | 2 | 51000 | R-454B
216766282 | 2.68 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCB004AS3 | S9X2B080U4PSB | 32200 | 16 | 12 | 8.7 | 32200 | 23800 | 73.91% | 2.11 | 21000 | R-454B
216766386 | 2.82 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCC007AS3 | S9V2C080U5VSB | 33800 | 17.1 | 12 | 9 | 32600 | 24200 | 74.23% | 2.21 | 21400 | R-454B
216056880 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Y91E080C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46000 | 33400 | 72.61% | 2 | 32200 | R-454B
216056699 | 2.6 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC100C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216766434 | 2.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7036A1 | 5TXCD010AS3 | S8V2D120M5PDB | 34600 | 17.1 | 12.5 | 9 | 32400 | 24000 | 74.07% | 2.24 | 21200 | R-454B
213821027 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0701712A* | 23200 | 16.5 | 9.5 | 8.1 | 24600 | 22200 | 90.24% | 2.86 | 19800 | R-410A
216761998 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HE35*48+TXV+AEFE4B* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
216760244 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,GE48*60+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
215683643 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3617AM*+UI | 58CU*A040C17**12 | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 19900 | R-454B
215683625 | 1.92 | No | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3017AM*+UI | 58TN*B045C17**12 | 23000 | 16.5 | 10 | 8.5 | 24000 | 16800 | 70% | 1.86 | 20200 | R-454B
215683627 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3017AM*+UI | 58TN*B070C14**12 | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
215683707 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 59MN7C060C21**20 | 24000 | 17 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215683709 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 59MN7C080C17**14 | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
214396960 | 2.8 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TM8E120C16MP11 | 33600 | 19 | 11 | 9 | 31400 | 25400 | 80.89% | 2 | 26000 | R-454B
215675675 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CSU0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2.12 | 46000 | R-454B
216735746 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *97CMN1002122B* | 23400 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
216735503 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)0902116A* | 23200 | 16 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216735512 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *80MS(N,L)1102120A* | 23600 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216735803 | 1.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *92MSN1002122A* | 23600 | 16 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.96 | 17700 | R-454B
213612286 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG86960+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
215654032 | 2.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E100C20SMPS1 | 32000 | 18 | 11 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
213088725 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P179+AEFE5* |  | 46000 | 18 | 11.7 | 9.3 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
213088750 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG88960+AEFE5* |  | 51500 | 17 | 11.7 | 9.5 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
216762061 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V36H175D14*+TXV+AEFE4B* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
214394518 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | U98MV0603A17UPS | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
216624595 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | LP40/60R*+TXV+LEFE5* |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
214396925 | 2.78 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TM8E080C16MP11 | 33400 | 19 | 11 | 9 | 31400 | 25400 | 80.89% | 2 | 26000 | R-454B
214396990 | 2.78 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF48C5CFS1 | TPLC100C16MP13 | 33400 | 18 | 11 | 9 | 31600 | 25400 | 80.38% | 2 | 26000 | R-454B
214397357 | 2.88 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TMLE120C20MP11 | 34600 | 17 | 11 | 8.5 | 32600 | 25600 | 78.53% | 2 | 26400 | R-454B
214396472 | 2.87 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM36C5CDS1 | TM8E080C20MP11 | 34400 | 17 | 11 | 8.5 | 32400 | 26400 | 81.48% | 2 | 28600 | R-454B
214396774 | 4.46 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60D5CJS1 | TM8E130D20MP11 | 53500 | 18 | 11 | 9 | 55500 | 40000 | 72.07% | 2 | 38500 | R-454B
214397039 | 3.67 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTM60C5CGS1 | TM8Y100C16MP11 | 44000 | 18 | 11.7 | 9 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
216760262 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,RG48*60+TXV+AEFE5* |  | 45500 | 17 | 11.5 | 8.35 | 45000 | 33200 | 73.78% | 1.84 | 37000 | R-454B
216760230 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V,G36H***D12*+TXV+AEFE3A* |  | 23000 | 19 | 12.5 | 9.2 | 22400 | 17000 | 75.89% | 1.96 | 21400 | R-454B
216760246 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | H,GE48*60+TXV+AEFE5* |  | 45500 | 17 | 11.5 | 8.35 | 45000 | 33200 | 73.78% | 1.84 | 37000 | R-454B
216762922 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V60H210P16*+TXV+AEFE5* |  | 44500 | 16 | 11 | 8.2 | 45000 | 33200 | 73.78% | 1.82 | 37000 | R-454B
215399952 | 2.53 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR |  | 30400 | 15.2 | 10.5 | 8.1 | 31000 | 31600 | 101.9% | 2.54 | 27000 | R-454B
214809200 | 3.63 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTU60C5XGS1+TXV | TM9V100C16MP12 | 43500 | 18 | 11.7 | 9 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
214421545 | 3.79 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTM60D5CGS1+JMET18DS2N1 |  | 45500 | 18 | 12 | 9.5 | 45500 | 33800 | 74.29% | 2 | 34000 | R-454B
211627922 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9E080C16MP12 | 32200 | 18 | 9.9 | 8.1 | 25200 | 31400 | 124.6% | 2.86 | 25200 | R-410A
211627974 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 25600 | 32000 | 125% | 2.82 | 25600 | R-410A
211628013 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TM9V100C16MP12 | 32000 | 17.5 | 9.9 | 8.5 | 25400 | 31600 | 124.4% | 2.87 | 25400 | R-410A
211627545 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B36+TDR | TL8E060A12UH11 | 32200 | 18 | 9.9 | 8.1 | 25400 | 31600 | 124.4% | 2.84 | 25400 | R-410A
211780576 | 2 | Yes | Yes | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE32936 | *92ESN0801716A* | 24000 | 17 | 10 | 8.5 | 25200 | 23800 | 94.44% | 1.96 | 18400 | R-410A
211627699 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM8E120C16MP11 | 31400 | 17.8 | 9.8 | 8.2 | 25000 | 31600 | 126.4% | 2.81 | 25200 | R-410A
211628106 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | TM9Y100C20MP11 | 31600 | 15.4 | 9.3 | 8.1 | 34000 | 27400 | 80.59% | 2.45 | 25400 | R-410A
211628115 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36A36+TDR | TM9Y120D20MP11 | 31000 | 16.2 | 9.2 | 8.3 | 25200 | 31800 | 126.2% | 2.89 | 25400 | R-410A
215611123 | 4.54 | Yes | No | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FHRNVM6024S*YECA |  | 54500 | 17.5 | 10.5 | 8.1 | 54500 | 53000 | 97.25% | 2 | 51000 | R-454B
214568840 | 2.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | H,PE9J936 | 59TN6B120C24**22 | 32000 | 17 | 11.5 | 8.5 | 30800 | 24400 | 79.22% | 2 | 30400 | R-410A
216788576 | 4.33 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,RG88*60+TXV+AEFE5* |  | 52000 | 18 | 11.7 | 9.4 | 53000 | 38000 | 71.7% | 2 | 42000 | R-454B
212985297 | 2.52 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X42L24A* | *92MSN1002120A* | 30200 | 15.2 | 9 | 8.1 | 34200 | 27400 | 80.12% | 1.8 | 23400 | R-410A
216762012 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LEM25*23G+TXV |  | 24000 | 16 | 11.7 | 8.8 | 22400 | 22200 | 99.11% | 1.78 | 18600 | R-454B
207154559 | 3.92 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWA7048A4 | 4PX*CU42BS3 | S8X1C100M5PSC | 47000 | 17 | 11.5 | 8.1 | 49500 | 46500 | 93.94% | 3.4 | 47500 | R-410A
212367397 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG34936 | BGH96M060B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212367411 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG34936 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216624577 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | L*18/36T*+TXV+LEFE3A* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
216624578 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | LH29/36X*+TXV+LEFE4B* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
215869164 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG37936+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 23600 | 72.39% | 1.9 | 27000 | R-410A
215821298 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | FE*G32*25+TXV |  | 23000 | 17 | 11 | 8.25 | 22400 | 16800 | 75% | 1.8 | 18000 | R-454B
211782039 | 1.92 | No | No | KEEPRITE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | H,GE22936 | *92ESN0801716A* | 23000 | 16 | 9.5 | 8.5 | 25200 | 23000 | 91.27% | 1.94 | 18400 | R-410A
216788571 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,RG35*48+TXV+AEFE4B* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
216762901 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HE35*48+TXV+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
214290124 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84160+TXV | BGH96M100D5B | 51500 | 18 | 11.7 | 8.5 | 52000 | 37400 | 71.92% | 1.85 | 37400 | R-410A
214290125 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84160+TXV | BGH96M120D5B | 51500 | 18 | 11.7 | 8.5 | 52000 | 37400 | 71.92% | 1.85 | 37400 | R-410A
216977172 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH29/36F*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977236 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LH40/61W*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.85 | 38000 | R-454B
216977238 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LP40/60R*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 8.95 | 45500 | 39000 | 85.71% | 1.84 | 38000 | R-454B
216977239 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | L*42/60Z*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.84 | 38000 | R-454B
216093485 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG35*48+TXV+AEFE4B* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-454B
216687181 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80SV405017UHS | 22800 | 20 | 12 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
214396303 | 4.42 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60C5CHS1 | TM9V100C20MP12 | 53000 | 19 | 11 | 8.5 | 53500 | 38500 | 71.96% | 2 | 37000 | R-454B
214396353 | 4.42 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | JHC60D5CJ2SS1 |  | 53000 | 19 | 11 | 8.5 | 54000 | 39000 | 72.22% | 2 | 37200 | R-454B
213821566 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0701412A* | 35200 | 16 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.63 | 29400 | R-410A
213821568 | 2.78 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0701712A* | 33400 | 16.4 | 9.8 | 8.1 | 37800 | 31800 | 84.13% | 2.73 | 29000 | R-410A
213821600 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80MS(N,L)1552420A* | 35400 | 16.5 | 10.5 | 8.1 | 38500 | 31800 | 82.6% | 2.71 | 29200 | R-410A
213821661 | 2.78 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *96VTN0801716B* | 33400 | 15.9 | 9.8 | 8.1 | 37800 | 31800 | 84.13% | 2.7 | 29000 | R-410A
213821668 | 2.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96VTN1002120B* | 35400 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.61 | 29400 | R-410A
216093469 | 1.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-24RXB-M15S | HG32*24+TXV+AEFE3A* |  | 23000 | 18 | 11 | 8.25 | 22400 | 16800 | 75% | 1.8 | 18000 | R-454B
215213868 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,YG9J936+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
213362467 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG35936 | BGH96M080B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
213821643 | 2.82 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *96MSN1002120A* | 33800 | 16.4 | 9.8 | 8.5 | 37800 | 31800 | 84.13% | 2.75 | 29000 | R-410A
213821645 | 2.85 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96MSN1002120A* | 34200 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.75 | 29000 | R-410A
216687213 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF97MV508521DH | 45500 | 19 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
214279015 | 1.93 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVC-36HDN1-M20G | F,PE*G32925 |  | 23200 | 20 | 12.5 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
214393218 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R802V0504A17UHS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
210693365 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VS800805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693383 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC800804C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215667219 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CTL0901716B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16400 | 70.69% | 2 | 19700 | R-454B
214393804 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R951V0603A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393813 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R951V0603A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
216762903 | 1.95 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | A36VBC*+TXV+AEFE4B* |  | 23400 | 20 | 12.5 | 9.25 | 22400 | 17000 | 75.89% | 1.96 | 21400 | R-454B
216487890 | 4.58 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | CE(P,V)6024G48*+TXV | 986TD60080C21*** | 55000 | 18 | 8.5 | 9 | 58000 | 41500 | 71.55% | 2.02 | 50500 | R-454B
216734491 | 1.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80CTL0701412B* | 22200 | 16.5 | 11 | 8.1 | 20800 | 18600 | 89.42% | 1.85 | 17500 | R-454B
216734393 | 1.85 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X36M17A* | *80MS(N,L)0701712A* | 22200 | 16.5 | 11 | 8.1 | 20800 | 18600 | 89.42% | 1.85 | 17500 | R-454B
212985008 | 2.55 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | EA*4X43L21A* | *92MSN0802120A* | 30600 | 15.5 | 9 | 8.5 | 33400 | 28200 | 84.43% | 1.76 | 23600 | R-410A
216760231 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V,G36H175D14*+TXV+AEFE4B* |  | 23800 | 20 | 13 | 9.45 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
216494144 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CE(P,V)3621G34*+TXV | 88*TB60090C21*** | 32800 | 20 | 11.5 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29200 | R-454B
216732368 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | PL60H210P16*+TXV+AEFE5* |  | 45500 | 18 | 11.7 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-454B
216788572 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V,R48H175P38*+TXV+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
213821553 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *96VTN1002122B* | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
214573614 | 2.62 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X36L21A*+WALLCON | *80CTL0702120B* | 31400 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.86 | 31200 | R-410A
214573744 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L21A*+WALLCON | *95CSU0802120B* | 31800 | 17 | 11 | 8.5 | 33000 | 24400 | 73.94% | 1.9 | 31400 | R-410A
214573814 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L24A*+WALLCON | *95CSU1002122B* | 31800 | 17.5 | 11 | 8.5 | 32800 | 24400 | 74.39% | 1.9 | 31200 | R-410A
214573864 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X43L21A*+WALLCON | *95CSU0802120B* | 32800 | 17.5 | 11 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
214573914 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L21A*+WALLCON | *80CTL0702120B* | 32200 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
216687192 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF96TV306017M4 | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
216687193 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF96TV304017M4 | 34200 | 20 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
216760257 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,RG48*60+TXV+AEFE5* |  | 46500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
216687174 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF96TV307017M4 | 22800 | 20 | 12 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
216687175 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF98MV306017UP | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
216687177 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF98MV307017UP | 22800 | 20 | 12 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
216762902 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HE2K*60+TXV+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-454B
215667093 | 1.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *97CMN0801714B* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
212367399 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG34936 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215667111 | 1.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *96CTN0401410B* | 22400 | 15.5 | 9 | 8.5 | 24400 | 17200 | 70.49% | 1.82 | 20800 | R-454B
215666982 | 1.9 | No | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CSU0601716A* | 22800 | 16.5 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20400 | R-454B
215675765 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *95CSU0802120B* | 48000 | 18.5 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
216768261 | 2 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H24HA5*** | FE*E34*25+TXV |  | 24000 | 18 | 11.7 | 9.95 | 22400 | 22600 | 100.9% | 1.8 | 17000 | R-454B
216788565 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,RG35*48+TXV+AEFE4B* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
214393938 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R951V1005A21M4S | 33000 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
213821545 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *96VTN1002120B* | 29600 | 15.2 | 9 | 8.5 | 34200 | 24200 | 70.76% | 2.69 | 23600 | R-410A
214393947 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R951V1005A21M4S | 32800 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394036 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R962V0603A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214573394 | 2.65 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X42L21**+WALLCON | *95CSU1002122B* | 31800 | 17 | 11.5 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31400 | R-410A
214573444 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X48L21**+WALLCON | *95CSU0802120B* | 32400 | 17.5 | 11.5 | 8.1 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
213253153 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213612285 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG84960+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
215039674 | 3.71 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ML17XP1-048-230A** | CH60B34+TDR | ML193UH090XE48C* | 44500 | 15.3 | 12.4 | 8.1 | 44500 | 32000 | 71.91% | 2.77 | 31000 | R-410A
213821550 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30B34+TDR | *96VTN1002122B* | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
216788567 | 4.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | V,R60H210P19*+TXV+AEFE5* |  | 53000 | 19 | 11.7 | 9.5 | 53000 | 53000 | 100% | 2 | 53000 | R-454B
213821044 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80MS(N,L)0901714A* | 23800 | 16.5 | 9.5 | 8.1 | 24800 | 22400 | 90.32% | 2.91 | 19900 | R-410A
213821047 | 1.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *80MS(N,L)0902116A* | 23200 | 16.5 | 9.5 | 8.1 | 24600 | 22000 | 89.43% | 2.86 | 19700 | R-410A
213821079 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36B34+TDR | *80VTL1102122B* | 23800 | 16 | 9.5 | 8.5 | 25200 | 22400 | 88.89% | 2.92 | 20000 | R-410A
213821145 | 1.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)36C34+TDR | *96VTN0401410B* | 23000 | 15.5 | 9.4 | 8.1 | 24400 | 22200 | 90.98% | 2.86 | 19700 | R-410A
216765900 | 1.97 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7024A1 | 5PX*BD06AS3 | S9X2B080D4PSB | 23600 | 17 | 12.5 | 8.5 | 22200 | 17300 | 77.93% | 1.96 | 15400 | R-454B
215667562 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0401712A* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 19900 | R-454B
214393241 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R802V0754A17DZ | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393245 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R802V0754A17DZ | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215667901 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0801714B* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
214393250 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R802V0754A17DZ | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393618 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R921V0603A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393620 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R921V0603A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
216687186 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF80TV405017UH | 22800 | 20 | 12 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
214588344 | 2.95 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L159 | 926TC60100V21*** | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
213088735 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG86960+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
210693378 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VM971005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216734984 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *80VSL0701716B* | 23200 | 16.5 | 11 | 8.5 | 21000 | 18600 | 88.57% | 1.96 | 17700 | R-454B
216457592 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | H,RG80936+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 23600 | 72.39% | 1.9 | 27000 | R-410A
216687170 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF96TV306017M4 | 22800 | 21 | 13 | 10 | 22800 | 18600 | 81.58% | 1.8 | 21200 | R-454B
214609067 | 1.92 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTM30B5ACS1 | Z9ES060B12SMPS1 | 23000 | 17 | 11.7 | 9.5 | 23000 | 19200 | 83.48% | 2 | 17900 | R-454B
214609160 | 1.92 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTF30A5ADS1 | Z9ES060A10SMPS1 | 23000 | 19 | 12 | 9 | 23000 | 18500 | 80.43% | 2 | 18200 | R-454B
214396819 | 2.85 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36C5CDS1 | TL8E080C16UH11 | 34200 | 18 | 11 | 8.5 | 32200 | 26400 | 81.99% | 2 | 28600 | R-454B
213821228 | 1.9 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | D(A,C,E)30C44+TDR | *80VTL0701716B* | 22800 | 17.5 | 9.8 | 8.5 | 25200 | 20000 | 79.37% | 3 | 18700 | R-410A
216687220 | 4.5 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1960MJAYCA | FCCA6021SYEA | FF80TV510021DZ | 54000 | 17 | 10 | 10 | 54000 | 48000 | 88.89% | 2 | 51000 | R-454B
215037861 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL17XP1-048-230A** | CH60B34+TDR | ML196UH110XE60C* | 45000 | 15.5 | 12.4 | 8.1 | 44500 | 31600 | 71.01% | 2.75 | 30800 | R-410A
210598032 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X48L21A*+WALLCON | *96CTN0601714A* | 24000 | 16.5 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20600 | R-410A
213362474 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | HG9J936 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
215942661 | 3 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CVAVA6124XMA*+UI | 987TA60080C21*** | 36000 | 22 | 12.5 | 8.5 | 37400 | 28200 | 75.4% | 2.04 | 32400 | R-454B
216093474 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | FE*TT1*37+TXV |  | 34200 | 19 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
214396910 | 2.77 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36B5CDS1 | TM9Y060B12MP11 | 33200 | 18 | 11 | 8.5 | 31200 | 25600 | 82.05% | 2 | 27800 | R-454B
216687197 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FCCA3621MYEA | FF97MV306017DH | 34200 | 21 | 12 | 10 | 34200 | 29600 | 86.55% | 2 | 30000 | R-454B
215864473 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5PX*B004AS3 | *UHMB060CCV3+LRP | 31600 | 18.1 | 10 | 8.5 | 33000 | 25800 | 78.18% | 2 | 31200 | R-454B
215864477 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5PX*B004AS3 | S9V2B080U4VSB+LRP | 31600 | 18.1 | 10 | 8.5 | 32800 | 25600 | 78.05% | 2 | 31000 | R-454B
215864493 | 2.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5PX*B004AS3 | S8V2B060M4PDB | 31600 | 18.1 | 10 | 8.5 | 32800 | 25400 | 77.44% | 2 | 31000 | R-454B
215654033 | 2.6 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E120C16SMPS1 | 31200 | 17.5 | 11.2 | 8.1 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
213785752 | 2.82 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA436A*031* | CSPH*6012AL*+UI | 59MN7C120C24**22 | 33800 | 19 | 12 | 8.5 | 36000 | 25400 | 70.56% | 2.02 | 30400 | R-410A
212367398 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | HG82936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
212367484 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36HDN1-M20G | H,RG34936 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
216788573 | 4.33 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V,R60H210P19*+TXV+AEFE5* |  | 52000 | 18 | 11.7 | 9.4 | 53000 | 38000 | 71.7% | 2 | 42000 | R-454B
216788575 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,RG84*48+TXV+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-454B
216624579 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | L*19/36U*+TXV+LEFE4B* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
216624580 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | LP25/36R*+TXV+LEFE4B* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
216624596 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | L*42/60Z*+TXV+LEFE5* |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
216056756 | 3.29 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C100C16MP13 | 39500 | 16.5 | 11.2 | 8.1 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
215864523 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5PX*C005AS3 | *UHMC100CCV4+LRP | 31800 | 18.1 | 10 | 8.5 | 32400 | 25200 | 77.78% | 2.1 | 30800 | R-454B
215864527 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5PX*C005AS3 | S8V2C080M5PDB | 31800 | 18.1 | 10 | 8.5 | 32600 | 25400 | 77.91% | 2.1 | 31000 | R-454B
215864575 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5TXCB004AS3 | S8V2B080M4PDB | 31800 | 18.1 | 10 | 8.5 | 33000 | 25600 | 77.58% | 2 | 31200 | R-454B
214242845 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CNPV*3621AL*+UI | 59TN6C100C21**22 | 23600 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.92 | 20800 | R-410A
216794421 | 2.52 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B080D4VSB+LRP | 30200 | 17.5 | 11 | 9 | 31800 | 30000 | 94.34% | 2.77 | 36600 | R-454B
214393709 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R921V1005A21M4S | 33000 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216487892 | 4.58 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | CE(P,V)6021G48*+TXV | 986TD66100C21*** | 55000 | 18 | 9 | 8.5 | 57500 | 41000 | 71.3% | 1.9 | 50000 | R-454B
214393718 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R921V1005A21M4S | 33400 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394070 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R962V0703A17M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216764223 | 2.68 | Yes | No | TRANE | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | 5TWX7036A1 | 5PX*B004AS3 |  | 32200 | 15.5 | 11 | 8.5 | 33000 | 24600 | 74.55% | 2 | 21800 | R-454B
213147043 | 3.08 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L159+AEFE4B* |  | 37000 | 16 | 10 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
215864675 | 3.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5TXCB006AS3 | S8V2B060M4PDB | 45000 | 18.1 | 10 | 8.5 | 46000 | 35400 | 76.96% | 2.1 | 43000 | R-454B
216951980 | 2.55 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8X2A040M3PTC | 30600 | 16 | 12 | 8.1 | 27800 | 20200 | 72.66% | 2.82 | 19700 | R-454B
215667542 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *96CTN0801714B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20200 | R-454B
211173337 | 2.95 | No | Yes | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1536S1R-**A | C(A,C,D,E)48D34+TDR | GDD96C110C5M | 35400 | 16.4 | 13 | 8.2 | 32000 | 22400 | 70% | 2.8 | 18700 | R-410A
215828421 | 4.21 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | FE*TT9*60+TXV |  | 50500 | 17.5 | 11.4 | 9.25 | 53000 | 38000 | 71.7% | 1.96 | 43000 | R-454B
215667131 | 1.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *96CTN0601714B* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
216735857 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96MSN1002122A* | 23400 | 16 | 11 | 8.5 | 20800 | 18600 | 89.42% | 1.98 | 17600 | R-454B
216735942 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *95MSU1002120A* | 23200 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216736094 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *97VTN1002122A* | 23200 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.96 | 17600 | R-454B
216736158 | 1.87 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X24M12A* | *80MS(N,L)0701412A* | 22400 | 15.2 | 10.5 | 8.1 | 21200 | 19000 | 89.62% | 1.85 | 17800 | R-454B
215667632 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701716B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214392058 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | U97MV1005A21DHS | 44000 | 15.5 | 10 | 8.2 | 45000 | 34200 | 76% | 3.06 | 32400 | R-410A
216762916 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | HG48*48+TXV+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
213821539 | 2.42 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30C44+TDR | *96VTN0802120B* | 29000 | 15.2 | 8.9 | 8.1 | 33400 | 23800 | 71.26% | 2.8 | 23200 | R-410A
213821638 | 2.9 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *96MSN0801716A* | 34800 | 16 | 10 | 8.1 | 38500 | 31800 | 82.6% | 2.68 | 29200 | R-410A
216687180 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF97MV306017DH | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
216760258 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,RG48*48+TXV+AEFE4B* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-454B
212986618 | 1.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *96MSN0401712A* | 23200 | 15.2 | 10 | 8.5 | 27200 | 24400 | 89.71% | 2.02 | 19100 | R-410A
212986866 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L14A* | *96MSN0601412A* | 23200 | 16.5 | 10 | 8.5 | 27000 | 26400 | 97.78% | 2.22 | 19400 | R-410A
212987469 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *96MSN0801716A* | 23800 | 17 | 10.5 | 8.5 | 26400 | 24000 | 90.91% | 2 | 19200 | R-410A
212988707 | 2 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *95MSU0401712A* | 24000 | 16.5 | 10 | 8.5 | 25200 | 22200 | 88.1% | 1.84 | 18800 | R-410A
216951600 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX5036A1 | DH36T4J | S8X2B060M4PSC | 31800 | 16.5 | 12 | 8.1 | 28600 | 20600 | 72.03% | 2.9 | 20000 | R-454B
211174169 | 3.58 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)48C34+TDR | GUH96C110C5M | 43000 | 15.3 | 12.3 | 8.3 | 45000 | 31600 | 70.22% | 2.79 | 13500 | R-410A
213252943 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M18M | HG84960+AEFE5* |  | 45000 | 17 | 10.2 | 9 | 45000 | 32600 | 72.44% | 1.9 | 37000 | R-410A
216762011 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | LEM48*1TT+TXV |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
205751065 | 2.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X37L21A*+WALLCON | *97CMN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
216732374 | 4.58 | Yes | No | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | PL60H210P19*+TXV+AEFE5* |  | 55000 | 16 | 10 | 8.4 | 54000 | 39000 | 72.22% | 1.85 | 38000 | R-454B
216788574 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | H,RG84*48+TXV+AEFE5* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-454B
215667525 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *96CTN0601714B* | 23000 | 17 | 10 | 8.5 | 23800 | 16700 | 70.17% | 1.86 | 20200 | R-454B
213612288 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,T48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
214290117 | 4.25 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84160+TXV | BGH96M100C5B | 51000 | 18 | 11 | 8.5 | 51500 | 36400 | 70.68% | 1.83 | 38500 | R-410A
215667709 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *96CTN0601714B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.96 | 20000 | R-454B
215667845 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0702120B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215667917 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0601714B* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
215039678 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ML17XP1-048-230A** | CH60B34+TDR | ML193UH110XE48C* | 45000 | 15.5 | 12.4 | 8.1 | 44500 | 32000 | 71.91% | 2.8 | 31000 | R-410A
214609204 | 3.79 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60C5CGS1 | Z9ES100C20SMPS1 | 45500 | 18 | 11.7 | 9 | 46500 | 34000 | 73.12% | 2 | 33800 | R-454B
214395403 | 3.83 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | JHC48C5CG2SS1 |  | 46000 | 19 | 12 | 9 | 46000 | 34000 | 73.91% | 2.1 | 35600 | R-454B
212367495 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG82936 | BGH96M060B3B | 24000 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
210693391 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC960804CNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693392 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VS960805CUA* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215683923 | 2.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 59MN7C100C21**22 | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
215683939 | 2.75 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**4221AM*+UI | 58TN*B070C17**16 | 33000 | 17.5 | 9.5 | 9 | 36000 | 25800 | 71.67% | 1.86 | 31000 | R-454B
213367732 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)36C24+TDR | Y81E080C20LMPS1 | 31400 | 16.4 | 8.5 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
210693320 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VM970803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216624594 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | LP41/61R*+TXV+LEFE5* |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
216977179 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH24/37X*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977180 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH24/37F*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977194 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH24/37X*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
210693339 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VM971005CNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693342 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+MBVC1601**-1A*+TXV |  | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693356 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VM970603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212367496 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | H,RG34936 | BGH96M080B3B | 23800 | 18 | 12 | 9 | 22400 | 17000 | 75.89% | 1.9 | 19000 | R-410A
214389722 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4A* | G*VC800603B*A* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214389737 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4A* | G*VM970603BNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214389738 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4A* | G*VM970803BNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
210693340 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VM971205DNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693341 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+MBVC1201**-1A*+TXV |  | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214396662 | 1.92 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | JHC36B5AD2SS1 |  | 23000 | 19 | 11.7 | 9.5 | 23000 | 17900 | 77.83% | 2 | 18400 | R-454B
213821620 | 2.85 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *92MSN0801716A* | 34200 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.74 | 29000 | R-410A
210693337 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VM970803BNB* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214397423 | 3.71 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60C5CGS1 | TM8E100C16MP11 | 44500 | 18 | 11 | 9 | 45500 | 34200 | 75.16% | 2 | 34200 | R-454B
214397453 | 3.71 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60C5CGS1 | TMLE080C16MP11 | 44500 | 18 | 11 | 9 | 45500 | 34200 | 75.16% | 2 | 34200 | R-454B
212987016 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X25L17A* | *96MSN0601412A* | 17800 | 16.5 | 10.5 | 8.1 | 17700 | 18700 | 105.6% | 2.26 | 12200 | R-410A
212985514 | 2.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *92MSN1002122A* | 35800 | 16.5 | 10 | 8.5 | 37800 | 34600 | 91.53% | 2.04 | 29000 | R-410A
212988223 | 2.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *96MSN1002122A* | 35600 | 16 | 10 | 8.5 | 37800 | 34600 | 91.53% | 2.04 | 29000 | R-410A
216762057 | 1.98 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V36H175D14*+TXV+AEFE4B* |  | 23800 | 20 | 13 | 9.45 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
214394431 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | U97MV0855A21DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
216494110 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)3621G34*+TXV | 987MC60060C21*** | 22600 | 16 | 9.5 | 9 | 22200 | 16000 | 72.07% | 2.02 | 18700 | R-454B
210693329 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VS960603BUA* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693352 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC960803BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693379 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+MBVC1201**-1A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216762013 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LEM25*23E+TXV |  | 24000 | 16 | 11.7 | 8.8 | 22400 | 22200 | 99.11% | 1.78 | 18600 | R-454B
214393756 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V0403A17M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
210693358 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VM970804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693359 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VM971005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215588221 | 4.33 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA154A*030* | CVAMA4921XMA*+UI | 59MN7C080C21**20 | 52000 | 19 | 11.5 | 8.1 | 53500 | 45500 | 85.05% | 1.9 | 48500 | R-454B
210693375 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VM970603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693393 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC961005CNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214272267 | 2.72 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | PL36H210P299 | 58TN*B045C17**12 | 32600 | 17 | 11 | 8.5 | 31600 | 25200 | 79.75% | 1.96 | 31200 | R-410A
216056772 | 2.57 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | YP9C100C20MP13 | 30800 | 17.5 | 9 | 8.1 | 45000 | 33800 | 75.11% | 2 | 33400 | R-454B
216056791 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM8E100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216056890 | 2.73 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | YP9C100C16MP13 | 32800 | 17 | 9.8 | 8.5 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
216093473 | 2.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG36*36+TXV+AEFE3A* |  | 34000 | 18 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
214392046 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | U802VA100521M | 44000 | 15.5 | 10 | 8.2 | 45000 | 33800 | 75.11% | 3.03 | 32200 | R-410A
215683877 | 2.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3717AM*+UI | 58TN*B090C17**16 | 34000 | 17.5 | 9.5 | 9 | 35800 | 25400 | 70.95% | 1.88 | 30800 | R-454B
214628165 | 1.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P039 | 58S(B,C)*B070M14**12 | 22200 | 17 | 9.5 | 8.5 | 24600 | 24200 | 98.37% | 2.06 | 18100 | R-410A
214628200 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H210P299 | 58S(B,C)*B070M17**16 | 24200 | 17 | 10.5 | 8.5 | 23600 | 21200 | 89.83% | 1.82 | 17700 | R-410A
212989331 | 1.47 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *95MSU0601716A* | 17600 | 16.5 | 11 | 8.1 | 18100 | 18700 | 103.3% | 2.24 | 12200 | R-410A
216780794 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTM60D5CHS1 | Y81E130D20LMPS1 | 54000 | 19 | 12 | 9 | 54500 | 38500 | 70.64% | 2 | 37000 | R-454B
211174257 | 3.71 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)60D34+TDR | GUH97M090C3M | 44500 | 15.3 | 12.4 | 8.2 | 45000 | 32000 | 71.11% | 2.86 | 13800 | R-410A
216054314 | 4.42 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG86*60+TXV+AEFE5* |  | 53000 | 18.75 | 11.7 | 9.95 | 53000 | 54500 | 102.8% | 2.09 | 54000 | R-454B
210693388 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VS960603BUA* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693336 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VM970603BNB* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693361 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+MBVC1601**-1A*+TXV |  | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693370 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC960603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213772495 | 2.02 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | CSPH*4812AL*+UI | 59CU5B060C17**16 | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2.02 | 20600 | R-410A
214393772 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R951V0403A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392839 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R801V0704A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214392871 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R801V0754A17DZ | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393640 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R921V0703A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214628301 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P149 | 58TP*B070V17**16 | 23600 | 17 | 10.5 | 8.5 | 24800 | 23800 | 95.97% | 2.02 | 18100 | R-410A
214628315 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | V,C36H***P429 | 59SC6A026M14**10 | 23400 | 16 | 10 | 8.5 | 25400 | 25800 | 101.6% | 2.2 | 18500 | R-410A
214628316 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV | 59SC6A026M14**10 | 23400 | 16 | 10 | 8.5 | 25400 | 25800 | 101.6% | 2.2 | 18500 | R-410A
214628402 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139 | 59SC6A060M14**12 | 23400 | 16 | 10 | 8.5 | 25400 | 26000 | 102.4% | 2.22 | 18400 | R-410A
215683927 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 59TN6C080C17**14 | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30600 | R-454B
215684027 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 58TN*B135C24**22 | 33800 | 16 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
216374536 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60D5CHS1 | Y92E120D20SMPS1 | 54000 | 19 | 11 | 9 | 55000 | 40000 | 72.73% | 2 | 38000 | R-454B
210693313 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | G*VS800604BUA* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215684039 | 2.78 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 59MN7C080C17**14 | 33400 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
213771474 | 2.03 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | TVH825GKA2* | EA*4X43L21A*+WALLCON | *80CTL0902120B* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
215684073 | 2.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*4212AM*+UI | 58TN*B110C21**20 | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215684087 | 2.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*4212AM*+UI | 59MN7C080C21**20 | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25200 | 70.79% | 1.78 | 30600 | R-454B
215864843 | 3.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5PX*C009AS3 | *UHMC100CCV4+LRP | 46000 | 18.1 | 10.5 | 8.5 | 45000 | 34600 | 76.89% | 2.1 | 42000 | R-454B
215864861 | 3.79 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5PX*D008AS3 | L8V1C100U5VSB+LRP | 45500 | 18.1 | 10.5 | 8.5 | 45500 | 35000 | 76.92% | 2.2 | 42500 | R-454B
215864927 | 3.79 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5TXCC007AS3 | S9V2C080U5PSC+LRP | 45500 | 18.1 | 10 | 8.5 | 46000 | 35200 | 76.52% | 2.1 | 43000 | R-454B
215864941 | 3.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5TXCC009AS3 | S8V2C100M5PDB | 46000 | 18.1 | 10 | 8.5 | 45500 | 35000 | 76.92% | 2.1 | 42500 | R-454B
215864991 | 3.83 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5TXCD010AS3 | S8V2C080M5PDB | 46000 | 18.1 | 10.5 | 8.5 | 45000 | 34600 | 76.89% | 2.2 | 42000 | R-454B
210693395 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VM970603BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215667877 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *95CSU1002122B* | 24000 | 17 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215667893 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0602120B* | 24000 | 17 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
216735276 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M17A* | *95MSU0601716A* | 22800 | 16.5 | 11 | 8.5 | 20600 | 18400 | 89.32% | 1.96 | 17500 | R-454B
216762913 | 3.96 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | HG48*60+TXV+AEFE5* |  | 47500 | 18 | 11.7 | 9.9 | 46500 | 48000 | 103.2% | 2.08 | 47500 | R-454B
214394191 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | U802VA050317M | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394209 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | U802VA050317M | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394258 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | U802VA075317Z | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393924 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R951V0855A21M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394040 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R962V0603A17M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
215865111 | 3.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | 5TXCD010AS3+P0V0C000M50SD+LRP |  | 46500 | 18.1 | 11 | 8.5 | 45000 | 34400 | 76.44% | 2.2 | 42000 | R-454B
210693323 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC800604B*A* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693357 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VM970803BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693374 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | G*VC961005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693390 | 2.82 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | G*VC960803BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214396507 | 2.87 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF48C5CFS1 | TMLE100C20MP11 | 34400 | 17 | 11 | 8.5 | 32600 | 25800 | 79.14% | 2 | 26400 | R-454B
216764813 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8X2C080M5PSC | 43000 | 17.1 | 11.7 | 9 | 44500 | 32600 | 73.26% | 2.1 | 29800 | R-454B
216764829 | 3.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCD010AS3 | S8X1D120M5PTC | 44000 | 17.1 | 12 | 9 | 44500 | 32400 | 72.81% | 2.2 | 29600 | R-454B
216766450 | 3.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3+P0V0C000M50SD |  | 43500 | 17 | 12.5 | 8.7 | 43500 | 31800 | 73.1% | 2.23 | 29000 | R-454B
216766452 | 3.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*C009AS3 | S9X2C100U5PSB | 43500 | 15.2 | 12 | 8.7 | 44000 | 32200 | 73.18% | 2.21 | 29200 | R-454B
216766550 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5PX*DD10AS3 | S8V2C100M5PDB | 43000 | 16 | 11.7 | 8.7 | 44500 | 32600 | 73.26% | 2.19 | 29800 | R-454B
216766552 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC007AS3 | S8V2C100M5PCB | 43000 | 16 | 12 | 8.7 | 45000 | 32800 | 72.89% | 2.21 | 29800 | R-454B
214394059 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R962V0703A17M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214396809 | 2.77 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36B5CDS1 | TM9E060B12MP12 | 33200 | 17 | 11 | 8.5 | 31600 | 25400 | 80.38% | 2 | 27400 | R-454B
214397109 | 1.92 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTF36B5ADS1 | TM8Y080B12MP11 | 23000 | 18 | 12 | 9.5 | 23000 | 18300 | 79.57% | 2 | 18000 | R-454B
214396271 | 1.92 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTM30B5ACS1 | TM9V080B12MP12 | 23000 | 17 | 12 | 9.5 | 23000 | 17800 | 77.39% | 2 | 18000 | R-454B
214396571 | 3.63 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60C5CGS1 | TM9V100C16MP12 | 43500 | 18 | 11.7 | 9 | 44000 | 33200 | 75.45% | 2 | 32200 | R-454B
214397176 | 4.5 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTM60D5CHS1+JME18D2SN1 |  | 54000 | 19 | 12 | 9 | 53500 | 38500 | 71.96% | 2 | 36600 | R-454B
214396856 | 2.83 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36B5CDS1+JMC12B2SN1 |  | 34000 | 19 | 11.7 | 9 | 31400 | 25600 | 81.53% | 2 | 27800 | R-454B
214397009 | 2.83 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM48C5CFS1 | TL8E100C20UH11 | 34000 | 19 | 11 | 9 | 31800 | 25400 | 79.87% | 2 | 26000 | R-454B
211174208 | 3.79 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)48D34+TDR | GUH96T090C3M | 45500 | 15.2 | 12.3 | 8.1 | 45000 | 31600 | 70.22% | 2.8 | 13500 | R-410A
216762911 | 2.85 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | HG37*36+TXV+AEFE4B* |  | 34200 | 19 | 12 | 9.5 | 32600 | 24000 | 73.62% | 2 | 27000 | R-454B
214394530 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | U98MV0603A17UPS | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394539 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | U98MV0603A17UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394621 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | U98MV1005A21UPS | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394632 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | U98MV1005A21UPS | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216762025 | 3 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H36HA5*** | FE*TT1*37+TXV |  | 36000 | 18 | 11.7 | 9.45 | 34400 | 29600 | 86.05% | 1.8 | 27000 | R-454B
215368038 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,G,JG84948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
210693321 | 2.83 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+MBVC1201**-1A*+TXV |  | 34000 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
210693353 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VC960804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216762921 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V60H210P16*+TXV+AEFE5* |  | 45500 | 18 | 11.7 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-454B
216762010 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | LEM60*6TT+TXV |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
216687206 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF80TV407517DZ | 45500 | 19 | 11.7 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
214389717 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA2422*4A* | G*VM970803BNB* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
214389724 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4A* | G*VS800604BUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
212985982 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *96MSN0261410A* | 17500 | 16 | 11 | 8.1 | 18200 | 16300 | 89.56% | 1.84 | 20200 | R-410A
212986986 | 1.48 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *96MSN0601412A* | 17800 | 16.5 | 10.5 | 8.1 | 17800 | 19400 | 109% | 2.34 | 12300 | R-410A
212987036 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *96MSN0601412A* | 17500 | 16.5 | 10.5 | 8.5 | 18100 | 19800 | 109.4% | 2.38 | 12500 | R-410A
216760240 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60MTB-M19E | H,GE35*48+TXV+AEFE4B* |  | 46000 | 18 | 11 | 9.5 | 46000 | 48000 | 104.3% | 2.02 | 47500 | R-454B
213356137 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A36VCA+TXV+CBPE3A* |  | 24000 | 18 | 10.5 | 8.85 | 25000 | 22600 | 90.4% | 1.9 | 18300 | R-410A
213821162 | 1.98 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24AAK | D(A,C,E)30B34+TDR | *96VTN0802120B* | 23800 | 16 | 9 | 8.5 | 25000 | 22400 | 89.6% | 2.92 | 20000 | R-410A
213360215 | 1.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*23/37Z9 | EL297UH045XV36B* | 22800 | 22 | 14.5 | 9.5 | 19600 | 19600 | 100% | 1.96 | 22400 | R-410A
213360233 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | L*35/36U9 | EL297UH090XV48C* | 22200 | 21 | 14.5 | 9.4 | 19800 | 19600 | 98.99% | 1.9 | 22600 | R-410A
213360235 | 1.85 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LH35/38X9 | EL297UH090XV48C* | 22200 | 21 | 14.5 | 9.4 | 19800 | 19600 | 98.99% | 1.9 | 22600 | R-410A
214392481 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R921V0703A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392540 | 1.68 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R951V0603A17UHU | 20200 | 17.7 | 9 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392551 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R951V0703A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392576 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R962V0403A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392592 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R962V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
213773837 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L24A*+WALLCON | *97CMN1002122B* | 24200 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
216687179 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FCCA2421HYEA | FF96TV304017M4 | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
216788579 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | H,RG34*36+TXV+AEFE3A* |  | 23600 | 20 | 12.5 | 9.45 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
216977210 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH24/37X*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977212 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP36/37R*+TXV | SL297UH060NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216057056 | 1.83 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR |  | 22000 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.67 | 18600 | R-454B
216760235 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RTB-M20S | V,G60H210P16*+TXV+AEFE5* |  | 45500 | 18 | 11.7 | 9.1 | 45500 | 33200 | 72.97% | 1.94 | 39000 | R-454B
214392193 | 1.72 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R801V0504A17UHU | 20600 | 17.8 | 9.7 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19000 | R-410A
214392327 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R802V0504A17UHN | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
216780980 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTF60C5CGS1 | Y81E080C16LMPS1 | 44500 | 18 | 12 | 9 | 44500 | 33400 | 75.06% | 2 | 33000 | R-454B
215667019 | 1.9 | No | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CTL0701412B* | 22800 | 17 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20400 | R-454B
215667717 | 1.93 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *96CTN0801714B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214394440 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | U97MV0855A21DHS | 32800 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
207820947 | 4.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV0X60A1 | TEM8B0C60V51+TDR |  | 54000 | 19.5 | 12 | 8.5 | 51000 | 37000 | 72.55% | 1.84 | 48500 | R-410A
214392448 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R921V0403A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214389660 | 3.67 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60481EA* | CA*EA6030*4A* | G*VC800804C*A* | 44000 | 17 | 10 | 8.5 | 43500 | 31000 | 71.26% | 2 | 28000 | R-410A
216624565 | 3 | Yes | Yes | GE Appliances | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | NS18H36HA5*** | FE*TT6*37+TXV |  | 36000 | 18 | 11.7 | 9.45 | 34400 | 29600 | 86.05% | 1.8 | 27000 | R-454B
216978076 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD19/36Y*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214392482 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R921V0703A17M4S | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392141 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R801V0503A14UH | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392189 | 1.72 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R801V0504A17UHU | 20600 | 17.8 | 9.7 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19000 | R-410A
214392264 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R801V1004A17UH | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
214392280 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0503A14DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392423 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R802V1004A17UHS | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392632 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | U802VA075317M | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
214392648 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | U802VA075317Z | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
213356134 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A24VBA+TXV+CBPE4B* |  | 23800 | 18 | 10 | 8.7 | 24800 | 22600 | 91.13% | 1.86 | 18200 | R-410A
212927224 | 1.98 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | L*18/36T9 | SLP98UH070XV36B* | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215667143 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *96CTN0601714B* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215667200 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CTL0701716B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16400 | 70.69% | 2 | 19700 | R-454B
214392599 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R962V0703A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392701 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | U98MV0603A17UPS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392717 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | U98MV0703A17UPS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
215389772 | 2.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3617AL* | 59TP6C060V17**16 | 34800 | 15.2 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.8 | 29600 | R-410A
215667177 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CTL0451712B* | 23800 | 17 | 10 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
215667779 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0601714B* | 23600 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 19900 | R-454B
215666977 | 1.9 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CSU0401712A* | 22800 | 16.5 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20200 | R-454B
215667827 | 2 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CSU0601716A* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
214392523 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R951V0603A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392057 | 3.63 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | U97MV1005A21DHS | 43500 | 15.3 | 10 | 8.1 | 45000 | 33800 | 75.11% | 3 | 32200 | R-410A
214392005 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | R802V1005A21UH | 44000 | 15.3 | 10 | 8.1 | 45500 | 36000 | 79.12% | 2.99 | 33600 | R-410A
215666942 | 1.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X24M14A*+WALLCON | *80CTL0701412B* | 22800 | 17 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
214392557 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R951V0703A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214391985 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | R801V1005A21UHU | 44000 | 15.3 | 10 | 8.1 | 45500 | 36400 | 80% | 3.01 | 33800 | R-410A
214392503 | 1.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R951V0403A17UHU | 21400 | 18 | 10 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392535 | 1.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R951V0603A17UHU | 21400 | 18 | 10 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392587 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R962V0603A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392605 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R962V0703A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392704 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | U98MV0603A17UPS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392203 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R801V0704A17UHU | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392204 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R801V0704A17UHU | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392235 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R801V0754A17UHN | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392252 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R801V0754A17UHS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392288 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R802V0503A14DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392304 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R802V0503A14UHN | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
213546633 | 2 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | L*35/36U9 | EL280UH070E36A* | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213546638 | 2 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | LH18/37D9 | EL280UH070E36A* | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214392443 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R921V0403A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392477 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R921V0703A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392530 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R951V0603A17M4S | 21000 | 17.9 | 9.8 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392561 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R951V0703A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392664 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | U97MV0603A17DHS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392695 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | U98MV0603A17UPS | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392696 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | U98MV0603A17UPS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
216766566 | 3.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7048A1 | 5TXCC009AS3 | S9X1C080U5PSB | 43000 | 16.5 | 12 | 8.7 | 43500 | 32000 | 73.56% | 2.21 | 29200 | R-454B
213184787 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,GE48960+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
213612274 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V,T60H210P299+AEFE5* |  | 45500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
216765116 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7060A1 | 5TXCD010AS3 | S8X2C080M5PSC | 52500 | 16.5 | 11 | 9 | 51000 | 38500 | 75.49% | 2.2 | 34000 | R-454B
214092759 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.63 | 25600 | R-410A
213281570 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E100C16SMPS1 | 34000 | 17.5 | 8.5 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
213821577 | 2.93 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36B34+TDR | *80MS(N,L)0901714A* | 35200 | 16.5 | 10 | 8.1 | 38500 | 32200 | 83.64% | 2.58 | 29400 | R-410A
213184797 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213612276 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG35948+AEFE4B* |  | 44500 | 17 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
213821584 | 2.93 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80MS(N,L)0902120A* | 35200 | 16.5 | 9.5 | 8.1 | 38500 | 32200 | 83.64% | 2.54 | 29400 | R-410A
216788577 | 2 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-36RTB-M20S | V,R36H175P15*+TXV+AEFE4B* |  | 24000 | 20 | 13 | 9.5 | 22400 | 17000 | 75.89% | 2 | 21400 | R-454B
215389812 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CNPV*4217AL* | GG96VTAB48060B** | 35400 | 15.5 | 10 | 8.5 | 38500 | 35000 | 90.91% | 1.94 | 29400 | R-410A
214092775 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9Y080C16MP11 | 32600 | 18.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.65 | 25800 | R-410A
214092792 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TMLE100C16MP11 | 33000 | 18 | 10 | 8.3 | 32800 | 29000 | 88.41% | 2.71 | 26000 | R-410A
214092823 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TPLC100C20MP13 | 32000 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214092826 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E040A12LMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.71 | 26400 | R-410A
214092842 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E080C16SMPS1 | 32400 | 18 | 10 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092857 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E100C16LMPS1 | 32400 | 18 | 9.5 | 8.5 | 33400 | 28400 | 85.03% | 2.7 | 25800 | R-410A
214092876 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | Y81E120C20LMPS1 | 32600 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
213296190 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8E080B12MP11 | 32000 | 18 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.61 | 25800 | R-410A
215667837 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0701716B* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215667885 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN0601714B* | 24000 | 17 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215747655 | 1.9 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1924MJAYCA | FHRAVM3621M*YECA |  | 22800 | 19 | 12 | 8.5 | 22800 | 19500 | 85.53% | 1.9 | 21200 | R-454B
215667433 | 1.92 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CTL0701716B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.96 | 20200 | R-454B
215667311 | 2 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *96CTN0801714B* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
216762018 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LEM60*6TT+TXV |  | 47500 | 15.2 | 10 | 8.5 | 45500 | 39000 | 85.71% | 1.85 | 39500 | R-454B
214392700 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | U98MV0603A17UPS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
215662841 | 2.9 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | FCMA5B48L0C*+WALLCON |  | 34800 | 19 | 11 | 9 | 34600 | 24600 | 71.1% | 1.96 | 29800 | R-454B
214862795 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84(1,2)60+TXV | BGH96M100D5B | 51500 | 18 | 11.7 | 8.5 | 52000 | 37400 | 71.92% | 1.85 | 37400 | R-410A
215667360 | 1.88 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X30M14A*+WALLCON | *96CTN0401410B* | 22600 | 15.5 | 9 | 8.5 | 24200 | 17100 | 70.66% | 1.84 | 20600 | R-454B
216494142 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CE(P,V)3621G34*+TXV | 88*TB48090C17*** | 32800 | 20 | 11 | 9.5 | 33000 | 26000 | 78.79% | 2.04 | 29400 | R-454B
216624584 | 2.83 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230** | LH35/36F*+TXV+LEFE4B* |  | 34000 | 15.2 | 10.5 | 8.5 | 32400 | 28400 | 87.65% | 1.75 | 26000 | R-454B
211174251 | 3.75 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)48D34+TDR | GUH97M090C3M | 45000 | 15.2 | 12.3 | 8.1 | 45000 | 31600 | 70.22% | 2.8 | 13700 | R-410A
215666959 | 1.87 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X24M14A*+WALLCON | *96CTN0401410B* | 22400 | 15.5 | 9 | 8.5 | 24600 | 17300 | 70.33% | 1.82 | 20800 | R-454B
213088727 | 3.88 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R48H175P469+AEFE4B* |  | 46500 | 18 | 11.7 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
214862796 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84(1,2)60+TXV | BGH96M120D5B | 51500 | 18 | 11.7 | 8.5 | 52000 | 37400 | 71.92% | 1.85 | 37400 | R-410A
213281448 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | V48H175P789+AEFE4B* |  | 45000 | 18 | 11.5 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
214628467 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | PL36H175P159 | 59SU5B040M17**12 | 23400 | 17 | 10 | 8.5 | 24400 | 24000 | 98.36% | 2.02 | 18000 | R-410A
216374503 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTU36B5XDS1+TXV | Y92E060B12SMPS1 | 33400 | 18 | 11 | 8.5 | 31600 | 24200 | 76.58% | 2 | 28200 | R-454B
214437579 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9V120D20MP12 | 32800 | 17 | 9.5 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
214384815 | 2.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE(D,N,U)+CM36B34+TDR |  | 32000 | 18.5 | 10.4 | 8.7 | 33200 | 26400 | 79.52% | 2.73 | 24600 | R-410A
214862793 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84(1,2)60+TXV | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
213821609 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *80VTL0902120B* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
213821611 | 2.87 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)36C34+TDR | *80VTL1102122B* | 34400 | 16.5 | 9.9 | 8.5 | 38000 | 31600 | 83.16% | 2.73 | 29000 | R-410A
213821675 | 2.83 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | D(A,C,E)42B34+TDR | *96VTN1202422B* | 34000 | 16.5 | 9.9 | 8.5 | 37800 | 31800 | 84.13% | 2.72 | 29000 | R-410A
215912373 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8V080B12MP12 | 22600 | 17 | 12 | 8.5 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
213296191 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM8E080B12MP11 | 29800 | 17.4 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.61 | 25800 | R-410A
213296192 | 2.48 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C26+TDR | TM8E080B12MP11 | 29800 | 17.4 | 9 | 8.5 | 34000 | 28000 | 82.35% | 2.61 | 25800 | R-410A
213927821 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.46 | 25800 | R-410A
213088732 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V,R60H210P199+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
213088748 | 3.92 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG84948+AEFE4B* |  | 47000 | 18 | 12 | 9.5 | 46000 | 33200 | 72.17% | 2 | 39000 | R-410A
214392305 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R802V0503A14UHN | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392337 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R802V0504A17UHN | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392352 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R802V0504A17UHS | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392368 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R802V0754A17DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392370 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R802V0754A17DZ | 21000 | 18.9 | 9.8 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392653 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | U802VA075317Z | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
213612281 | 3.83 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG48960+AEFE5* |  | 46000 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
212367402 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84948 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
216624588 | 2.83 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230** | LH18/37D*+TXV+LEFE3A* |  | 34000 | 15.2 | 10.5 | 8.5 | 32400 | 28400 | 87.65% | 1.75 | 26000 | R-454B
212361470 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36960 | BGH96M100C5A | 44500 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34600 | R-410A
212361439 | 3.75 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M120D5A | 45000 | 17 | 11.5 | 9 | 45000 | 33000 | 73.33% | 1.9 | 34600 | R-410A
216977227 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH24/37F*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214290115 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84160+TXV | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
214272381 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | V,C36H175P459 | 59TN6C080C17**14 | 32800 | 17 | 11 | 8.5 | 31400 | 25000 | 79.62% | 1.98 | 31000 | R-410A
215676035 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *97CMN0602120B* | 48500 | 19 | 10 | 9 | 50000 | 37200 | 74.4% | 1.98 | 47000 | R-454B
215676115 | 3.88 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M21A*+WALLCON | *80CTL0701716B* | 46500 | 18 | 9.5 | 9 | 50000 | 36800 | 73.6% | 1.98 | 46000 | R-454B
215675715 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0702120B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
214391690 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R962V0603A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.9 | 16000 | R-410A
215684043 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 59MN7C100C21**22 | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
216675391 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X30M17A* | *80CSU0401712A* | 24200 | 15.2 | 10 | 8.5 | 24400 | 19500 | 79.92% | 1.92 | 19000 | R-454B
212367403 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG88960 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
212367506 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,RG84948 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
216762007 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | LEM25*43G+TXV |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
213612275 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | H,TG35948+AEFE5* |  | 44500 | 18 | 11 | 9 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
215667787 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0801714B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19900 | R-454B
216624581 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | LH18/37R*+TXV+LEFE3A* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
215683873 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3717AM*+UI | 58TN*B070C14**12 | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 30800 | R-454B
212367421 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG84948 | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
214568835 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | H,PE8J936 | 59TN6B060C17**14 | 23600 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.94 | 19800 | R-410A
212367486 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | H,RG84948 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
213281367 | 1.97 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | V36H***P219+AEFE3A* |  | 23600 | 19 | 12.5 | 9.5 | 22400 | 17200 | 76.79% | 2 | 21400 | R-410A
216558396 | 2.78 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*S+CM36B36+TDR |  | 33400 | 18 | 9 | 8.5 | 35000 | 25000 | 71.43% | 2.73 | 24000 | R-410A
216558397 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*S+CM48E46+TDR |  | 34400 | 18 | 9 | 8.5 | 35000 | 25200 | 72% | 2.81 | 24000 | R-410A
215611120 | 2.85 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1936MJAYCA | FHRAVM3621M*YECA |  | 34200 | 19 | 12 | 8.5 | 34200 | 29400 | 85.96% | 2.1 | 30000 | R-454B
213281329 | 4.29 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG86960+AEFE5* |  | 51500 | 17 | 11.7 | 9.45 | 53000 | 38000 | 71.7% | 2.02 | 42500 | R-410A
216762008 | 2.83 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230** | LEM37*3TT+TXV |  | 34000 | 15.2 | 10.5 | 8.5 | 32400 | 28400 | 87.65% | 1.75 | 26000 | R-454B
216624591 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230** | LH40/61W*+TXV+LEFE5* |  | 47500 | 15.2 | 10 | 8.5 | 46000 | 38500 | 83.7% | 1.75 | 39000 | R-454B
216977168 | 1.98 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH18/36D*+TXV | SL297UH040NV36B* | 23800 | 17 | 11.7 | 8.85 | 22400 | 20400 | 91.07% | 1.78 | 18800 | R-454B
215667502 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *97CMN0801714B* | 23000 | 17 | 10 | 8.5 | 23800 | 16700 | 70.17% | 1.86 | 20200 | R-454B
215667645 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701716B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215912407 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TPLC080B12MP13 | 21600 | 17 | 11.7 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
213927874 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B3G+TXV+TDR | TM9V060B12MP12 | 32200 | 17.5 | 9.4 | 8.1 | 34000 | 27800 | 81.76% | 2.49 | 25600 | R-410A
216977198 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*18/36V*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214290116 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84160+TXV | BGH96M080C4B | 42500 | 17 | 11.7 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
216764845 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S8X1D120M5PTC | 51500 | 16.5 | 11 | 9 | 51500 | 39000 | 75.73% | 2.1 | 34400 | R-454B
216977226 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH24/37X*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977233 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH24/37X*+TXV | SL297UH080NV48C* | 34600 | 17 | 10.5 | 8.95 | 34200 | 28000 | 81.87% | 1.88 | 27600 | R-454B
216977174 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*19/36S*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977183 | 1.97 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH18/36D*+TXV | SL297UH060NV36B* | 23600 | 17 | 11.7 | 8.85 | 22400 | 20400 | 91.07% | 1.78 | 18800 | R-454B
211174173 | 3.71 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)48D34+TDR | GUH96C110C5M | 44500 | 15.4 | 12.3 | 8.3 | 45000 | 31600 | 70.22% | 2.82 | 13700 | R-410A
216678682 | 2.9 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L17A* | *97VTN0601716A* | 34800 | 15.2 | 9.5 | 8.5 | 38500 | 34800 | 90.39% | 1.75 | 29600 | R-410A
216678730 | 3.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X43L21A* | *97VTN0601716A* | 36200 | 15.5 | 10 | 8.5 | 38000 | 34400 | 90.53% | 1.96 | 29200 | R-410A
216977166 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LP36/37R*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20200 | 90.18% | 1.85 | 18800 | R-454B
216977173 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*19/36U*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977214 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*18/36V*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
213307195 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM9E080B12MP12 | 31400 | 17.4 | 9.8 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
213307211 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM9Y120D20MP11 | 31000 | 16.2 | 9.2 | 8.3 | 32200 | 28000 | 86.96% | 2.73 | 25200 | R-410A
213307363 | 2.62 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM9E080B12MP12 | 31400 | 17.4 | 9.8 | 8.1 | 33600 | 27200 | 80.95% | 2.55 | 25200 | R-410A
216977217 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH29/36F*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977231 | 2.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP25/36R*+TXV | SL297UH080NV48C* | 34800 | 17 | 11 | 8.95 | 34200 | 28000 | 81.87% | 1.9 | 27600 | R-454B
215683887 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3717AM*+UI | 59TN6C060C17**14 | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215683889 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3717AM*+UI | 59TN6C080C17**14 | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.88 | 30800 | R-454B
215683907 | 2.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 58TN*B110C21**20 | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
211174175 | 3.75 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)60B34+TDR | GUH96C110C5M | 45000 | 15.3 | 12.3 | 8.1 | 45000 | 31600 | 70.22% | 2.76 | 13700 | R-410A
216977196 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP36/37R*+TXV | SL297UH040NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977197 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH18/36D*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216978066 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LD19/36Y*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216978080 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LD42/61Y*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.84 | 38000 | R-454B
214394735 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R951V0855A21M4S | 51500 | 16.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214394753 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R962V0855A21M4S | 51500 | 16.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
216977229 | 2.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH29/36X*+TXV | SL297UH080NV48C* | 34800 | 17 | 11 | 9 | 34200 | 28000 | 81.87% | 1.9 | 27600 | R-454B
213311615 | 3.08 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | V36H175P159+CBPE4B* |  | 37000 | 16 | 10 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
213350128 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E080C16LMPS1 | 32000 | 18 | 9.9 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
216755687 | 2.6 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH30AAK | EA*5X43M21A* | *80MSU0802120A* | 31200 | 15.5 | 9.5 | 9 | 34200 | 30000 | 87.72% | 1.8 | 21200 | R-454B
214272317 | 2.63 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | PL36H175P159 | 59MN7C080C17**14 | 31600 | 17 | 11 | 8.1 | 31800 | 24200 | 76.1% | 1.88 | 30600 | R-410A
216977181 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LP36/37R*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20200 | 90.18% | 1.85 | 18800 | R-454B
216977190 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LP25/36R*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
215674463 | 3.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU0802120A* | 46000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
216977203 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*19/36S*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214627764 | 1.45 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PL36H175P159 | 59SC6A060M17**16 | 17400 | 16 | 10.5 | 8.5 | 16400 | 18300 | 111.6% | 2.24 | 11200 | R-410A
215666936 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X24M14A*+WALLCON | *80CTL0701412B* | 22800 | 17 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215667137 | 1.9 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *96CTN0601714B* | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215667421 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *80CTL0701412B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
213311617 | 3 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L159+CBPE3A* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
215667621 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701412B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215667638 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701716B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214391986 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R801V1005A21UHU | 44500 | 15.5 | 10 | 8.2 | 45500 | 36600 | 80.44% | 3.07 | 34000 | R-410A
216977202 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*19/36U*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977186 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH29/36X*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977187 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH29/36F*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977204 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP25/36R*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977221 | 2.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP29/36X*+TXV | SL297UH060NV36B* | 34400 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977177 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*30/36U*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977178 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*35/36U*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977213 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH18/36D*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977228 | 2.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP36/37R*+TXV | SL297UH080NV48C* | 34800 | 17 | 11 | 9 | 34200 | 28000 | 81.87% | 1.9 | 27600 | R-454B
215683921 | 2.87 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 59MN7C080C21**20 | 34400 | 18 | 10 | 8.1 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
214394798 | 2.73 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*030* | H,PG53936 | 59TN6C080C17**14 | 32800 | 17 | 11 | 8.5 | 31200 | 24800 | 79.49% | 1.98 | 31000 | R-410A
215667069 | 1.9 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X24M17A*+WALLCON | *80CTL0901716B* | 22800 | 17 | 10 | 9 | 24000 | 16800 | 70% | 1.96 | 20400 | R-454B
215667628 | 1.93 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CTL0701412B* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
216977184 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*18/36V*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 8.95 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977241 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LH42/62W*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.85 | 38000 | R-454B
216977232 | 2.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP29/36X*+TXV | SL297UH080NV48C* | 34800 | 17 | 11 | 9 | 34200 | 28000 | 81.87% | 1.9 | 27600 | R-454B
212362558 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VS800604BUA* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362559 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VC800604B*A* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216624587 | 2.83 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230** | L*35/36U*+TXV+LEFE4B* |  | 34000 | 15.2 | 10.5 | 8.5 | 32400 | 28400 | 87.65% | 1.75 | 26000 | R-454B
212362824 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VM971005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362840 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CSCF3642N6D*+TXV | G*VC961205DNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362790 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VC800604B*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216977171 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH29/36X*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977188 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*19/36U*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977237 | 3.71 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | L*42/60S*+TXV | SL297UH080NV60C* | 44500 | 17 | 10.5 | 8.7 | 45500 | 39000 | 85.71% | 1.8 | 38000 | R-454B
213546678 | 1.98 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | L*35/36U9 | EL296UH070XV36B* | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
214394635 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V0755A21DZ | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214394769 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U802VA125524M | 52000 | 18.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50000 | R-410A
216977225 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*35/36S*+TXV | SL297UH060NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977182 | 1.97 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH18/36R*+TXV | SL297UH060NV36B* | 23600 | 17 | 11.7 | 8.85 | 22400 | 20400 | 91.07% | 1.78 | 18800 | R-454B
216977191 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LP29/36X*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977193 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*35/36U*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977200 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH29/36X*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
204456429 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X24L17A*+WALLCON | *80CTL0901716A* | 23400 | 17 | 11 | 8.1 | 21800 | 16700 | 76.61% | 1.9 | 21000 | R-410A
204456438 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X25L17A*+WALLCON | *80CTL0451712A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16800 | 78.5% | 2 | 20800 | R-410A
216762019 | 3.96 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LEM48*1TT+TXV |  | 47500 | 15.2 | 10 | 8.5 | 45500 | 39000 | 85.71% | 1.84 | 39500 | R-454B
216977175 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LP25/36R*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977209 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*35/36S*+TXV | SL297UH040NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216978078 | 2.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD24/35Y*+TXV | SL297UH060NV36B* | 34400 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216978067 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LD24/35Z*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
215675935 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M24A*+WALLCON | *97CMN1202422B* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
214394531 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | U98MV0603A17UPS | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214391648 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R801V0754A17DZ | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.87 | 15900 | R-410A
214391657 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R802V0503A14DZ | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.84 | 15900 | R-410A
216494126 | 3.63 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)4824G1K*+TXV | 88*TB36045C17*** | 43500 | 17 | 9 | 9 | 47000 | 34600 | 73.62% | 2.02 | 42500 | R-454B
213350133 | 2.67 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y81E080C16SMPS1 | 32000 | 18 | 9.9 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
216960327 | 1.53 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A3J+TDR | S9V2B040U3PSC+LRP | 18300 | 19.3 | 11.2 | 8.5 | 22200 | 25200 | 113.5% | 2.47 | 20800 | R-454B
214440939 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG53936 | 59TN6C060C17**14 | 24000 | 20 | 13 | 10.5 | 25000 | 19400 | 77.6% | 2.52 | 23800 | R-410A
215864577 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | 5TXCB004AS3 | S8V2B080M4PCB | 31800 | 18.1 | 10 | 8.5 | 33000 | 25600 | 77.58% | 2 | 31200 | R-454B
216952900 | 4.29 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5060A1 | DH60T4J | S8X1C080M5PSC | 51500 | 15.5 | 11 | 8.1 | 50000 | 35400 | 70.8% | 2.85 | 34600 | R-454B
214395721 | 2.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36C5CDS1 | YPLC100C16MP13 | 34000 | 18 | 11 | 8.5 | 31600 | 26000 | 82.28% | 2 | 28200 | R-454B
212362622 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VC801005C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362573 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VM970803BNB* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362574 | 2.77 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VM970804CNB* | 33200 | 19 | 12 | 8.2 | 33600 | 24400 | 72.62% | 1.8 | 21400 | R-410A
212362575 | 2.77 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VM971005CNB* | 33200 | 19 | 12 | 8.2 | 33600 | 24400 | 72.62% | 1.8 | 21400 | R-410A
216978072 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD19/36Y*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
212362793 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VC800805C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362776 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VC960603BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215667214 | 2 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CTL0701716B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16400 | 70.69% | 2 | 19700 | R-454B
215667747 | 1.97 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *80CTL0451712B* | 23600 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215667867 | 2 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *80CTL0902120B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
216977169 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*18/36V*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 8.95 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
213281443 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | V60H210P299+AEFE5* |  | 45500 | 18 | 11.7 | 9.35 | 46000 | 33200 | 72.17% | 1.98 | 39000 | R-410A
214239018 | 2.67 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | END4X42L17**+WALLCON | *97CMN0801714B* | 32000 | 16.5 | 11 | 8.1 | 33200 | 24800 | 74.7% | 1.88 | 31600 | R-410A
216977185 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*18/36T*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 8.95 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216679416 | 1.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X36L17A* | *97VTN0601716A* | 23600 | 17 | 10 | 9 | 25800 | 23200 | 89.92% | 1.82 | 18900 | R-410A
216679836 | 3 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X37L17A* | *97VTN0801716A* | 36000 | 15.2 | 10 | 8.5 | 38500 | 34600 | 89.87% | 1.92 | 29400 | R-410A
216681036 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *97VTN0802120A* | 35600 | 16 | 10 | 8.5 | 38500 | 34600 | 89.87% | 1.75 | 29400 | R-410A
207573546 | 2.73 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | FG82936 | *80CSU0401712A* | 32800 | 17 | 11.5 | 8.1 | 31200 | 27600 | 88.46% | 2.22 | 30800 | R-410A
216978075 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD19/36Z*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
204456627 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L17A*+WALLCON | *97CMN0601714A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.92 | 20800 | R-410A
204456645 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L17A*+WALLCON | *80CTL0701412A* | 23600 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
216977189 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*19/36S*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
215667476 | 1.92 | No | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X30M17A*+WALLCON | *97CMN0601714B* | 23000 | 16.5 | 10 | 8.5 | 24000 | 16800 | 70% | 1.86 | 20200 | R-454B
215667671 | 1.92 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *97CMN0601714B* | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.98 | 20000 | R-454B
215667760 | 1.98 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X37M17A*+WALLCON | *80CTL0701716B* | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
216764865 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D010AS3 | S8X2C080M5PSC | 52500 | 16.5 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 34000 | R-454B
216764897 | 4.38 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5TXCD010AS3 | S8X1C100M5PTC | 52500 | 16.5 | 11.2 | 9 | 51000 | 38500 | 75.49% | 2.2 | 34200 | R-454B
213881427 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L159 | 58TP*B070V17**16 | 35000 | 16 | 9.5 | 8.5 | 36200 | 34400 | 95.03% | 2.02 | 28000 | R-410A
207573590 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | FG80936 | *80CTL0901716A* | 32400 | 18 | 11.5 | 8.1 | 30800 | 27200 | 88.31% | 2.2 | 30400 | R-410A
216978071 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD19/36Z*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214609615 | 3.05 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P299 | 58SU*B060M17**16 | 36600 | 16 | 10 | 8.5 | 36400 | 34400 | 94.51% | 2.08 | 28000 | R-410A
214391653 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R801V1004A17UHN | 22400 | 16 | 11.9 | 8.3 | 23000 | 17000 | 73.91% | 3.03 | 16300 | R-410A
214391669 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R802V1004A17UHN | 22400 | 16 | 11.9 | 8.3 | 23000 | 17000 | 73.91% | 3.04 | 16300 | R-410A
214392003 | 3.63 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | R802V1005A21DZ | 43500 | 15.4 | 10 | 8.1 | 45500 | 36000 | 79.12% | 2.99 | 33600 | R-410A
216977205 | 2.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP29/36X*+TXV | SL297UH040NV36B* | 34400 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
212434806 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AD-32(P,U)*****9 | TM8E080C16MP11 | 33000 | 18 | 10 | 8.5 | 32400 | 22800 | 70.37% | 2.04 | 25000 | R-410A
214836555 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y91E080B12SMPS1 | 31000 | 16.9 | 10 | 8.5 | 32200 | 22600 | 70.19% | 1.8 | 25200 | R-410A
204456357 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X24L14A*+WALLCON | *80CTL0701412A* | 23400 | 17 | 10.5 | 8.1 | 22000 | 16800 | 76.36% | 1.9 | 21000 | R-410A
204456456 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X25L17A*+WALLCON | *96CTN0601714A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
215375225 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R801V1005A21DZ | 45500 | 16 | 10 | 8.1 | 45500 | 32200 | 70.77% | 2.4 | 25200 | R-410A
215668772 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0801714B* | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30600 | R-454B
215935780 | 2.87 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X36M21A*+WALLCON | *96CTN1002122B* | 34400 | 21 | 12 | 8.5 | 38500 | 28000 | 72.73% | 2.06 | 32000 | R-454B
215936480 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *95CSU0802120B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215936750 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X60M24A*+WALLCON | *80CTL0702120B* | 35400 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
216796513 | 2.52 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X1A040M3PTC | 30200 | 15.5 | 11.7 | 8.1 | 30400 | 21800 | 71.71% | 2.89 | 21200 | R-454B
216977211 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH24/37F*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
215667923 | 2 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0601714B* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2 | 19700 | R-454B
216684003 | 4.75 | Yes | Yes | PIONEER | HSP-A (Single-Package Heat Pump Air-Source) | Centrally-Ducted | PRD-60HWD1N10-M18G |  |  | 57000 | 19 | 11.2 | 9 | 57000 | 40000 | 70.18% | 1.85 | 43000 | R-454B
212989139 | 1.95 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X24L17A* | *95MSU0601716A* | 23400 | 17 | 10 | 9 | 26800 | 26400 | 98.51% | 2.24 | 19400 | R-410A
212361586 | 3.67 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE35(1,2)48+TXV | BGH96M100C5A | 44000 | 17 | 11.5 | 8.8 | 44500 | 32400 | 72.81% | 1.9 | 34000 | R-410A
215674103 | 3.67 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0602120B* | 44000 | 17 | 9.5 | 9 | 49000 | 34600 | 70.61% | 2.04 | 43000 | R-454B
215674153 | 3.67 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN1002122B* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.04 | 42500 | R-454B
215667928 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0801714B* | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215674003 | 3.71 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0802120A* | 44500 | 18 | 9.5 | 9 | 48500 | 34000 | 70.1% | 2.06 | 42500 | R-454B
215674303 | 3.83 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0601716A* | 46000 | 18 | 9.5 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
214239318 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EN(A,D)4X48L24**+WALLCON | *97CMN1002122B* | 32400 | 17 | 11.7 | 8.1 | 32600 | 24600 | 75.46% | 1.96 | 31400 | R-410A
215654046 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | TM8V080C16MP12 | 41000 | 17 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
213772357 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *97CMN1002122B* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
214391655 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R801V1004A17UHS | 22400 | 16 | 11.9 | 8.3 | 23000 | 17000 | 73.91% | 3.03 | 16300 | R-410A
214391662 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R802V0504A17UHS | 22400 | 16 | 11.9 | 8.3 | 23000 | 17200 | 74.78% | 3.06 | 16400 | R-410A
216978070 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LD24/35Z*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
214392791 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R801V0504A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392809 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R801V0504A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214392868 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R801V0754A17DZ | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216612213 | 1.85 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | 5TXCB006AS3 | S9V2B060U4VSB+LRP | 22200 | 21.4 | 12 | 10 | 22600 | 18200 | 80.53% | 2.2 | 22200 | R-454B
207573727 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG36948 | *95CSU1002122A* | 45000 | 17 | 10 | 8.5 | 45000 | 32400 | 72% | 2.28 | 36000 | R-410A
216766636 | 4.25 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR7060A1 | 5PX*D008AS3 | S9X2D120U5PSB | 51000 | 15.2 | 11.2 | 8.7 | 51500 | 39000 | 75.73% | 2.19 | 34000 | R-454B
214650286 | 4.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTU60D5XHS1+TXV | TM9E120D20MP12 | 53500 | 19 | 11 | 8.5 | 54500 | 39500 | 72.48% | 2 | 37800 | R-454B
214650319 | 3.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTU60D5XGS1+TXV | Y81E130D20SMPS1 | 45000 | 18 | 12 | 9 | 45000 | 33200 | 73.78% | 2 | 32400 | R-454B
207573587 | 2.68 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | PL36H175P159 | *80CTL0901716A* | 32200 | 18 | 11.5 | 8.1 | 30800 | 27200 | 88.31% | 2.2 | 30400 | R-410A
207573589 | 2.67 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | FG35936 | *80CTL0901716A* | 32000 | 18 | 11 | 8.1 | 30800 | 27200 | 88.31% | 2.2 | 30400 | R-410A
214391871 | 3.21 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | CP49B34+TDR | R801V1005A21DZ | 38500 | 15.3 | 10 | 8.1 | 40000 | 30000 | 75% | 2.96 | 28600 | R-410A
204456609 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L17A*+WALLCON | *96CTN0601714A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.92 | 20800 | R-410A
216977219 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*19/36S*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977222 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*30/36U*+TXV | SL297UH060NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977170 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*18/36T*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 8.95 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977235 | 3.71 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LH42/60D*+TXV | SL297UH080NV60C* | 44500 | 17 | 10.5 | 8.7 | 45500 | 39000 | 85.71% | 1.8 | 38000 | R-454B
214572779 | 2.68 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4821AL*+UI | 935CB60080C21*** | 32200 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214572799 | 2.68 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4821AL*+UI | 987MC60060C21*** | 32200 | 17 | 11 | 8.5 | 32600 | 25200 | 77.3% | 1.96 | 31600 | R-410A
214836554 | 2.57 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y91E060B12SMPS1 | 30800 | 16.4 | 10 | 8.5 | 32000 | 22400 | 70% | 1.8 | 25000 | R-410A
216505459 | 2.62 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | AE*S+CM36B34+TDR |  | 31400 | 17 | 10 | 8.1 | 32200 | 26400 | 81.99% | 2.75 | 24000 | R-410A
214573199 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CSPH*4812AL*+UI | 935CB60080C21*** | 32600 | 17.5 | 11 | 8.5 | 32800 | 25000 | 76.22% | 1.98 | 31600 | R-410A
214573399 | 2.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CNPV*4221AL*+UI | 987MC60060C21*** | 31600 | 16.5 | 11 | 8.1 | 33200 | 24600 | 74.1% | 1.86 | 31600 | R-410A
213772645 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | CAP**2417AL*+UI | 58TN*B090C17**16 | 23400 | 16.5 | 10.5 | 8.1 | 21800 | 16800 | 77.06% | 1.88 | 21000 | R-410A
212390909 | 1.87 | Yes | No | DUCANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4HP18V36P | A(E,F)W304+TDR |  | 22400 | 15.2 | 11.7 | 8.1 | 22000 | 24000 | 109.1% | 2.71 | 20000 | R-410A
216977220 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LP25/36R*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214393191 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R802V0504A17UHN | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393202 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R802V0504A17UHN | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393220 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R802V0504A17UHS | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393261 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R802V0754A17DZ | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216487480 | 3.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)6024G48*+TXV | 88*TB60070C21*** | 45000 | 18 | 10 | 9 | 45500 | 33200 | 72.97% | 2.08 | 41000 | R-454B
216487493 | 3.71 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)4821G1K*+TXV | 88*TB60090C21*** | 44500 | 18 | 9.5 | 9 | 46500 | 33600 | 72.26% | 2.06 | 41500 | R-454B
216978074 | 2.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD24/35Y*+TXV | SL297UH040NV36B* | 34400 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
205301886 | 4.33 | No | Yes | PIONEER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YD060GMFI20MR2 | DC060GMFI20HT2 |  | 52000 | 18 | 11.7 | 9.5 | 55000 | 38500 | 70% | 2.02 | 43500 | R-410A
215674453 | 3.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN1002122B* | 46000 | 18 | 10 | 9 | 47500 | 33800 | 71.16% | 2.08 | 42000 | R-454B
216977223 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*30/36S*+TXV | SL297UH060NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214391982 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R801V1005A21UHN | 44500 | 15.5 | 10 | 8.2 | 45500 | 36400 | 80% | 3.06 | 33800 | R-410A
204456672 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *80CTL0701716A* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20800 | R-410A
215375210 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R801V0755A21DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375108 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R801V0504A17UHU | 33000 | 18 | 10 | 8.1 | 34200 | 31600 | 92.4% | 1.9 | 29800 | R-410A
216797142 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S8V2B080M4PCB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
216797144 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S8V2B080M4PDB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
215399949 | 1.88 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.69 | 18700 | R-454B
215912368 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TM8E100B12MP11 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215912401 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TP9C060B12MP13 | 21600 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215912402 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TP9C060B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
215912403 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TP9C060B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
207573714 | 3.79 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG86960 | *80CTL1352422A* | 45500 | 17 | 10.5 | 8.1 | 44000 | 31400 | 71.36% | 2.26 | 35000 | R-410A
213205276 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)36B34+TDR | *80ES(N,L)1552420A* | 29600 | 15.2 | 9 | 8.1 | 33800 | 24000 | 71.01% | 2.7 | 23400 | R-410A
213613577 | 1.9 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24B4 |  | 22800 | 15.5 | 9.4 | 8.8 | 25400 | 22600 | 88.98% | 2.84 | 20200 | R-410A
216057057 | 1.88 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.72 | 18700 | R-454B
216487578 | 4.58 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | CE(P,V)6024G48*+TXV | 987MC66120C24*** | 55000 | 18 | 9 | 8.5 | 57500 | 41000 | 71.3% | 1.9 | 50000 | R-454B
212927474 | 1.9 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-36HDN1-M20G | CP2505A+TXV+TD |  | 22800 | 17 | 12 | 9.3 | 22400 | 17200 | 76.79% | 1.96 | 21400 | R-410A
216487645 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)6021G48*+TXV | 88*TB48070C17*** | 43500 | 20 | 10.5 | 9 | 47000 | 37000 | 78.72% | 2 | 39500 | R-454B
215375284 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R802V1255A24UHS | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375302 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R921V1005A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
204459234 | 1.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X30AAL+WALLCON | *80CTL0701412A* | 23800 | 16 | 10.5 | 8.1 | 21800 | 16700 | 76.61% | 1.98 | 20800 | R-410A
204459243 | 1.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X30AAL+WALLCON | *80CTL0901716A* | 23800 | 16 | 10.5 | 8.1 | 21800 | 16700 | 76.61% | 1.98 | 20800 | R-410A
213546869 | 1.98 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | L*35/36U9 | SLP98UH070XV36B* | 23800 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216504991 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A36+TDR | Y91E080C20SMPS1 | 32800 | 16 | 8.5 | 8.1 | 36000 | 26800 | 74.44% | 2.78 | 25600 | R-410A
216505462 | 2.88 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*L+CM48C34+TDR |  | 34600 | 18 | 9 | 8.5 | 35000 | 25200 | 72% | 2.81 | 24000 | R-410A
215912417 | 1.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Y82E080B12LMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
215912420 | 1.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Y91E026A08SMPS1 | 20800 | 17.5 | 11.7 | 8.1 | 22800 | 17300 | 75.88% | 2 | 17600 | R-454B
215912434 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | YP9C080B12MP13 | 22200 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216056280 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TL9E060B12UH11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216056346 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE100B12MP11 | 22000 | 17 | 12 | 8.1 | 22600 | 18000 | 79.65% | 2 | 18200 | R-454B
216056379 | 1.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Y91E040A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17800 | 78.07% | 2 | 18300 | R-454B
216056448 | 1.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Y81E040A12SMPS1 | 20600 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18300 | R-454B
216056495 | 1.88 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | YP9C080B12MP13 | 22600 | 17 | 12 | 8.5 | 22800 | 18300 | 80.26% | 2 | 18500 | R-454B
213307137 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVB-60HDN1-M20G | HG2K948+AEFE5* |  | 45500 | 18 | 11.7 | 9.15 | 46000 | 33200 | 72.17% | 1.94 | 39000 | R-410A
215375244 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D34+TDR | R801V1255A24UH | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375258 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B44+TDR | R802V0755A21UHS | 44000 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375192 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R951V0855A21M4S | 33000 | 18 | 10 | 8.1 | 34200 | 31400 | 91.81% | 1.9 | 29600 | R-410A
206133759 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L17A*+WALLCON | *95CSU0601716A* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.92 | 20800 | R-410A
211257333 | 1.54 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PF4MN*B24L* |  | 18500 | 15.5 | 10.5 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
211259757 | 1.52 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 82*TA36070V14*** | 18200 | 16.5 | 11 | 8.5 | 18100 | 17600 | 97.24% | 2.14 | 12200 | R-410A
211259964 | 1.53 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 912SD30040E14*** | 18400 | 15.5 | 10.5 | 8.5 | 18500 | 17600 | 95.14% | 2.12 | 12400 | R-410A
211260055 | 1.55 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | OVMAAB042112 | 18600 | 15.5 | 10.5 | 8.5 | 18700 | 17500 | 93.58% | 2.12 | 12600 | R-410A
216487310 | 1.9 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)2417G31*+TXV | 88*TB36070C14*** | 22800 | 17 | 10 | 9 | 23000 | 16400 | 71.3% | 1.96 | 19400 | R-454B
216487812 | 1.88 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)3614G34*+TXV | 986TD66100C21*** | 22600 | 17 | 9.5 | 9 | 22000 | 15900 | 72.27% | 2.02 | 18600 | R-454B
212362624 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VS960603BUA* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216487744 | 4.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | CE(P,V)6024G48*+TXV | 88*TB60110C21*** | 55500 | 19 | 11 | 8.5 | 58500 | 46000 | 78.63% | 2.02 | 46500 | R-454B
216487761 | 4.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN060**AA* | CE(P,V)6024G48*+TXV | 987MC66120C24*** | 55500 | 18 | 11 | 8.5 | 58500 | 45500 | 77.78% | 2.06 | 46000 | R-454B
214574049 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**6024AL*+UI | 935CB66100C21*** | 32800 | 17.5 | 11.5 | 8.5 | 31600 | 24800 | 78.48% | 2 | 31000 | R-410A
215674220 | 3.75 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *95CSU0802120B* | 45000 | 17.5 | 9.5 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
215674370 | 3.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0902120B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
216494116 | 2.77 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | CE(P,V)3621G34*+TXV | 88*TB60070C21*** | 33200 | 18 | 9.5 | 9 | 33400 | 24600 | 73.65% | 1.88 | 29200 | R-454B
216494102 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN024**AA* | CE(P,V)3621G34*+TXV | 88*TB48070C17*** | 23200 | 17 | 10 | 9 | 22600 | 16200 | 71.68% | 1.98 | 19000 | R-454B
214391872 | 3.25 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ42AJ2N | CP61B34+TDR | R801V1005A21DZ | 39000 | 15.5 | 10 | 8.2 | 40000 | 30000 | 75% | 3.01 | 28600 | R-410A
214391633 | 1.39 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ18AJ2N | CP31A34+TDR | U802VA050317M | 16700 | 15.5 | 11.8 | 8.2 | 17200 | 12200 | 70.93% | 2.7 | 11900 | R-410A
214393745 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R951V0403A17M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393752 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R951V0403A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393802 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R951V0603A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393829 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R951V0603A17UHU | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214395986 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTM60C5CHS1 | TM8Y120C20MP11 | 54000 | 19 | 11 | 9 | 55000 | 39500 | 71.82% | 2 | 38000 | R-454B
214391610 | 1.39 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ18AJ2N | CP31A34+TDR | R801V0503A14DZ | 16700 | 15.5 | 11.8 | 8.3 | 17200 | 12200 | 70.93% | 2.72 | 11900 | R-410A
213613576 | 1.83 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24A4 |  | 22000 | 15.3 | 9.3 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
211259759 | 1.51 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 82*TA48090V17*** | 18100 | 16.5 | 11 | 8.5 | 18100 | 17700 | 97.79% | 2.14 | 12200 | R-410A
211259762 | 1.52 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 926TB36040V17*** | 18200 | 15.5 | 10.5 | 8.5 | 18300 | 17600 | 96.17% | 2.12 | 12300 | R-410A
216494155 | 3.58 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)4824G1K*+TXV | 88*TB48070C17*** | 43000 | 20 | 10.5 | 9 | 46500 | 36800 | 79.14% | 2 | 39000 | R-454B
214574069 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**6024AL*+UI | 987MC60080C21*** | 32800 | 17.5 | 11.5 | 8.5 | 31600 | 24800 | 78.48% | 2 | 31000 | R-410A
215935246 | 2.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *95CSU0802120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.04 | 32800 | R-454B
215935366 | 2.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X60M24A*+WALLCON | *80CTL1352422B* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28400 | 74.74% | 2.04 | 32600 | R-454B
215935196 | 2.97 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0702120B* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 33200 | R-454B
214282654 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LEM3793TT |  | 33400 | 20 | 13 | 9.1 | 34400 | 26200 | 76.16% | 1.92 | 32800 | R-410A
216487913 | 4.13 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 291VAN054**AA* | CE(P,V)6021G48*+TXV | 986TD66120C24*** | 49500 | 19 | 11.5 | 10.5 | 50500 | 53000 | 105% | 1.96 | 49500 | R-454B
215375075 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R801V0504A17UHN | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
213613581 | 1.5 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M24F4 |  | 18000 | 15.2 | 9.5 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
214393904 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R951V0855A21M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394038 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R962V0603A17M4S | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214397258 | 2.78 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTF36B5CDS1 | TM9Y080B12MP11 | 33400 | 18 | 11 | 8.5 | 31400 | 25600 | 81.53% | 2 | 27800 | R-454B
216978079 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LD42/61Z*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.84 | 38000 | R-454B
216761970 | 2.07 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | H,PG9J936 | 927TA60080V21*** | 24800 | 16 | 10 | 9 | 23200 | 19000 | 81.9% | 2.14 | 19000 | R-410A
207573742 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | PL48H210P299 | *96CTN1002122A* | 44500 | 17 | 10 | 8.5 | 44500 | 34600 | 77.75% | 2 | 34600 | R-410A
213612048 | 2.28 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ30AJ2N | D(A,C,E)36A34+TDR | R962V0603A17M4S | 27400 | 15.4 | 11.7 | 8.1 | 28400 | 21000 | 73.94% | 2.63 | 20200 | R-410A
214394438 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | U97MV0855A21DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
214392507 | 1.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R951V0403A17UHU | 21400 | 18 | 10 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392509 | 1.72 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R951V0403A17UHU | 20600 | 17.8 | 9.7 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392514 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | R951V0403A17UHU | 20800 | 17.9 | 9.8 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392573 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R962V0403A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392593 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R962V0603A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392125 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R801V0503A14DZ | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392205 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R801V0704A17UHU | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
213821552 | 2.47 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | D(A,C,E)30D44+TDR | *96VTN1002122B* | 29600 | 15.2 | 9 | 8.1 | 34200 | 24200 | 70.76% | 2.65 | 23600 | R-410A
214440959 | 2.02 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | H,PG53936 | 59TN6C100C21**22 | 24200 | 20 | 13.5 | 10.5 | 24800 | 19200 | 77.42% | 2.56 | 23600 | R-410A
216794246 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | L8V1B080U4VSB+LRP | 19500 | 20.9 | 11.2 | 10 | 22200 | 21800 | 98.2% | 2.91 | 27000 | R-454B
216794275 | 1.64 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S8V2B080M4PDB | 19700 | 21.5 | 11 | 9.5 | 22400 | 22000 | 98.21% | 2.84 | 27200 | R-454B
216794307 | 1.63 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X24A1 | D(A,C,E)30A4J+TDR | S9V2B060U4PSC+LRP | 19600 | 21 | 11.2 | 10 | 22200 | 21800 | 98.2% | 2.93 | 27000 | R-454B
215223137 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PE9J936 | 987MB66120C24*** | 23800 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.96 | 19800 | R-410A
215223138 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | H,PG9J930 | 987MC42060C17*** | 23600 | 16 | 11 | 8.1 | 20000 | 16300 | 81.5% | 1.94 | 19800 | R-410A
216644584 | 1.52 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X30M17A* | OLV098A12* | 18200 | 15.2 | 11 | 9.5 | 20400 | 18400 | 90.2% | 1.94 | 15500 | R-454B
216374520 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTU36B5XDS1+TXV | Y92E080B12SMPS1 | 23000 | 18 | 12 | 9.5 | 23000 | 17500 | 76.09% | 2 | 17600 | R-454B
212632729 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD30/36Z9 | SL280DF080NV60C* | 33400 | 20 | 13 | 8.6 | 34400 | 28800 | 83.72% | 1.76 | 32800 | R-410A
212632763 | 2.75 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD19/36Y9 | SLP99DF090XV60C* | 33000 | 20 | 12.5 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 33000 | R-410A
212632765 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD30/36Z9 | SLP99DF090XV60C* | 33400 | 20 | 13 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 33000 | R-410A
214269144 | 3.54 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG84960 | BGH96M080B3B | 42500 | 17 | 11.7 | 8.8 | 41500 | 30600 | 73.73% | 1.9 | 34000 | R-410A
215389773 | 2.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | CAP**3617AL* | GG96VTAB48060B** | 34800 | 15.2 | 9.5 | 8.1 | 38500 | 35200 | 91.43% | 1.8 | 29600 | R-410A
216977207 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*30/36S*+TXV | SL297UH040NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977218 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*19/36U*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977234 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH24/37F*+TXV | SL297UH080NV48C* | 34600 | 17 | 10.5 | 8.95 | 34200 | 28000 | 81.87% | 1.88 | 27600 | R-454B
216978068 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LD19/36Z*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
214392216 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R801V0754A17DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392284 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R802V0503A14DZ | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2 | 18900 | R-410A
214392300 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R802V0503A14UHN | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
215375358 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R802V0755A21UHS | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 50500 | 93.52% | 1.75 | 49500 | R-410A
213772407 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *96CTN1002122B* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
213772527 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *97CMN1002122B* | 24200 | 16 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
216762703 | 2.88 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AA3* | H,PG9J936 | 927TA60080V21*** | 34600 | 15.2 | 10 | 9.5 | 34600 | 26800 | 77.46% | 2.22 | 24200 | R-410A
216761969 | 2.03 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | H,PG7J936 | 927TA60080V21*** | 24400 | 16 | 9.5 | 9 | 23200 | 19000 | 81.9% | 2.14 | 19000 | R-410A
215375083 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R802V0503A14DZ | 21600 | 17 | 10 | 8.1 | 22600 | 18900 | 83.63% | 2 | 16800 | R-410A
215375267 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1005A21UHN | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
216679864 | 2.92 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X42L21A* | *97VTN0801716A* | 35000 | 15.5 | 9.8 | 8.5 | 38500 | 34600 | 89.87% | 1.76 | 29400 | R-410A
216681018 | 2.9 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X36L21A* | *97VTN0802120A* | 34800 | 16 | 9.8 | 8.5 | 38500 | 34800 | 90.39% | 1.75 | 29400 | R-410A
216643197 | 1.53 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X25M17A* | *80MS(N,L)0451412A* | 18300 | 15.2 | 11.5 | 10.5 | 19800 | 17500 | 88.38% | 2 | 14800 | R-454B
215912430 | 1.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Y91E080B12SMPS1 | 22400 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216797131 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | *UHMD120CCV5+LRP | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.86 | 51500 | R-454B
216797138 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S8V2B060M4PCB | 45000 | 18 | 9.8 | 8.5 | 46000 | 46000 | 100% | 2.65 | 52000 | R-454B
216797165 | 3.75 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)48C3J+TDR | S9V2C100D4VSB+LRP | 45000 | 17.5 | 10 | 8.1 | 45000 | 45000 | 100% | 2.61 | 51000 | R-454B
216797172 | 3.75 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X48A1 | D(A,C,E)60B3J+TDR | S9V2C100U5PSC+LRP | 45000 | 18 | 9.8 | 8.5 | 45500 | 45500 | 100% | 2.8 | 51500 | R-454B
216056217 | 1.65 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TMLE040A12MP11 | 19800 | 16 | 11.2 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216056260 | 1.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Y91E060A10SMPS1 | 19600 | 17 | 11.2 | 8.5 | 23000 | 17600 | 76.52% | 2 | 18200 | R-454B
216056367 | 1.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Y81E100B12SMPS1 | 20400 | 18.7 | 11.2 | 9.5 | 22600 | 18000 | 79.65% | 2 | 18300 | R-454B
214573679 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**3721AL*+UI | 935CB60080C21*** | 32800 | 17.5 | 11 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
214573729 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**4221AL*+UI | 88*TB60070C21*** | 31800 | 17 | 11 | 8.5 | 33000 | 24400 | 73.94% | 1.9 | 31400 | R-410A
214574129 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**6121AL*+UI | 987MC60080C21*** | 33200 | 17.5 | 11.5 | 8.5 | 32000 | 24800 | 77.5% | 2 | 31200 | R-410A
214574349 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CSPH*4812AL*+UI | 935CB66100C21*** | 32600 | 17.5 | 11 | 8.5 | 32600 | 24800 | 76.07% | 1.98 | 31600 | R-410A
214574399 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CSPH*6012AL*+UI | 935CB60080C21*** | 33000 | 17 | 11 | 8.5 | 32200 | 25000 | 77.64% | 2 | 31400 | R-410A
213771947 | 1.98 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X30AAL+WALLCON | *80CTL0901716B* | 23800 | 16 | 10.5 | 8.1 | 21800 | 16800 | 77.06% | 1.96 | 21000 | R-410A
214572829 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4824AL*+UI | 88*TB60070C21*** | 32400 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214572849 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4824AL*+UI | 935CB66100C21*** | 32400 | 17.5 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 2 | 31400 | R-410A
216643531 | 1.48 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X30M17A* | *80MSU0401712A* | 17800 | 15.2 | 11 | 9.5 | 20000 | 18100 | 90.5% | 1.92 | 15300 | R-454B
207573775 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG36960 | *97CMN1002122A* | 44500 | 17 | 10 | 8.5 | 44500 | 34600 | 77.75% | 2 | 34600 | R-410A
216056741 | 3.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9V120D20MP12 | 40000 | 17.5 | 11.2 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
213548664 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | L*23/37Z9 | SLP98UH090XV60C* | 33600 | 21 | 13 | 8.6 | 32800 | 26200 | 79.88% | 1.8 | 29600 | R-410A
216056071 | 1.67 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | TL8E060A12UH11 | 20000 | 17.5 | 11.2 | 8.5 | 22600 | 17900 | 79.2% | 2 | 18100 | R-454B
216056153 | 1.78 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | YP9C080B12MP13 | 21400 | 17 | 9.8 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18300 | R-454B
216056156 | 1.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | YPLC080B12MP13 | 21000 | 17 | 9.8 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216056186 | 1.64 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E026A08MP12 | 19700 | 16 | 10 | 9 | 23000 | 17600 | 76.52% | 2 | 17900 | R-454B
216056337 | 1.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TMLE040A12MP11 | 20600 | 16.5 | 11.2 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216056353 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TP9C080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18400 | R-454B
216762020 | 4 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LEM60*7TT+TXV |  | 48000 | 15.2 | 10 | 8.5 | 45500 | 39000 | 85.71% | 1.85 | 39000 | R-454B
215375319 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R951V1005A21M4S | 44000 | 15.2 | 10 | 8.1 | 45500 | 32600 | 71.65% | 2.3 | 25600 | R-410A
213780937 | 2.72 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X37L21A*+WALLCON | *96CTN0601714B* | 32600 | 17 | 11 | 8.1 | 33000 | 25400 | 76.97% | 1.94 | 32000 | R-410A
214393742 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R951V0403A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393755 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R951V0403A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393842 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R951V0603A17UHU | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393188 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R802V0504A17UHN | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393588 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R921V0403A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393589 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R921V0403A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393641 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R921V0703A17M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393692 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R921V0855A21M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216056355 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | TPLC080B12MP13 | 22000 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216056389 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Y91E080B12SMPS1 | 22000 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
216056473 | 1.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.5 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
216056571 | 1.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216056574 | 1.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E040A10MP12 | 21000 | 17 | 10.5 | 9 | 23000 | 18100 | 78.7% | 2 | 18400 | R-454B
216681535 | 1.95 | No | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X24AAL | *97VTN0802120A* | 23400 | 16 | 9.8 | 9 | 26000 | 23800 | 91.54% | 1.86 | 19100 | R-410A
216681568 | 1.98 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X36L21** | *97VTN0802120A* | 23800 | 17 | 10.5 | 9 | 26000 | 23200 | 89.23% | 1.82 | 19000 | R-410A
215938399 | 3.79 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X60M24A*+WALLCON | *96CTN1202422B* | 45500 | 20.5 | 11.5 | 8.1 | 52500 | 38000 | 72.38% | 1.95 | 43000 | R-454B
216436713 | 1.82 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVA-36HDN1-M20G | L(E,F)W30F4 |  | 21800 | 19 | 11.7 | 9 | 23600 | 17600 | 74.58% | 2 | 22400 | R-410A
213281312 | 3.71 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | PL48H175P159+AEFE4B* |  | 44500 | 18 | 11 | 9.05 | 45500 | 33200 | 72.97% | 1.92 | 39000 | R-410A
212361433 | 3.46 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HE36(1,2)60+TXV | BGH96M080C4A | 41500 | 16 | 11.5 | 8.8 | 42500 | 31000 | 72.94% | 1.9 | 34000 | R-410A
214392044 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | U802VA075421Z | 44000 | 15.5 | 10 | 8.2 | 45000 | 34200 | 76% | 3.06 | 32400 | R-410A
214391974 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R801V0755A21UH | 44500 | 15.5 | 10 | 8.2 | 45500 | 37000 | 81.32% | 3.08 | 34200 | R-410A
214394026 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R962V0603A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394058 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R962V0703A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394391 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | U97MV0603A17DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216762014 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LEM25*43G+TXV |  | 24000 | 16 | 11.7 | 9 | 22400 | 22200 | 99.11% | 1.8 | 18600 | R-454B
214394441 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | U97MV0855A21DHS | 33400 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
214573869 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**4321AL*+UI | 935CB66100C21*** | 33000 | 17.5 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 2 | 31600 | R-410A
204456790 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *80CTL0901716A* | 23600 | 17.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
204456826 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L17A*+WALLCON | *80CTL0701716A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
211260173 | 1.49 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2414AL* | 915SB30026E14*** | 17900 | 15.5 | 10.5 | 8.5 | 19000 | 18900 | 99.47% | 2.26 | 12600 | R-410A
214573899 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**4321AL*+UI | 986TD60080C21*** | 33000 | 18.5 | 11.5 | 8.5 | 32600 | 25000 | 76.69% | 2 | 31600 | R-410A
215399947 | 1.8 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR |  | 21600 | 15.2 | 11 | 8.1 | 22600 | 21200 | 93.81% | 2.63 | 18600 | R-454B
215295439 | 2.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG48936 | *96VTN0801716B* | 35600 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.98 | 28200 | R-410A
215295448 | 2.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE9J936 | *96VTN0801716B* | 34600 | 16 | 9.5 | 8.1 | 36200 | 34400 | 95.03% | 2 | 28000 | R-410A
215295475 | 2.92 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HE35936 | *96VTN0802120A* | 35000 | 16 | 9.5 | 8.1 | 36800 | 34600 | 94.02% | 1.86 | 28400 | R-410A
215295516 | 3 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE36936 | *96VTN0802120B* | 36000 | 16 | 10 | 8.5 | 36400 | 34400 | 94.51% | 2.04 | 28000 | R-410A
216487662 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)6024G48*+TXV | 88*TB60070C21*** | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
214052876 | 1.83 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | HG80936 | SL280UH070V36A* | 22000 | 21 | 13.5 | 9.55 | 19800 | 19600 | 98.99% | 1.98 | 22400 | R-410A
216760237 | 2.8 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60RXB-M15S | V,G36H175D14*+TXV+AEFE4B* |  | 33600 | 16 | 11.5 | 8.35 | 32600 | 33800 | 103.7% | 1.78 | 33200 | R-454B
216056383 | 1.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Y91E060A10SMPS1 | 20600 | 17.5 | 11 | 8.1 | 22800 | 17600 | 77.19% | 2 | 18100 | R-454B
216056433 | 1.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9Y040A10MP11 | 21000 | 16.5 | 10.5 | 8.1 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216977216 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH29/36X*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
215674190 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL0902120B* | 45000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
215673990 | 3.67 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716A* | 44000 | 17.5 | 9.5 | 9 | 48500 | 34200 | 70.52% | 2.04 | 42500 | R-454B
216977167 | 1.98 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH18/36R*+TXV | SL297UH040NV36B* | 23800 | 17 | 11.7 | 8.85 | 22400 | 20400 | 91.07% | 1.78 | 18800 | R-454B
216977176 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LP29/36X*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216977199 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*18/36T*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
213307134 | 3.79 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVA-60HDN1-M20G | HG3K960+AEFE5* |  | 45500 | 18 | 11.7 | 9.25 | 46000 | 33200 | 72.17% | 1.96 | 39000 | R-410A
215295541 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE24936 | *96VTN1002120A* | 34400 | 15.2 | 9.5 | 8.1 | 37800 | 34800 | 92.06% | 1.9 | 28400 | R-410A
215675965 | 4.04 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X61M24A*+WALLCON | *80CSU1002120A* | 48500 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2.1 | 46500 | R-454B
215295591 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HE34936 | *96VTN1002120B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
216977192 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | L*30/36U*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20200 | 90.18% | 1.85 | 18800 | R-454B
216977240 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | L*43/61Z*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.85 | 38000 | R-454B
212362635 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VM971205DNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216978073 | 2.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD24/35Z*+TXV | SL297UH040NV36B* | 34400 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
214392004 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R802V1005A21DZ | 44500 | 15.5 | 10.1 | 8.2 | 45500 | 36400 | 80% | 3.07 | 33800 | R-410A
216505460 | 2.78 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*S+CM36B34+TDR |  | 33400 | 18 | 9 | 8.5 | 35000 | 25000 | 71.43% | 2.73 | 24000 | R-410A
213281558 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E100B12LMPS1 | 33600 | 17.5 | 8.5 | 8.1 | 36000 | 25600 | 71.11% | 2.6 | 25000 | R-410A
214391703 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | U97MV0703A17DHS | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.9 | 16000 | R-410A
214391650 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R801V0754A17UH | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.87 | 15900 | R-410A
214391691 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R962V0603A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.9 | 16000 | R-410A
210693325 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VS800805CUA* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362553 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | A*VC960603BNB* | 33600 | 18 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362555 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | A*VM970603BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215611121 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FHRAVM4821S*YECA |  | 45500 | 19 | 12 | 8.5 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
216410831 | 2.82 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DBCN1 | Y92E080C16SMPS1 | 33800 | 17.5 | 9.5 | 8.5 | 34200 | 24000 | 70.18% | 2.04 | 26400 | R-410A
216613170 | 2.73 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | RH2VY3621MTACN |  | 32800 | 19 | 13 | 10 | 32800 | 27800 | 84.76% | 2.1 | 28000 | R-454B
216505463 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*L+CM48E44+TDR |  | 34400 | 18 | 9 | 8.5 | 35000 | 25200 | 72% | 2.81 | 24000 | R-410A
214391696 | 1.87 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | U802VA075317M | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16100 | 70% | 2.99 | 15800 | R-410A
213281562 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E100B12SMPS1 | 33600 | 17.5 | 8.5 | 8.1 | 36000 | 25600 | 71.11% | 2.6 | 25000 | R-410A
213281571 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E100C20LMPS1 | 32400 | 16.1 | 8 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
216494191 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)4824G1K*+TXV | 986TD60080C21*** | 43500 | 21 | 10.5 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
214573029 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**6124AL*+UI | 935CB66100C21*** | 33200 | 18.5 | 11.5 | 8.5 | 31800 | 24800 | 77.99% | 2 | 31200 | R-410A
214573179 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CSPH*4212AL*+UI | 986TD60080C21*** | 32600 | 17.5 | 11 | 8.5 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
214239668 | 2.67 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | END4X42L17**+WALLCON | *80CTL0901716B* | 32000 | 17 | 11.5 | 8.1 | 33000 | 24600 | 74.55% | 1.9 | 31400 | R-410A
212972981 | 1.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X24L17** | *96VSN0401410B* | 23000 | 16 | 10 | 8.5 | 27000 | 24800 | 91.85% | 2.04 | 19200 | R-410A
212973631 | 1.95 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EN(A,D)4X30L17** | *96VSN0601412B* | 23400 | 16.5 | 10 | 8.1 | 26200 | 24600 | 93.89% | 2.04 | 19100 | R-410A
213546826 | 1.97 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | L*35/36U9 | ML296UH045XV36B* | 23600 | 20 | 13 | 8.5 | 21600 | 15200 | 70.37% | 1.88 | 13600 | R-410A
213546642 | 2 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | L*35/36U9 | EL280UH070XE36A* | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213546645 | 2 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | LH18/37D9 | EL280UH070XE36A* | 24000 | 21 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
216487847 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | H,PG53*36+TXV | 986TD60080C21*** | 34400 | 18 | 10 | 9 | 33800 | 24800 | 73.37% | 1.88 | 29400 | R-454B
213281575 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E100C20SMPS1 | 32400 | 16.1 | 8 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
213281576 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Y81E100C20SMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
206133297 | 1.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X24L17A*+WALLCON | *80CSU0401712A* | 23200 | 16.5 | 10.5 | 8.1 | 22000 | 16800 | 76.36% | 1.9 | 21000 | R-410A
215375243 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R801V1255A24UH | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
216977201 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH29/36F*+TXV | SL297UH040NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
215375259 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V0755A21UHS | 44000 | 15.2 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25600 | R-410A
215375275 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1255A24DZ | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
216436715 | 1.85 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVA-36HDN1-M20G | L(E,F)W36D4 |  | 22200 | 19 | 11.7 | 9 | 23800 | 17600 | 73.95% | 2 | 22400 | R-410A
216681069 | 3.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | EA*4X48L21A* | *97VTN0802120A* | 36200 | 16 | 10 | 9 | 38000 | 34400 | 90.53% | 1.96 | 29000 | R-410A
213281583 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E120C16SMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
206771138 | 2.63 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X36L21A*+WALLCON | *96CTN1002122A* | 31600 | 17 | 11 | 8.1 | 33200 | 24200 | 72.89% | 1.86 | 31200 | R-410A
206771345 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X37L21A*+WALLCON | *96CTN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
214396672 | 1.92 | Yes | Yes | JOHNSON CONTROLS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTF36B5ADS1 | TM9Y060B12MP11 | 23000 | 18 | 12 | 9.5 | 23000 | 18400 | 80% | 2 | 18100 | R-454B
216764915 | 1.88 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWX7024A1 | 5PX*B004AS3 | S8X2B080M4PSC | 22600 | 17.5 | 12 | 8.7 | 21600 | 17000 | 78.7% | 1.9 | 15100 | R-454B
214391645 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R801V0504A17UHU | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.89 | 16000 | R-410A
214391649 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R801V0754A17DZ | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.87 | 15900 | R-410A
214391663 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R802V0504A17UHS | 22400 | 16 | 11.9 | 8.3 | 23000 | 17200 | 74.78% | 3.06 | 16400 | R-410A
214391972 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R801V0755A21DZ | 44500 | 15.5 | 10 | 8.2 | 45500 | 36600 | 80.44% | 3.06 | 34000 | R-410A
212380519 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | PL36H210P749 | 58TN*A045C17**12 | 23400 | 20 | 13 | 8.1 | 25000 | 19600 | 78.4% | 2.42 | 24000 | R-410A
214522661 | 2.6 | Yes | Yes | BOSCH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | BOVD-36HDN1-M20G | AFM354+TDR |  | 31200 | 18 | 11 | 8.8 | 33800 | 24000 | 71.01% | 1.9 | 28000 | R-410A
212632236 | 1.98 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | LD24/35Z9 | SL280DF060NV36B* | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
213281553 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36B34+TDR | Y81E080C20SMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
214573059 | 2.77 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**6124AL*+UI | 986TD60080C21*** | 33200 | 18.5 | 11.5 | 8.5 | 31800 | 24800 | 77.99% | 2.02 | 31200 | R-410A
214573329 | 2.62 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CNPV*3621AL*+UI | 935CB66100C21*** | 31400 | 17 | 11 | 8.1 | 33000 | 24000 | 72.73% | 1.84 | 31000 | R-410A
216977242 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-060-230A** | LP42/62W*+TXV | SL297UH080NV60C* | 45500 | 17 | 11 | 9 | 45500 | 39000 | 85.71% | 1.85 | 38000 | R-454B
214392758 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R801V0504A17UHS | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214391687 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP37A34+TDR | R951V0703A17M4S | 22400 | 16 | 11.9 | 8.3 | 23000 | 17200 | 74.78% | 3.07 | 16400 | R-410A
214392600 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R962V0703A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392668 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | U97MV0603A17DHS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214394261 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | U802VA075317Z | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394270 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | U802VA075317Z | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394272 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | U802VA075317Z | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214392765 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R801V0504A17UHS | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214392840 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R801V0704A17UHU | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214392869 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | R801V0754A17DZ | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
212362823 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VM970804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216675569 | 2.08 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | ESH5X36M12A* | *80CSU1002120A* | 25000 | 15.2 | 10 | 8.5 | 24200 | 19500 | 80.58% | 1.92 | 19000 | R-454B
214391642 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R801V0503A14UH | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16300 | 70.87% | 2.88 | 15900 | R-410A
214391998 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R802V0755A21DZ | 44500 | 15.5 | 10 | 8.2 | 45500 | 36600 | 80.44% | 3.06 | 34000 | R-410A
216761992 | 3.21 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG48936 | 927TA60100V21*** | 38500 | 18 | 11.5 | 11.5 | 42000 | 41500 | 98.81% | 2.32 | 37000 | R-410A
214391698 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | U802VA075317Z | 22400 | 16.4 | 11.8 | 8.3 | 23000 | 16600 | 72.17% | 2.99 | 16100 | R-410A
214572569 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**3721AL*+UI | 987MC60080C21*** | 32800 | 17.5 | 11.5 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
213088501 | 3 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | V,R36H***P449+AEFE3A* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
214572719 | 2.73 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4321AL*+UI | 935CB60080C21*** | 32800 | 17.5 | 11 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
214572819 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4821AL*+UI | 986TD60080C21*** | 32400 | 17.5 | 11.5 | 8.5 | 32400 | 24800 | 76.54% | 2 | 31400 | R-410A
216794484 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S8V2B060M4PCB | 42000 | 19.2 | 11.7 | 9.5 | 46500 | 42500 | 91.4% | 2.76 | 51000 | R-454B
216794489 | 3.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60C3J+TDR | S8V2B060M4PDB | 42000 | 19.2 | 11.7 | 9.5 | 46500 | 42500 | 91.4% | 2.76 | 51000 | R-454B
216794516 | 3.54 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S8V2C100M5PDB | 42500 | 20 | 11.7 | 9.5 | 47000 | 42500 | 90.43% | 2.77 | 50500 | R-454B
216797099 | 2.47 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | S9V2B040U3VSB+LRP | 29600 | 18 | 9.8 | 8.5 | 32800 | 32800 | 100% | 2.67 | 37000 | R-454B
216794357 | 2.72 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | L8V1A060U3VSB+LRP | 32600 | 19.6 | 11.7 | 9 | 32600 | 31800 | 97.55% | 2.91 | 39000 | R-454B
216794405 | 2.58 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2B060D3PSC+LRP | 31000 | 17.5 | 11.2 | 9.5 | 31200 | 30600 | 98.08% | 2.91 | 38000 | R-454B
214392000 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R802V0755A21UH | 44500 | 15.5 | 10 | 8.2 | 45500 | 37000 | 81.32% | 3.08 | 34200 | R-410A
216487960 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | CE(P,V)6024G48*+TXV | 986TD60080C21*** | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216505461 | 2.87 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | AE*S+CM48E44+TDR |  | 34400 | 18 | 9 | 8.5 | 35000 | 25200 | 72% | 2.81 | 24000 | R-410A
216797058 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | *DHMB060CCV3+LRP | 30200 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.74 | 38500 | R-454B
216797060 | 2.52 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | *DHMB080CCV3+LRP | 30200 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.72 | 38500 | R-454B
216797061 | 2.5 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)36C3J+TDR | *DHMC100CCV4+LRP | 30000 | 18 | 9.8 | 8.5 | 34000 | 34000 | 100% | 2.67 | 38500 | R-454B
216797108 | 2.53 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV8X36A1 | D(A,C,E)48C3J+TDR | S9V2B060U4PSC+LRP | 30400 | 18 | 9.8 | 8.5 | 33000 | 33000 | 100% | 2.72 | 38000 | R-454B
214393785 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R951V0403A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
212380542 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | V,C36H175P139 | 58TN*A070C17**16 | 23400 | 20 | 13.5 | 8.5 | 25000 | 19400 | 77.6% | 2.46 | 23800 | R-410A
212380546 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | C36A***L129 | 58TN*A090C17**16 | 23200 | 21 | 13.5 | 8.5 | 25000 | 19300 | 77.2% | 2.46 | 23800 | R-410A
215651669 | 3.88 | No | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV0X48A1 | H,TG49960 | S9V2C080U5PSB+RP | 46500 | 19 | 11.7 | 8.5 | 40000 | 28000 | 70% | 1.8 | 35400 | R-410A
214391997 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | R802V0755A21DZ | 44000 | 15.3 | 10 | 8.1 | 45500 | 36400 | 80% | 3.01 | 33800 | R-410A
214391999 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | R802V0755A21UH | 44000 | 15.3 | 10 | 8.1 | 45500 | 36600 | 80.44% | 3.01 | 34000 | R-410A
210693327 | 2.8 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | G*VC801005C*A* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
206765647 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0451712A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.92 | 20800 | R-410A
215939869 | 2.85 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CTN0801716A* | 34200 | 20 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30400 | R-454B
215939969 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X36M12A*+WALLCON | *97CTN0601716A* | 33000 | 18 | 10.5 | 9 | 35600 | 27400 | 76.97% | 1.9 | 31400 | R-454B
215940019 | 2.8 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0802120B* | 33600 | 19 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.92 | 30600 | R-454B
215940169 | 2.82 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *97CTN1202422A* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.92 | 30400 | R-454B
213281555 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E100B12LMPS1 | 32600 | 17.5 | 8 | 8.1 | 36000 | 25600 | 71.11% | 2.6 | 25000 | R-410A
216762706 | 2.83 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AA3* | H,PG9J936 | 927TA60100V21*** | 34000 | 16 | 10 | 9.5 | 34200 | 26200 | 76.61% | 2.26 | 23800 | R-410A
210693343 | 2.78 | Yes | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | G*VS800604BUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213281552 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Y81E080C20SMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
206771354 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X37L21A*+WALLCON | *80CTL0901716A* | 33000 | 18 | 11.7 | 8.5 | 32800 | 25000 | 76.22% | 2 | 31800 | R-410A
206771390 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *80CTL0701716A* | 31800 | 17 | 11 | 8.1 | 33200 | 24600 | 74.1% | 1.88 | 31400 | R-410A
216978069 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LD19/36Y*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216794550 | 3.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | D(A,C,E)60B4J+TDR | S9V2C100D4VSB+LRP | 41500 | 20 | 11.7 | 9 | 46000 | 41500 | 90.22% | 2.69 | 49500 | R-454B
215936430 | 2.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X49M24A*+WALLCON | *80CSU1002120A* | 35400 | 21.5 | 12 | 8.5 | 38500 | 28600 | 74.29% | 2.04 | 33000 | R-454B
215936580 | 2.97 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVD5X60M21A*+WALLCON | *80CSU1002120A* | 35600 | 21.5 | 12 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32800 | R-454B
214392006 | 3.71 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP61B34+TDR | R802V1005A21UH | 44500 | 15.5 | 10 | 8.2 | 45500 | 36400 | 80% | 3.06 | 33800 | R-410A
214392047 | 3.63 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ48AJ2N | CP49B34+TDR | U802VA100521Z | 43500 | 15.3 | 10 | 8.1 | 45000 | 33400 | 74.22% | 2.97 | 32000 | R-410A
214392199 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R801V0704A17UHU | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392215 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R801V0754A17DZ | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392247 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R801V0754A17UHS | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
213281549 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36B34+TDR | Y81E080C20LMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213281567 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E100C16SMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
216977195 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LH24/37F*+TXV | SL297UH060NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216056505 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
214392256 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R801V0754A17UHS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
216504989 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A36+TDR | Y91E080B12SMPS1 | 32200 | 16.5 | 8.5 | 8.1 | 36000 | 26000 | 72.22% | 2.73 | 25200 | R-410A
213281548 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+TDR | Y81E080C20LMPS1 | 34000 | 17 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213281578 | 2.93 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E100C20SMPS1 | 35200 | 16.5 | 9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
212632235 | 1.98 | No | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | LD19/36Y9 | SL280DF060NV36B* | 23800 | 20 | 13.5 | 8.5 | 22000 | 15400 | 70% | 1.92 | 13700 | R-410A
215668955 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X43M21A*+WALLCON | *80CSU0401712A* | 34400 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
216754802 | 2.65 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH30AAK | EA*5X43M21A* | *80CSU0601716A* | 31800 | 15.2 | 9.5 | 9 | 34400 | 30200 | 87.79% | 1.8 | 21400 | R-454B
214244070 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CNPV*4221AL*+UI | 88*TB60090C21*** | 23400 | 20 | 13 | 10 | 26600 | 19800 | 74.44% | 2.44 | 24800 | R-410A
215667153 | 2 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X25M17A*+WALLCON | *80CSU0401712A* | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
216487864 | 3.67 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN048**AA* | CE(P,V)4817G1K*+TXV | 986TD42080C17*** | 44000 | 17 | 9.5 | 9 | 47000 | 33600 | 71.49% | 2.04 | 41500 | R-454B
214391670 | 1.87 | Yes | Yes | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R802V1004A17UHS | 22400 | 16 | 11.9 | 8.3 | 23000 | 17000 | 73.91% | 3.04 | 16300 | R-410A
214391674 | 1.87 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | CP31A34+TDR | R921V0603A17M4S | 22400 | 15.6 | 11.9 | 8.3 | 23000 | 16500 | 71.74% | 2.9 | 16000 | R-410A
212380978 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | V,C60H210P299 | 58TN*A090C21**20 | 44000 | 21 | 12 | 8.5 | 44000 | 35800 | 81.36% | 2.36 | 42500 | R-410A
216984635 | 3.71 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | V,C60H210P17*+TXV | 987TA60080C21*** | 44500 | 21 | 11 | 9.5 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
216984653 | 3.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN048**AA* | V,C60H245P76*+TXV | 987TA66120C24*** | 43500 | 21 | 11 | 9.45 | 46500 | 36200 | 77.85% | 2 | 38500 | R-454B
213281573 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36B34+TDR | Y81E100C20LMPS1 | 34000 | 16.5 | 8.9 | 8.1 | 36000 | 26800 | 74.44% | 2.83 | 25600 | R-410A
214392735 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R801V0504A17UHN | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
215667568 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0401712A* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 19900 | R-454B
213281554 | 2.93 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E080C20SMPS1 | 35200 | 17 | 9 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
213281563 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E100C16LMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
213281579 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E120C16LMPS1 | 33000 | 17.5 | 8 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
214394620 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | U98MV1005A21UPS | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394631 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | U98MV1005A21UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216410828 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DBCN1 | Y92E080B12SMPS1 | 33200 | 17.5 | 10 | 8.5 | 33000 | 23200 | 70.3% | 2 | 25800 | R-410A
215669111 | 2.82 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CSU0601716A* | 33800 | 18 | 9.5 | 9 | 35000 | 25200 | 72% | 1.88 | 30400 | R-454B
213281566 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E100C16LMPS1 | 34000 | 17.5 | 8.5 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
216984310 | 4.63 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN060**AA* | A60VHA*+TXV | 987TA66100C21*** | 55500 | 18 | 9 | 9 | 58000 | 41500 | 71.55% | 2.02 | 50500 | R-454B
216984601 | 2.75 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | PL36H175P15*+TXV | 987TA42060C17*** | 33000 | 19 | 11 | 9 | 33800 | 26600 | 78.7% | 1.9 | 30000 | R-454B
214392267 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R801V1004A17UH | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
214392299 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V0503A14UHN | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214393744 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R951V0403A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216984242 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | PL36H210P29*+TXV | 987TA42060C17*** | 34200 | 17 | 9.5 | 9 | 34000 | 25000 | 73.53% | 1.88 | 29600 | R-454B
214573769 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**4221AL*+UI | 987MC60080C21*** | 31800 | 17 | 11 | 8.5 | 32800 | 24400 | 74.39% | 1.9 | 31200 | R-410A
214573969 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**4824AL*+UI | 88*TB60070C21*** | 32400 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
216984253 | 2.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 290VAN036**AA* | C36A***L53*+TXV | 987TA42060C17*** | 34200 | 17 | 9.5 | 9 | 34000 | 25000 | 73.53% | 1.88 | 29600 | R-454B
214393769 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | R951V0403A17UHU | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393805 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R951V0603A17M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393835 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R951V0603A17UHU | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393846 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V0603A17UHU | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393855 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | R951V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393928 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V0855A21M4S | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393628 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R921V0703A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393651 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R921V0703A17M4S | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394389 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C44+TDR | U97MV0603A17DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394428 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | U97MV0855A21DHS | 33000 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
216772741 | 3.96 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH48AAK | FTMA5B60L0D* |  | 47500 | 15.2 | 9 | 9 | 49000 | 44000 | 89.8% | 1.8 | 35200 | R-454B
215295593 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG35936 | *96VTN1002120B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215295659 | 2.83 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG24936 | *96VTN1002122B* | 34000 | 16 | 9.5 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
213350135 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E080C20LMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 28200 | 84.94% | 2.71 | 25600 | R-410A
213350160 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E100C20LMPS1 | 32000 | 17.5 | 9.4 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213350194 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | Y82E100C20LMPS1 | 32000 | 18.5 | 9.4 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213296019 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TM8E080B12MP11 | 31600 | 17.9 | 9.3 | 8.4 | 34000 | 28000 | 82.35% | 2.62 | 25800 | R-410A
213296028 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TM8V100C20MP12 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
213296035 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
216056501 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216056510 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
214392508 | 1.68 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R951V0403A17UHU | 20200 | 17.7 | 9 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392556 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R951V0703A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214394378 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | U97MV0603A17DHS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394448 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | U97MV0855A21DHS | 32800 | 18 | 10 | 8.1 | 34200 | 29400 | 85.96% | 1.9 | 31200 | R-410A
216980381 | 2.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTM36B5CDS1 | Y82E080B12LMPS1 | 33800 | 18 | 11 | 8.5 | 31800 | 24000 | 75.47% | 2 | 27800 | R-454B
215399951 | 2.57 | Yes | No | YORK | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR |  | 30800 | 15.2 | 10 | 8.1 | 31000 | 31600 | 101.9% | 2.52 | 27000 | R-454B
216056544 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216056558 | 2.55 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Y82E080B12LMPS1 | 30600 | 19 | 11 | 8.5 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
216056594 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216056608 | 2.55 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM9V080B12MP12 | 30600 | 18 | 10.5 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216056617 | 2.55 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE080B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216056628 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C080C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216056660 | 2.58 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8E100B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216056694 | 2.6 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
214394521 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | U98MV0603A17UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394212 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | U802VA050317M | 33800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214392567 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R962V0403A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392583 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R962V0603A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214394271 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | U802VA075317Z | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
216056712 | 2.78 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | YPLC080C16MP13 | 33400 | 18 | 11 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
213927819 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D3G+TXV+TDR | TM9E060A10MP12 | 32600 | 17.5 | 9.5 | 8.1 | 33800 | 27400 | 81.07% | 2.48 | 25400 | R-410A
215654049 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | TM8V120C20MP12 | 41500 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33200 | R-454B
215654056 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60A3J+TDR | Y81E130D20SMPS1 | 41500 | 18 | 11.7 | 9 | 44500 | 33600 | 75.51% | 2 | 33000 | R-454B
216056737 | 3.38 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM9E120D20MP12 | 40500 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
214392715 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | U98MV0703A17UPS | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392333 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0504A17UHN | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214570669 | 2 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CAP**4821AL*+UI | 88*TB60070C21*** | 24000 | 16.5 | 11 | 8.5 | 21000 | 16600 | 79.05% | 2.02 | 20400 | R-410A
215669171 | 2.82 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0902120B* | 33800 | 18 | 10 | 9 | 35000 | 25000 | 71.43% | 1.9 | 30200 | R-454B
215675175 | 3.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0701716B* | 45000 | 16 | 9 | 8.5 | 48500 | 34200 | 70.52% | 1.94 | 42500 | R-454B
215675245 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *95CSU0802120B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
215675445 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *97CMN0802120B* | 47000 | 18.5 | 10 | 9 | 50000 | 36600 | 73.2% | 2 | 46000 | R-454B
214522533 | 2.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DX36E34+TDR | Y81E080C16SMPS1 | 33000 | 18 | 10 | 8.5 | 33400 | 23400 | 70.06% | 1.98 | 25800 | R-410A
215669561 | 2.88 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0801714B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
214392860 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R801V0754A17DZ | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393251 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R802V0754A17DZ | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393610 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R921V0603A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394528 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | U98MV0603A17UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214572639 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4221AL*+UI | 986TD60080C21*** | 31800 | 17.5 | 11 | 8.5 | 32800 | 24400 | 74.39% | 1.9 | 31200 | R-410A
214570599 | 1.98 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CAP**4224AL*+UI | 986TD60080C21*** | 23800 | 17 | 11 | 8.5 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
214570649 | 2.03 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CAP**4321AL*+UI | 987MC60080C21*** | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
216056769 | 3.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Y91E120D20SMPS1 | 42000 | 17.5 | 11.2 | 8.1 | 46500 | 34200 | 73.55% | 2 | 34000 | R-454B
216056778 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TL8E080C16UH11 | 41000 | 17 | 11.5 | 8.5 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216056810 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TM8Y100C16MP11 | 41000 | 17 | 11 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216056835 | 3.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TM9Y080C16MP11 | 40500 | 17 | 10.5 | 8.5 | 44000 | 33800 | 76.82% | 2 | 32600 | R-454B
216056862 | 3.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C16MP13 | 40500 | 17 | 11 | 8.5 | 43500 | 33200 | 76.32% | 2 | 31800 | R-454B
216056867 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216056869 | 3.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
214572659 | 2.65 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**4224AL*+UI | 935CB60080C21*** | 31800 | 17 | 11 | 8.5 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
214572509 | 2.63 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**3621AL*+UI | 987MC60080C21*** | 31600 | 17 | 11 | 8.1 | 33000 | 24200 | 73.33% | 1.86 | 31200 | R-410A
216056555 | 2.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | Y81E100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
216056621 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE100C16MP11 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216056637 | 2.55 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Y81E100B12SMPS1 | 30600 | 18 | 11 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26600 | R-454B
216056639 | 2.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Y81E100C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31800 | 25400 | 79.87% | 2 | 27800 | R-454B
216056755 | 3.29 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TP9C080C16MP13 | 39500 | 16.5 | 10.5 | 8.1 | 43500 | 33600 | 77.24% | 2 | 32200 | R-454B
216978065 | 2 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230A** | LD19/36Z*+TXV | SL297UH040NV36B* | 24000 | 17 | 12 | 9 | 22400 | 20400 | 91.07% | 1.8 | 18800 | R-454B
216643571 | 1.53 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH18AAK | EA*5X19M17A* | *80MSU0401712A* | 18400 | 15.5 | 11.5 | 9.5 | 20000 | 17700 | 88.5% | 2 | 14900 | R-454B
215295537 | 3.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG82936 | *96VTN0802120B* | 36200 | 16 | 10 | 8.5 | 36400 | 34400 | 94.51% | 2.04 | 28000 | R-410A
215295554 | 2.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG35936 | *96VTN1002120A* | 35800 | 15.2 | 10 | 8.1 | 37800 | 34800 | 92.06% | 1.9 | 28400 | R-410A
215295586 | 2.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE33936 | *96VTN1002120B* | 35200 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215295605 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG8J936 | *96VTN1002120B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
214393732 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R951V0403A17M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393784 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | R951V0403A17UHU | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393832 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42C44+TDR | R951V0603A17UHU | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393834 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R951V0603A17UHU | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214393864 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | R951V0703A17M4S | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393917 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R951V0855A21M4S | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214393950 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R951V1005A21M4S | 33800 | 17 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215669352 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6024AM*+UI | 59CU5B100C21**22 | 34400 | 18 | 10 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
214392781 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | R801V0504A17UHS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393198 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | R802V0504A17UHN | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393232 | 2.82 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D44+TDR | R802V0504A17UHS | 33800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
214393680 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C44+TDR | R921V0855A21M4S | 33000 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394201 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | U802VA050317M | 33400 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394251 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | U802VA075317Z | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215295675 | 2.92 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE35936 | *96VTN1002122B* | 35000 | 17 | 10 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
215295684 | 2.92 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE7J936 | *96VTN1002122B* | 35000 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
215295693 | 2.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE1K936 | *96VTN1002122B* | 35200 | 17 | 10 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
215295734 | 3 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG80936 | *96VTN1202422A* | 36000 | 16 | 10 | 8.5 | 36800 | 34200 | 92.93% | 2.06 | 28000 | R-410A
215295743 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG32936 | *96VTN1202422B* | 33600 | 16 | 9.5 | 8.5 | 36200 | 34200 | 94.48% | 2.02 | 28000 | R-410A
215684021 | 2.8 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 58TN*B090C17**16 | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
212362572 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VM970603BNB* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362590 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | A*VS960805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362625 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VC960603BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215669452 | 2.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6121AM*+UI | 58TN*B045C17**12 | 34400 | 17.5 | 9.5 | 9 | 34600 | 25200 | 72.83% | 1.9 | 30200 | R-454B
215683891 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 58CU*A040C17**12 | 34400 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
213281559 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E100B12SMPS1 | 32600 | 17.5 | 8 | 8.1 | 36000 | 25600 | 71.11% | 2.6 | 25000 | R-410A
213307379 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM9Y120D20MP11 | 31000 | 16.2 | 9.2 | 8.3 | 32200 | 28000 | 86.96% | 2.73 | 25200 | R-410A
215654028 | 2.58 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E080C16SMPS1 | 31000 | 17.5 | 11.2 | 8.1 | 30600 | 25000 | 81.7% | 2 | 27000 | R-454B
215654029 | 2.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH36B3J+TDR | Y81E080C20SMPS1 | 31600 | 19 | 10.5 | 8.5 | 32000 | 25800 | 80.62% | 2 | 28000 | R-454B
215654045 | 2.63 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CH48A3J+TDR | Y81E120C20SMPS1 | 31600 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27800 | R-454B
216056515 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y100C20MP11 | 30800 | 18 | 11 | 8.5 | 30600 | 25000 | 81.7% | 2 | 26800 | R-454B
216056563 | 2.65 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | YP9C080B12MP13 | 31800 | 18 | 11 | 8.5 | 30800 | 25200 | 81.82% | 2 | 27000 | R-454B
216056565 | 2.65 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | YP9C100C16MP13 | 31800 | 18 | 11 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216056581 | 2.6 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL8E080C16UH11 | 31200 | 18 | 10.5 | 8.5 | 31800 | 25600 | 80.5% | 2 | 28000 | R-454B
216056649 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | YP9C100C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216056698 | 2.6 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TPLC080C16MP13 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216056713 | 2.57 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | YPLC100C16MP13 | 30800 | 18 | 11 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
214092697 | 2.72 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL8E100C20UH11 | 32600 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.68 | 25400 | R-410A
214092699 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TL9E060B12UH11 | 32600 | 18 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.6 | 25600 | R-410A
214092700 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TL9E080C16UH11 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.64 | 25800 | R-410A
215295620 | 2.8 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE23936 | *96VTN1002122A* | 33600 | 16 | 9.5 | 8.1 | 36800 | 34800 | 94.57% | 1.82 | 28400 | R-410A
215295638 | 2.98 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG36936 | *96VTN1002122A* | 35800 | 16 | 10 | 8.5 | 36200 | 34200 | 94.48% | 2.06 | 27800 | R-410A
215295652 | 3 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG80936 | *96VTN1002122A* | 36000 | 16 | 10 | 8.5 | 36200 | 34200 | 94.48% | 2.06 | 27800 | R-410A
215295655 | 3 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG81936 | *96VTN1002122A* | 36000 | 16 | 10.5 | 8.1 | 36800 | 34400 | 93.48% | 2.02 | 28200 | R-410A
215295687 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE8J936 | *96VTN1002122B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215295689 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG9J936 | *96VTN1002122B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215295704 | 2.9 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG32936 | *96VTN1202422A* | 34800 | 16 | 9.5 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215375084 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B36+TDR | R802V0503A14UHN | 21600 | 17 | 10 | 8.1 | 22600 | 19000 | 84.07% | 2 | 16900 | R-410A
214392440 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R921V0403A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392524 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R951V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392667 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | U97MV0603A17DHS | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392699 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | U98MV0603A17UPS | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392240 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R801V0754A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214092715 | 2.75 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8E100C16MP11 | 33000 | 18 | 10 | 8.2 | 32800 | 28600 | 87.2% | 2.68 | 25800 | R-410A
214092717 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.2 | 33000 | 29000 | 87.88% | 2.72 | 26000 | R-410A
214092734 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM8Y080C16MP11 | 32400 | 18.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.66 | 25400 | R-410A
214092766 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TM9V100C20MP12 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
214092767 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9V100C20MP12 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
214092799 | 2.73 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TMLV100C16MP12 | 32800 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
215654061 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CH60B3J+TDR | Y81E080C16SMPS1 | 41000 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
215912453 | 3.38 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Y81E080C16SMPS1 | 40500 | 17.5 | 11.7 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32600 | R-454B
214392315 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V0503A14UHS | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392331 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V0504A17UHN | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392365 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0754A17DZ | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392401 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R802V0754A17UHS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392408 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V1004A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392433 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R802V1004A17UHS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392615 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | U802VA050317M | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392658 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | U802VA075317Z | 21000 | 18.9 | 9.8 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214092816 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | TPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.63 | 26400 | R-410A
214092832 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.68 | 26200 | R-410A
215912469 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Y81E100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
215912471 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | Y81E100C20SMPS1 | 41500 | 18 | 11.7 | 8.5 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
214092833 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E080B12LMPS1 | 33000 | 18 | 9.5 | 8.3 | 32800 | 29800 | 90.85% | 2.73 | 26400 | R-410A
214092847 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E080C20SMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 28200 | 84.94% | 2.71 | 25600 | R-410A
214092848 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E080C20SMPS1 | 32400 | 18 | 10 | 8.5 | 33400 | 28400 | 85.03% | 2.71 | 25800 | R-410A
214092864 | 2.72 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | Y81E100C20LMPS1 | 32600 | 17.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092865 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y81E100C20SMPS1 | 31600 | 17.5 | 9.3 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
214092866 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | Y81E100C20SMPS1 | 32400 | 17.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
214092899 | 2.72 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | YP9C080C16MP13 | 32600 | 17.5 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
214092915 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A46+TDR | YPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.5 | 32400 | 27800 | 85.8% | 2.69 | 25200 | R-410A
214092099 | 2.7 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TMLV100C16MP12 | 32400 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214092146 | 2.75 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | Y81E080B12SMPS1 | 33000 | 18 | 9.5 | 8.3 | 32800 | 29800 | 90.85% | 2.73 | 26400 | R-410A
215674536 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *95CSU1002122B* | 46000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
214092199 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | YP9C100C20MP13 | 32400 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.69 | 26000 | R-410A
214092213 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | YPLC100C16MP13 | 31600 | 17.5 | 9.8 | 8.4 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
216056716 | 3.33 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL9E080C16UH11 | 40000 | 17.5 | 10.5 | 8.1 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
216056730 | 3.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TM8Y100C16MP11 | 40000 | 17.5 | 11.2 | 8.1 | 43500 | 33400 | 76.78% | 2 | 32200 | R-454B
216056747 | 3.42 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080C20MP11 | 41000 | 16.5 | 10.5 | 8.1 | 46000 | 35000 | 76.09% | 2 | 35000 | R-454B
216056783 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TL9E080C16UH11 | 41000 | 18 | 10.5 | 8.5 | 45500 | 34400 | 75.6% | 2 | 34000 | R-454B
214092216 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | YPLC100C20MP13 | 31000 | 16.3 | 8.8 | 8.5 | 32200 | 27600 | 85.71% | 2.7 | 25000 | R-410A
214091998 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | TM8Y060A12MP11 | 32400 | 18 | 9.9 | 8.1 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
214392444 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R921V0403A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392461 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R921V0603A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392496 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R951V0403A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392497 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R951V0403A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392513 | 1.72 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R951V0403A17UHU | 20600 | 17.8 | 9.7 | 8.1 | 22400 | 17100 | 76.34% | 2 | 19100 | R-410A
214392545 | 1.72 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R951V0603A17UHU | 20600 | 17.8 | 9.7 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392560 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R951V0703A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392663 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | U97MV0603A17DHS | 21600 | 19 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
216056846 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TMLE100C16MP11 | 41000 | 18 | 10.5 | 8.5 | 45000 | 34200 | 76% | 2 | 33800 | R-454B
216056864 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
214092747 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B36+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.59 | 25800 | R-410A
213296015 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TL9E080C16UH11 | 31600 | 17.5 | 9.3 | 8.5 | 33800 | 27800 | 82.25% | 2.65 | 25600 | R-410A
213296016 | 2.78 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.1 | 33600 | 29000 | 86.31% | 2.71 | 26200 | R-410A
213296034 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TM8Y100C20MP11 | 33600 | 18 | 9.5 | 8.1 | 33600 | 30000 | 89.29% | 2.72 | 26800 | R-410A
213296049 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TM9V120D20MP12 | 31200 | 16.8 | 9.3 | 8.5 | 32200 | 28000 | 86.96% | 2.79 | 25200 | R-410A
213296065 | 2.58 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A3G+TXV+TDR | TMLV120C20MP12 | 31000 | 16.3 | 8.8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
213296214 | 2.77 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A46+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.2 | 33800 | 28600 | 84.62% | 2.7 | 26000 | R-410A
214437577 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
214437578 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9V100C16MP12 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.67 | 25400 | R-410A
213350131 | 2.63 | No | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E080C16SMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 27400 | 82.53% | 2.7 | 25200 | R-410A
213350145 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y81E100B12LMPS1 | 32000 | 18.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
213350179 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y81E120C20SMPS1 | 31600 | 17.5 | 9.3 | 8.5 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
213350180 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | Y81E120C20SMPS1 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
215932306 | 2.7 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *97CMN0801714B* | 32400 | 19.5 | 11 | 9.5 | 35400 | 27200 | 76.84% | 2 | 31000 | R-454B
215932356 | 2.73 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X42M21A*+WALLCON | *96CTN1002122B* | 32800 | 20 | 11.5 | 9.5 | 34800 | 26600 | 76.44% | 2 | 30600 | R-454B
213307208 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A34+TDR | TM9Y080C16MP11 | 31200 | 18.3 | 9.3 | 8.1 | 33600 | 28000 | 83.33% | 2.6 | 25600 | R-410A
213770930 | 1.97 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EA*4X36L21A*+WALLCON | *80CTL0901716B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20800 | R-410A
213771130 | 2.02 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EA*4X37L21A*+WALLCON | *80CTL0451712B* | 24200 | 16.5 | 10.5 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
213771180 | 2.03 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA2* | EA*4X37L21A*+WALLCON | *95CSU0601716B* | 24400 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2.02 | 20600 | R-410A
214394210 | 2.57 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D24+TDR | U802VA050317M | 30800 | 17.6 | 9.6 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214394260 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D34+TDR | U802VA075317Z | 32800 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
214392771 | 2.78 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42D44+TDR | R801V0504A17UHS | 33400 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31400 | R-410A
213350181 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y81E120C20SMPS1 | 32000 | 17.5 | 9.4 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
213350197 | 2.67 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | Y82E100C20LMPS1 | 32000 | 18.5 | 9.4 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
215037806 | 3.75 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL17XP1-048-230A** | CH60B34+TDR | ML180UH090E60C* | 45000 | 15.7 | 12.4 | 8.1 | 44500 | 31200 | 70.11% | 2.74 | 30600 | R-410A
215674310 | 3.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CSU0802120A* | 46000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
214394525 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)42B44+TDR | U98MV0603A17UPS | 33000 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
214394541 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48D34+TDR | U98MV0603A17UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
213281582 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E120C16LMPS1 | 34000 | 17.5 | 8.5 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
216762707 | 2.87 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AA3* | H,PG1K936 | 927TA60100V21*** | 34400 | 16 | 10 | 9.5 | 34200 | 26200 | 76.61% | 2.26 | 23800 | R-410A
216504986 | 2.55 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A36+TDR | Y91E080C16SMPS1 | 30600 | 16.5 | 9.8 | 8.1 | 32000 | 27600 | 86.25% | 2.67 | 25000 | R-410A
211259843 | 1.53 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 926TB36060V14*** | 18400 | 16 | 11 | 8.5 | 18400 | 17600 | 95.65% | 2.12 | 12400 | R-410A
214392520 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R951V0603A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
212632696 | 1.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-024-230A** | LD24/35Y9 | SLP99DF090XV48C* | 21800 | 19 | 12 | 9.2 | 20000 | 18400 | 92% | 1.76 | 23800 | R-410A
215674360 | 3.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0901716B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
215674410 | 3.79 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0602120B* | 45500 | 17.5 | 9.5 | 9 | 48000 | 34200 | 71.25% | 2.06 | 42500 | R-454B
215674460 | 3.83 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CSU0802120A* | 46000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
216687204 | 3.79 | Yes | Yes | FUJITSU | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FOP1948MJAYCA | FCCA4821SYEA | FF80TV510021DZ | 45500 | 19 | 12 | 10 | 45500 | 41500 | 91.21% | 2.1 | 42000 | R-454B
213088483 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | V,R36H175P159+AEFE4B* |  | 24200 | 18 | 10.5 | 9 | 25000 | 22600 | 90.4% | 1.92 | 18300 | R-410A
215667587 | 1.93 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H0V24*K*AAA* | EA*5X36M17A*+WALLCON | *80CSU0601716A* | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
214392536 | 1.68 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R951V0603A17UHU | 20200 | 17.7 | 9 | 8.1 | 22400 | 17000 | 75.89% | 2 | 19100 | R-410A
214392571 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R962V0403A17M4S | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392572 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R962V0403A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392589 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R962V0603A17M4S | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 17000 | 75.22% | 2 | 19000 | R-410A
214392604 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R962V0703A17M4S | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392672 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | U97MV0603A17DHS | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392721 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | U98MV0703A17UPS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392136 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R801V0503A14UH | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392176 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R801V0504A17UHS | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392177 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R801V0504A17UHS | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392209 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R801V0704A17UHU | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214394734 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R951V0705A21M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
215684055 | 2.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*4212AM*+UI | 58CU*A040C17**12 | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
214392349 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0504A17UHS | 20800 | 17.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392376 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24D24+TDR | R802V0754A17UHN | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392381 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0754A17UHN | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392397 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R802V0754A17UHS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392151 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)24C34+TDR | R801V0504A17UHN | 21600 | 18 | 10 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392219 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R801V0754A17DZ | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392221 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30D24+TDR | R801V0754A17DZ | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214392268 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | R801V1004A17UH | 20400 | 18.6 | 9 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
214392320 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36B24+TDR | R802V0503A14UHS | 20400 | 17.7 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
214392385 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | R802V0754A17UHN | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
214394777 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U97MV0855A21DHS | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394692 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V1005A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394652 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V1005A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394683 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R802V0755A21UHS | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394684 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V0755A21UHS | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394700 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V1255A24DZ | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394766 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U802VA100521M | 52000 | 18.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
215375291 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R802V1505A24UHS | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215375309 | 3.79 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)60D36+TDR | R921V1155A24M4S | 45500 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
215669391 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN1002122B* | 34400 | 18 | 10.5 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215674353 | 3.83 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0702120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.06 | 42000 | R-454B
214394640 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V0755A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394679 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R802V0755A21UHN | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394715 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R802V1505A24UHS | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
215375350 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R801V1005A21UHN | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
216977206 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*30/36U*+TXV | SL297UH040NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977208 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*35/36U*+TXV | SL297UH040NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977215 | 2.82 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*18/36T*+TXV | SL297UH060NV36B* | 33800 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
216977224 | 2.88 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | L*35/36U*+TXV | SL297UH060NV36B* | 34600 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
212362803 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VM970803BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362821 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VM970603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214242040 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | END4X42L17**+WALLCON | *97CMN0601714B* | 23800 | 16 | 11 | 8.1 | 21400 | 16700 | 78.04% | 1.96 | 20800 | R-410A
214242240 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X48L21**+WALLCON | *80CTL0902120B* | 24200 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
214392379 | 1.8 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30B34+TDR | R802V0754A17UHN | 21600 | 19 | 10 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18900 | R-410A
215375343 | 3.67 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ48AJ3N | D(A,C,E)48B46+TDR | R962V1155A24M4S | 44000 | 16 | 10 | 8.1 | 45500 | 32400 | 71.21% | 2.4 | 25400 | R-410A
211260399 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 82*TA36070V14*** | 17700 | 16.5 | 10.5 | 8.5 | 18500 | 19100 | 103.2% | 2.3 | 12400 | R-410A
211260481 | 1.45 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 926TB30040V14*** | 17400 | 16 | 10.5 | 8.5 | 18300 | 19200 | 104.9% | 2.3 | 12300 | R-410A
215683893 | 2.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 58CU*A060C17**16 | 34400 | 18 | 9.5 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
211261517 | 1.49 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 82*SA36045V14*** | 17900 | 16 | 10.5 | 8.5 | 18400 | 18500 | 100.5% | 2.22 | 12400 | R-410A
215375366 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R802V1505A24UHS | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 50500 | 94.39% | 1.75 | 49000 | R-410A
216735846 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | EA*5X37M21A* | *96MSN1002120A* | 23400 | 16 | 11 | 8.5 | 20800 | 18500 | 88.94% | 1.98 | 17600 | R-454B
215683637 | 1.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3017AM*+UI | 59TN6C040C14**10 | 22600 | 15.5 | 9 | 8.5 | 24400 | 17100 | 70.08% | 1.84 | 20400 | R-454B
215683653 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3617AM*+UI | 58TN*B090C17**16 | 23200 | 17 | 10.5 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215683703 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 59CU5B100C21**22 | 24000 | 17 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215674486 | 3.83 | No | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL0902120B* | 46000 | 18.5 | 10 | 9 | 48000 | 33600 | 70% | 2.08 | 42000 | R-454B
215674640 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *96CTN1002122B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
215674981 | 3.71 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X48M12A*+WALLCON | *97CMN0801714B* | 44500 | 16 | 9 | 8.5 | 49500 | 34800 | 70.3% | 1.92 | 43500 | R-454B
213892611 | 1.88 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CAP**2414AL*+UI | 986TD30040C14*** | 22600 | 17.5 | 11.5 | 9.5 | 27400 | 20800 | 75.91% | 2.2 | 25800 | R-410A
215668828 | 2.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CTL0702120B* | 33000 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
213892613 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CAP**2517AL*+UI | 986TD30040C14*** | 23600 | 18 | 12 | 10 | 26800 | 20400 | 76.12% | 2.4 | 25400 | R-410A
215675365 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X48M21A*+WALLCON | *80CSU0802120A* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
215675265 | 3.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0602120B* | 45000 | 16 | 9 | 8.5 | 48500 | 34200 | 70.52% | 1.96 | 42500 | R-454B
212362569 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VS960805CUA* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362594 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | A*VM970804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213892619 | 1.95 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 284ANV024*0**B* | CSPH*4212AL*+UI | 986TD30040C14*** | 23400 | 17 | 11.7 | 10 | 26800 | 20200 | 75.37% | 2.4 | 25400 | R-410A
213892582 | 1.08 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV013*0**A* | CAP**1917AL*+UI | 986TD30040C14*** | 13000 | 15.5 | 12 | 8.1 | 11800 | 8800 | 74.58% | 1.98 | 11200 | R-410A
212362619 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VC800804C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362621 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VC800805C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215375182 | 2.75 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36C46+TDR | R951V0403A17UHU | 33000 | 18 | 10 | 8.1 | 34200 | 31600 | 92.4% | 1.9 | 29800 | R-410A
214394757 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R962V1005A21M4S | 51500 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 51000 | R-410A
214394762 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R962V1155A24M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214394791 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | U98MV1005A21UPS | 51500 | 16.9 | 9.8 | 8.1 | 54500 | 49500 | 90.83% | 1.75 | 51000 | R-410A
214394730 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R921V1155A24M4S | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49000 | 90.74% | 1.75 | 50500 | R-410A
214392642 | 1.75 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36D24+TDR | U802VA075317M | 21000 | 18.9 | 9.8 | 8.1 | 22600 | 16800 | 74.34% | 2.1 | 18800 | R-410A
213367398 | 2.4 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ30AB3* | H,PG31930 | 59TP6C100V21**22 | 28800 | 15.2 | 8.5 | 8.1 | 32600 | 27600 | 84.66% | 1.78 | 22600 | R-410A
215375377 | 4.29 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D36+TDR | R962V0855A21M4S | 51500 | 16.9 | 9.8 | 8.1 | 54000 | 51000 | 94.44% | 1.75 | 49500 | R-410A
215668540 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *80CSU0601716A* | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.88 | 30800 | R-454B
214394611 | 2.77 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)36D44+TDR | U98MV1005A21UPS | 33200 | 18 | 10 | 8.1 | 34200 | 29600 | 86.55% | 1.9 | 31400 | R-410A
215684023 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 58TN*B090C21**20 | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30800 | R-454B
216796570 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S8X2C100M5PSC | 31200 | 15.2 | 11.7 | 8.5 | 31400 | 22400 | 71.34% | 3 | 21800 | R-454B
216796656 | 2.65 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2C080U5PSC | 31800 | 15.5 | 12 | 8.5 | 31200 | 22200 | 71.15% | 3.01 | 21600 | R-454B
216796738 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9X1C100D5PSB | 31600 | 15.5 | 12 | 8.1 | 32200 | 22600 | 70.19% | 2.87 | 22200 | R-454B
211260095 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2414AL* | 926SA36060V14*** | 17800 | 16 | 10.5 | 8.5 | 18800 | 19000 | 101.1% | 2.28 | 12500 | R-410A
216680604 | 1.98 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EHD4X36AAL | *97VTN0801716A* | 23800 | 16 | 10 | 8.5 | 25200 | 22400 | 88.89% | 1.75 | 18700 | R-410A
214394538 | 2.73 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ36AJ3N | D(A,C,E)48C34+TDR | U98MV0603A17UPS | 32800 | 18 | 10 | 8.1 | 34200 | 29800 | 87.13% | 1.9 | 31600 | R-410A
213773017 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *96CTN0601714B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213773167 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L17A*+WALLCON | *80CTL0701412B* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20600 | R-410A
213773237 | 2 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L17A*+WALLCON | *96CTN0601714B* | 24000 | 16 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.98 | 20800 | R-410A
213772967 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0901716B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.92 | 20800 | R-410A
213773337 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *97CMN1002122B* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213773437 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L21A*+WALLCON | *97CMN0601714B* | 23600 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.94 | 20800 | R-410A
214573529 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CNPV*4824AL*+UI | 987MC60080C21*** | 32400 | 17.5 | 11.5 | 8.5 | 32800 | 24800 | 75.61% | 1.96 | 31600 | R-410A
211263549 | 1.51 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | OLV098A12* | 18100 | 15.5 | 10.5 | 8.5 | 19100 | 18700 | 97.91% | 2.24 | 12700 | R-410A
211264760 | 1.45 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | FEM4P18**AL |  | 17400 | 16 | 10.5 | 8.5 | 18300 | 19400 | 106% | 2.34 | 12300 | R-410A
215676275 | 3.92 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVD5X48M24A*+WALLCON | *96CTN1202422B* | 47000 | 18.5 | 10 | 9 | 50000 | 36400 | 72.8% | 2 | 45500 | R-454B
213311584 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | C36A***L139+CBPE4B* |  | 23800 | 18 | 10 | 8.75 | 25000 | 22600 | 90.4% | 1.88 | 18300 | R-410A
214570483 | 2.03 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X37L21A*+WALLCON | *96CTN0802120B* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
214570633 | 2.03 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EA*4X43L21A*+WALLCON | *95CSU1002122B* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
216683456 | 1.45 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EHD4X24AAL | *97VTN1202422A* | 17400 | 15.2 | 10 | 8.1 | 18100 | 18400 | 101.7% | 2.05 | 12300 | R-410A
212979204 | 1.93 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*2417AL* | 8(0,1)*SB48070M17*** | 23200 | 16.5 | 10 | 8.5 | 26800 | 25400 | 94.78% | 2.14 | 19400 | R-410A
214242260 | 2 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X48L21**+WALLCON | *95CSU0601716B* | 24000 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
214242290 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D,W)4X48L21**+WALLCON | *97CMN1002122B* | 24200 | 17 | 11.5 | 8.1 | 21200 | 16500 | 77.83% | 2 | 20600 | R-410A
214242360 | 2.02 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D)4X48L24**+WALLCON | *97CMN1002122B* | 24200 | 17 | 11.5 | 8.1 | 21200 | 16500 | 77.83% | 2 | 20600 | R-410A
216796543 | 2.65 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S8X1D120M5PSC | 31800 | 16 | 11.7 | 8.5 | 31400 | 22000 | 70.06% | 2.94 | 21600 | R-454B
216796609 | 2.63 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)48C3J+TDR | S9V2B060D3PSC | 31600 | 15.5 | 12 | 8.1 | 32200 | 22600 | 70.19% | 2.85 | 22200 | R-454B
216796677 | 2.6 | Yes | No | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWR5036A1 | D(A,C,E)36C3J+TDR | S9V2C100U4VSB | 31200 | 15.2 | 12 | 8.5 | 31200 | 22200 | 71.15% | 3 | 21600 | R-454B
212974636 | 1.44 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L14A* | *96VTN0401410B* | 17300 | 15.5 | 10.5 | 8.5 | 18400 | 19400 | 105.4% | 2.32 | 12400 | R-410A
212974753 | 1.45 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X30L17** | *96VTN0401410B* | 17400 | 16 | 10.5 | 8.1 | 18000 | 18700 | 103.9% | 2.24 | 12200 | R-410A
206765433 | 1.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *96CTN0601714A* | 23200 | 16 | 10.5 | 8.1 | 22000 | 16900 | 76.82% | 1.88 | 21200 | R-410A
212517498 | 2.78 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CV365*9 | YP9C100C20MP13 | 33400 | 17 | 9.5 | 8.5 | 32400 | 23200 | 71.6% | 2.06 | 26000 | R-410A
212517499 | 2.78 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CH367C9 | YP9C100C20MP13 | 33400 | 17 | 9.5 | 8.5 | 32400 | 23200 | 71.6% | 2.06 | 26000 | R-410A
206765683 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *97CMN0601714A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.92 | 20800 | R-410A
206765890 | 2 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L17A*+WALLCON | *97CMN0601714A* | 24000 | 16 | 10.5 | 8.1 | 21600 | 16900 | 78.24% | 1.98 | 20800 | R-410A
215932506 | 2.75 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X48M21A*+WALLCON | *96CTN0601714B* | 33000 | 19.5 | 11 | 9.5 | 34000 | 26000 | 76.47% | 2.04 | 29800 | R-454B
215932606 | 2.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 34000 | 20 | 11.7 | 9.5 | 34200 | 26000 | 76.02% | 2.06 | 29800 | R-454B
216453217 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X60A1 | 5PX*C007AS3 | S8V2C100M5PDB | 51500 | 18.2 | 10 | 9 | 54500 | 38500 | 70.64% | 2 | 48000 | R-454B
216453249 | 4.29 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X60A1 | 5PX*DD10AS3 | S8V2C100M5PDB | 51500 | 18.2 | 10 | 9 | 53500 | 38000 | 71.03% | 2 | 47500 | R-454B
212362775 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VS960603BUA* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362806 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+MBVC1201**-1A*+TXV |  | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362807 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+MBVC1601**-1A*+TXV |  | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362626 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VC960803BNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216794432 | 2.67 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X36A1 | D(A,C,E)48C3J+TDR | S9V2C080U5VSB+LRP | 32000 | 19.9 | 12 | 9 | 32200 | 30200 | 93.79% | 2.77 | 36600 | R-454B
214228975 | 1.51 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X19L17A* | *80MSU0601716A* | 18100 | 16.5 | 11 | 8.5 | 18000 | 17700 | 98.33% | 2.14 | 12200 | R-410A
212979240 | 1.97 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | CNPV*3621AL* | 8(0,1)*SB48070M17*** | 23600 | 17 | 10.5 | 8.5 | 26400 | 24200 | 91.67% | 2.02 | 19100 | R-410A
213281586 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)48B44+TDR | Y81E120C16SMPS1 | 34000 | 17.5 | 8.5 | 8.1 | 36000 | 25400 | 70.56% | 2.65 | 24800 | R-410A
214573643 | 2.62 | Yes | No | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X36L21A*+WALLCON | *97CMN0602120B* | 31400 | 17 | 10.5 | 8.1 | 33200 | 24400 | 73.49% | 1.84 | 31400 | R-410A
214572873 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X48L24A*+WALLCON | *97CMN0802120B* | 32400 | 17.5 | 11 | 8.5 | 32400 | 25000 | 77.16% | 1.98 | 31400 | R-410A
214572923 | 2.72 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EA*4X60L24A*+WALLCON | *97CMN0602120B* | 32600 | 17.5 | 11 | 8.5 | 31800 | 25000 | 78.62% | 1.96 | 31200 | R-410A
214573273 | 2.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EHD4X60AAL+WALLCON | *95CSU1002122B* | 33000 | 18 | 11.5 | 8.5 | 32000 | 24800 | 77.5% | 2.02 | 31200 | R-410A
214573573 | 2.73 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA** | EN(A,D,W)4X60L24**+WALLCON | *95CSU1002122B* | 32800 | 19 | 12 | 8.5 | 32200 | 24600 | 76.4% | 1.98 | 31200 | R-410A
214807379 | 2.87 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTU48C5XFS1+JMC17C2SN1+TXV |  | 34400 | 19 | 11.7 | 9 | 32000 | 25200 | 78.75% | 2 | 25800 | R-454B
211260263 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 926SA42060V17*** | 17700 | 16 | 10.5 | 8.5 | 18600 | 19100 | 102.7% | 2.3 | 12400 | R-410A
211260429 | 1.44 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 82*TA48070V17*** | 17300 | 16 | 10.5 | 8.5 | 18100 | 19200 | 106.1% | 2.32 | 12200 | R-410A
211261045 | 1.53 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2517AL* | 912SD30040E14*** | 18400 | 15.5 | 10.5 | 8.5 | 18400 | 17500 | 95.11% | 2.12 | 12400 | R-410A
214392673 | 1.73 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)36C24+TDR | U97MV0603A17DHS | 20800 | 18.8 | 9.7 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
213772627 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *80CTL0701412B* | 23400 | 16.5 | 10.5 | 8.1 | 22000 | 16800 | 76.36% | 1.88 | 21000 | R-410A
213772727 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0701412B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
215675325 | 3.79 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *96CTN1002122B* | 45500 | 16.5 | 9.5 | 8.5 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215675505 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *80CSU0802120A* | 48000 | 19 | 10 | 9 | 50000 | 36600 | 73.2% | 2.12 | 46000 | R-454B
213773127 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *96CTN0601714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213773527 | 1.98 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L24A*+WALLCON | *97CMN1002122B* | 23800 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
213773597 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X43L21A*+WALLCON | *80CTL0902120B* | 24400 | 17 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213773677 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X43L21A*+WALLCON | *96CTN1002122B* | 24400 | 16.5 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
216680848 | 1.43 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *97VTN0801716A* | 17200 | 16 | 10.5 | 8.5 | 18100 | 19200 | 106.1% | 2.2 | 12200 | R-410A
206765503 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0701716A* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213773667 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X43L21A*+WALLCON | *96CTN0801714B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
216679728 | 1.47 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X30L17A* | *97VTN0601716A* | 17600 | 16 | 10.5 | 8.5 | 18100 | 18300 | 101.1% | 2.12 | 12200 | R-410A
212290953 | 1.38 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA1818*4A* | A*VS960603BUA* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
212290968 | 1.38 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS601810A* | CA*EA2422*4A* | A*VC960603BNB* | 16600 | 17.5 | 10.9 | 8.5 | 17400 | 13000 | 74.71% | 2.1 | 10800 | R-410A
214421490 | 4.46 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X60A1 | V,T60H245P189+P0V0D000M50SC+RP |  | 53500 | 18 | 12 | 8.2 | 49500 | 38500 | 77.78% | 1.75 | 48500 | R-410A
206765460 | 1.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *97CMN0801714A* | 23200 | 16 | 10.5 | 8.1 | 22000 | 16900 | 76.82% | 1.88 | 21200 | R-410A
206765593 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *96CTN0601714A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.9 | 20800 | R-410A
215940319 | 2.97 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V36*K*AAA* | EVM5X44M21A*+WALLCON | *97CTN1002122A* | 35600 | 22 | 12.5 | 8.5 | 38000 | 28600 | 75.26% | 2.02 | 32600 | R-454B
213773587 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X43L21A*+WALLCON | *80CTL0901716B* | 24200 | 17 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2.02 | 20600 | R-410A
215675615 | 3.96 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X49M21A*+WALLCON | *97CMN0801714B* | 47500 | 18.5 | 10 | 9 | 50000 | 37400 | 74.8% | 1.98 | 47000 | R-454B
211259871 | 1.52 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**1917AL* | 926TB42060V17*** | 18200 | 16 | 10.5 | 8.5 | 18200 | 17700 | 97.25% | 2.14 | 12300 | R-410A
211260623 | 1.47 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 8(0,1)*SA36070E14*** | 17600 | 16 | 10.5 | 8.5 | 18400 | 19100 | 103.8% | 2.3 | 12400 | R-410A
205751066 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X37L21A*+WALLCON | *97CMN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
214571249 | 2.02 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV025*0**C* | CNPV*4821AL*+UI | 987MC60080C21*** | 24200 | 17 | 11.5 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
213613571 | 1.5 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M36A4 |  | 18000 | 15.2 | 10 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
213613575 | 1.5 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M36E4 |  | 18000 | 15.2 | 10 | 8.5 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
216761978 | 2.12 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG9J936 | 927TA48080V17*** | 25400 | 18 | 11.5 | 10 | 24200 | 33200 | 137.2% | 2.54 | 18600 | R-410A
213773027 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *96CTN0801714B* | 23600 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
214389735 | 1.92 | No | Yes | Liberty Heating & Air Conditioning | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZS60241EA* | CA*EA3026*4A* | G*VS960805CUA* | 23000 | 17 | 10 | 8.6 | 23000 | 16100 | 70% | 2 | 16000 | R-410A
216978077 | 2.87 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LD24/35Z*+TXV | SL297UH060NV36B* | 34400 | 17 | 11 | 8.5 | 34000 | 28000 | 82.35% | 1.85 | 27800 | R-454B
213773777 | 2 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L21A*+WALLCON | *96CTN0601714B* | 24000 | 16.5 | 10.5 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
213773427 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L21A*+WALLCON | *95CSU0601716B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.94 | 20800 | R-410A
213772987 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *97CMN0601714B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213773387 | 1.98 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L21A*+WALLCON | *80CTL0701716B* | 23800 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
213773537 | 1.98 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L24A*+WALLCON | *97CMN1202422B* | 23800 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.96 | 20600 | R-410A
213773637 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X43L21A*+WALLCON | *97CMN0801714B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
215668604 | 2.72 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *96CTN0401410B* | 32600 | 16 | 9.5 | 8.5 | 36200 | 25600 | 70.72% | 1.76 | 31000 | R-454B
215668788 | 2.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0401712A* | 33000 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
207573703 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG86960 | *80CTL0902120A* | 45500 | 17 | 10 | 8.5 | 43500 | 34400 | 79.08% | 2 | 34400 | R-410A
207573712 | 3.83 | Yes | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG86960 | *80CTL1102120A* | 46000 | 17 | 10 | 8.1 | 44000 | 31600 | 71.82% | 2.26 | 35200 | R-410A
207573728 | 3.75 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG36960 | *95CSU1002122A* | 45000 | 17 | 10 | 8.5 | 45000 | 32400 | 72% | 2.28 | 36000 | R-410A
207573748 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG84948 | *96CTN1002122A* | 45500 | 17 | 10 | 8.5 | 43500 | 34400 | 79.08% | 2 | 34400 | R-410A
207573771 | 3.71 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | PL48H210P299 | *97CMN1002122A* | 44500 | 17 | 10 | 8.5 | 44500 | 34600 | 77.75% | 2 | 34600 | R-410A
207573778 | 3.79 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH848GKA2* | FG84960 | *97CMN1002122A* | 45500 | 17 | 10 | 8.5 | 43500 | 34400 | 79.08% | 2 | 34400 | R-410A
213772617 | 1.93 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *80CTL0451712B* | 23200 | 16 | 10 | 8.1 | 22000 | 16900 | 76.82% | 1.88 | 21200 | R-410A
213772667 | 1.92 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *97CMN0601714B* | 23000 | 16 | 10 | 8.1 | 22000 | 16900 | 76.82% | 1.88 | 21000 | R-410A
213773217 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L17A*+WALLCON | *97CMN0801714B* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.98 | 20800 | R-410A
215674579 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN0802120B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
207573539 | 2.7 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | PL36H210P299 | *80CSU0401712A* | 32400 | 18 | 11 | 8.1 | 30400 | 27200 | 89.47% | 2.22 | 30400 | R-410A
216504988 | 2.68 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A36+TDR | Y91E060B12SMPS1 | 32200 | 16 | 8.3 | 8.1 | 36000 | 26400 | 73.33% | 2.69 | 25400 | R-410A
214571133 | 1.95 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH825GKA3* | EN(A,D)4X36L21**+WALLCON | *97CMN0802120B* | 23400 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
216738927 | 1.88 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CUHAH24AAK | ESH5X36M12A* | *97VTN1002120A* | 22600 | 16 | 11 | 8.1 | 20800 | 18400 | 88.46% | 1.85 | 17500 | R-454B
215683597 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**2517AM*+UI | 58CU*A040C17**12 | 24000 | 17.5 | 10.5 | 9 | 23400 | 16400 | 70.09% | 2.02 | 19700 | R-454B
215674496 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1102120B* | 46000 | 18.5 | 10 | 9 | 47500 | 33600 | 70.74% | 2.08 | 42000 | R-454B
213367339 | 1.45 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG9J936 | 59TP6C060V17**16 | 17400 | 16 | 10.5 | 8.5 | 16800 | 19100 | 113.7% | 2.34 | 11400 | R-410A
213367341 | 1.48 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | H,PG9J936 | 59TP6C080V17**16 | 17700 | 16 | 11 | 8.5 | 17100 | 18700 | 109.4% | 2.3 | 11500 | R-410A
214568839 | 2.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA837A*031* | H,PE9J936 | 59TN6B100C21**22 | 32000 | 17 | 11.5 | 8.5 | 31000 | 24400 | 78.71% | 2 | 30400 | R-410A
207820956 | 4.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X60A1 | TEM6B0C60H51+TDR+RP |  | 54000 | 18 | 12 | 8.5 | 52500 | 38000 | 72.38% | 1.8 | 48500 | R-410A
215683661 | 1.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3617AM*+UI | 59TN6C060C17**14 | 23000 | 17 | 10 | 9 | 23800 | 16700 | 70.17% | 1.96 | 20000 | R-454B
215683681 | 1.95 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3717AM*+UI | 59TN6C040C14**10 | 23400 | 16 | 9.5 | 9 | 24000 | 16900 | 70.42% | 1.98 | 20200 | R-454B
215675155 | 3.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *80CTL0451712B* | 45000 | 15.5 | 9 | 8.5 | 48500 | 34600 | 71.34% | 1.94 | 43000 | R-454B
215675275 | 3.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | ESH5X60M12A*+WALLCON | *97CMN0801714B* | 45000 | 16 | 9 | 8.5 | 48500 | 34200 | 70.52% | 1.94 | 42500 | R-454B
214628967 | 2.9 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H175P149 | 58S(B,C)*B045M14**12 | 34800 | 15.2 | 9.5 | 8.5 | 36800 | 34800 | 94.57% | 2 | 28400 | R-410A
214629000 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H***P449 | 58S(B,C)*B070M14**12 | 35000 | 16 | 9.5 | 8.1 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
214629102 | 2.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P749 | 58S(B,C)*B090M17**14 | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
214629117 | 3 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | PL36H210P299 | 58S(B,C)*B090M21**20 | 36000 | 16 | 10.5 | 8.1 | 36800 | 34600 | 94.02% | 2 | 28200 | R-410A
214629151 | 2.88 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | V,C36H***P219 | 58TP*B045V14**12 | 34600 | 16 | 9.5 | 8.1 | 36800 | 34600 | 94.02% | 1.94 | 28400 | R-410A
215683881 | 2.8 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3717AM*+UI | 59MN7C060C17**14 | 33600 | 17 | 9.5 | 9 | 36000 | 25800 | 71.67% | 1.86 | 31000 | R-454B
215683711 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 59MN7C100C21**22 | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
215684031 | 2.8 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*3612AM*+UI | 59CU5B080C21**20 | 33600 | 16 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215684097 | 2.82 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*4212AM*+UI | 59TN6C080C17**14 | 33800 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30800 | R-454B
212362564 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VC960403BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362616 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+MBVC1601**-1A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
206133327 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X25L17A*+WALLCON | *80CSU0601716A* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
206133427 | 2.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L17A*+WALLCON | *80CSU0601716A* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
211261426 | 1.52 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3014AL* | 8(0,1)*SA36045E14*** | 18200 | 16.5 | 10.5 | 8.5 | 18600 | 18400 | 98.92% | 2.22 | 12500 | R-410A
215668588 | 2.8 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0601714B* | 33600 | 17 | 9.5 | 9 | 36000 | 25800 | 71.67% | 1.86 | 31000 | R-454B
215674203 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *80CTL1102120B* | 45000 | 18 | 10 | 9 | 47500 | 33400 | 70.32% | 2.08 | 41500 | R-454B
215674253 | 3.75 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 45000 | 18 | 10 | 9 | 47500 | 33600 | 70.74% | 2.06 | 42000 | R-454B
214394774 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | U802VA125524Z | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
212632744 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Y9 | SL280DF090V60C* | 33400 | 20 | 13 | 8.7 | 34400 | 28800 | 83.72% | 1.76 | 32600 | R-410A
212632751 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD30/36Z9 | SLP99DF070XV36B* | 33400 | 21 | 12.5 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 33000 | R-410A
212632708 | 2.77 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Y9 | EL296DF070XV48B* | 33200 | 20 | 12.5 | 8.6 | 34400 | 29600 | 86.05% | 1.76 | 33000 | R-410A
211260909 | 1.53 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2517AL* | 915SB36060E14*** | 18400 | 16.5 | 11 | 8.5 | 18200 | 17500 | 96.15% | 2.12 | 12300 | R-410A
214573999 | 2.68 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**B* | CAP**4824AL*+UI | 987MC60060C21*** | 32200 | 17 | 11 | 8.5 | 32600 | 25200 | 77.3% | 1.96 | 31600 | R-410A
212362773 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VC801005C*A* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
211260387 | 1.47 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 82*TA36045V14*** | 17600 | 16.5 | 10.5 | 8.5 | 18500 | 19100 | 103.2% | 2.3 | 12400 | R-410A
211260403 | 1.48 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 926TB36040V17*** | 17700 | 15.5 | 10.5 | 8.5 | 18700 | 19100 | 102.1% | 2.28 | 12500 | R-410A
211260120 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2414AL* | 82*TA36070V14*** | 17700 | 16 | 10.5 | 8.5 | 18500 | 19100 | 103.2% | 2.3 | 12400 | R-410A
213613570 | 1.5 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24K4 |  | 18000 | 15.2 | 10 | 9 | 19300 | 18300 | 94.82% | 2.2 | 12800 | R-410A
212632731 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Z9 | SL280DF080NV60C* | 33400 | 20 | 13 | 8.6 | 34400 | 28800 | 83.72% | 1.76 | 32800 | R-410A
212632749 | 2.8 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Z9 | SL280DF110V60C* | 33600 | 20 | 13 | 8.7 | 34400 | 28800 | 83.72% | 1.76 | 32600 | R-410A
216453201 | 3.75 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5TWV0X48A1 | 5TXCD008AS3 | S8V2D120M5PCB | 45000 | 20.2 | 12 | 10 | 47500 | 34000 | 71.58% | 2.1 | 43000 | R-454B
214629187 | 2.98 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L159 | 58TP*B110V21**22 | 35800 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.9 | 28400 | R-410A
216551803 | 3.79 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP19AY48AJVC | TCFY4821SEAAM | FR802V1005A21UH | 45500 | 19 | 12 | 10 | 45500 | 41500 | 91.21% | 2.1 | 42000 | R-454B
211260519 | 1.47 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 926TB42060V17*** | 17600 | 15.5 | 10.5 | 8.5 | 18600 | 19100 | 102.7% | 2.3 | 12400 | R-410A
211260637 | 1.54 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2417AL* | 83*SA48060E17*** | 18500 | 16 | 10.5 | 9 | 19400 | 18600 | 95.88% | 2.26 | 12800 | R-410A
211260937 | 1.54 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2517AL* | 926TB36060V14*** | 18500 | 16 | 11 | 8.5 | 18300 | 17400 | 95.08% | 2.12 | 12300 | R-410A
211261057 | 1.53 | Yes | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2517AL* | 912SD36040E17*** | 18400 | 15.5 | 10.5 | 8.5 | 18300 | 17500 | 95.63% | 2.12 | 12400 | R-410A
216819136 | 1.75 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2417MTANM | FR98MV0603A17UP | 21000 | 18 | 10 | 8.1 | 21000 | 17000 | 80.95% | 1.9 | 18200 | R-454B
211261241 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3014AL* | 82*SA36045V14*** | 17800 | 16 | 10.5 | 8.5 | 18400 | 18500 | 100.5% | 2.22 | 12400 | R-410A
216551796 | 3.79 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP19AY48AJVC | TCFY4821SEAAM | FR802V0754A17UH | 45500 | 19 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
216551811 | 3.79 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP19AY48AJVC | TCFY4821SEAAM | FR962V0705A21M4 | 45500 | 18 | 12 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
214392620 | 1.7 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ24AJ3N | D(A,C,E)30C24+TDR | U802VA050317M | 20400 | 18.6 | 9 | 8.1 | 22600 | 16900 | 74.78% | 2 | 19000 | R-410A
215932706 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *80CTL0702120B* | 34400 | 20.5 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.96 | 30000 | R-454B
215932756 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU0802120B* | 34400 | 20 | 11.7 | 9 | 34400 | 26200 | 76.16% | 1.96 | 30000 | R-454B
215932826 | 2.85 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | EA*5X61M21A*+WALLCON | *96CTN0801714B* | 34200 | 20 | 11.5 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30200 | R-454B
215933476 | 2.78 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | ESH5X42M12A*+WALLCON | *96CTN0801714B* | 33400 | 19 | 11 | 9 | 35000 | 26800 | 76.57% | 1.9 | 30800 | R-454B
215295609 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG9J936 | *96VTN1002120B* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215295668 | 2.93 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HE33936 | *96VTN1002122B* | 35200 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215295682 | 3 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG48936 | *96VTN1002122B* | 36000 | 17 | 10.5 | 8.1 | 36800 | 34400 | 93.48% | 2 | 28200 | R-410A
215295709 | 2.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HG33936 | *96VTN1202422A* | 35400 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
213773787 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L21A*+WALLCON | *96CTN0801714B* | 24000 | 16.5 | 11 | 8.1 | 21000 | 16600 | 79.05% | 2 | 20400 | R-410A
214649696 | 2.83 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48D44+TDR | MGH96M060B3A | 34000 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
214572919 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 288BNV037*0**A* | CAP**6024AL*+UI | 987MC60060C21*** | 32600 | 17.5 | 11 | 8.5 | 31800 | 25000 | 78.62% | 1.96 | 31200 | R-410A
213773327 | 2.03 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *97CMN0801714B* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
214649704 | 2.77 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48C34+TDR | MGH96M080C4A | 33200 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
215668580 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *95CSU0601716B* | 33800 | 17 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
212632762 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Y9 | SLP99DF090XV48C* | 33400 | 21 | 12.5 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 33000 | R-410A
216677594 | 2.03 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X37M17A* | *96VSN0801716B* | 24400 | 15.5 | 10 | 8.5 | 23600 | 19300 | 81.78% | 1.94 | 18700 | R-454B
212973881 | 2.02 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X37L17A* | *96VSN0801716B* | 24200 | 17 | 10 | 8.5 | 25800 | 21200 | 82.17% | 1.78 | 18700 | R-410A
212974970 | 1.95 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH24ABK | EA*4X30L17A* | *96VTN0401410B* | 23400 | 16 | 10 | 8.5 | 26400 | 24800 | 93.94% | 2.06 | 19200 | R-410A
212975121 | 1.46 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *96VTN0401712B* | 17500 | 15.5 | 10.5 | 8.5 | 18600 | 18600 | 100% | 2.22 | 12200 | R-410A
212973381 | 1.46 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EN(A,D)4X24L17** | *96VSN0601412B* | 17500 | 16 | 10.5 | 8.5 | 18500 | 18700 | 101.1% | 2.24 | 12200 | R-410A
215674620 | 3.83 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EA*5X61M24A*+WALLCON | *97CMN1202422B* | 46000 | 18 | 10 | 9 | 48000 | 33800 | 70.42% | 2.08 | 42000 | R-454B
215295736 | 3 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GG81936 | *96VTN1202422A* | 36000 | 16 | 10 | 8.5 | 36800 | 34200 | 92.93% | 2.06 | 28000 | R-410A
215295753 | 2.88 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HE34936 | *96VTN1202422B* | 34600 | 16 | 9.5 | 8.5 | 36200 | 34200 | 94.48% | 2.02 | 28000 | R-410A
214394639 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V0755A21UHN | 52000 | 17.8 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214394648 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R801V1005A21DZ | 52000 | 17.9 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394671 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D34+TDR | R801V1505A24UH | 52000 | 17.8 | 9.8 | 8.1 | 53500 | 49000 | 91.59% | 1.75 | 50500 | R-410A
214394680 | 4.33 | No | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD17AZ60AJ3N | D(A,C,E)60D44+TDR | R802V0755A21UHN | 52000 | 17.9 | 9.8 | 8.1 | 54000 | 49500 | 91.67% | 1.75 | 50500 | R-410A
214649703 | 2.8 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36D44+TDR | MGH96M080C4A | 33600 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
214573673 | 2.73 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X37L21A*+WALLCON | *80CTL0702120B* | 32800 | 17.5 | 11 | 8.5 | 32800 | 25200 | 76.83% | 2 | 31800 | R-410A
214573743 | 2.65 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X42L21A*+WALLCON | *95CSU0802120B* | 31800 | 17 | 11 | 8.5 | 33000 | 24400 | 73.94% | 1.9 | 31400 | R-410A
215668596 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *97CMN0801714B* | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
216984603 | 2.7 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | PL36H210P74*+TXV | 987TA42060C17*** | 32400 | 19 | 10.5 | 9 | 34000 | 27000 | 79.41% | 1.88 | 30400 | R-454B
213367405 | 2.97 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | H,PG9J936 | 59TP6C080V21**20 | 35600 | 16 | 10 | 8.1 | 36800 | 34800 | 94.57% | 1.9 | 28400 | R-410A
206771588 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L24A*+WALLCON | *96CTN1002122A* | 31800 | 17.5 | 11.5 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
213355418 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | L(E,G)M36F6 |  | 33000 | 17 | 9.5 | 8.1 | 31800 | 27000 | 84.91% | 2.73 | 24600 | R-410A
214649709 | 2.8 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48C34+TDR | MGH96M100C5A | 33600 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
214649710 | 2.88 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48D44+TDR | MGH96M100C5A | 34600 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
214629301 | 2.92 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | A36VCA+TXV | 59SU5B060M17**16 | 35000 | 16 | 9.5 | 8.1 | 36800 | 34600 | 94.02% | 1.86 | 28400 | R-410A
213772677 | 1.93 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X24L17A*+WALLCON | *97CMN0801714B* | 23200 | 16 | 10.5 | 8.1 | 22000 | 16800 | 76.36% | 1.88 | 21000 | R-410A
213772927 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *96CTN0801714B* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.9 | 20800 | R-410A
215668628 | 2.87 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *80CSU0401712A* | 34400 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
211261179 | 1.57 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**2517AL* | OVMAAB036098 | 18800 | 16 | 11 | 8.5 | 18700 | 17300 | 92.51% | 2.12 | 12500 | R-410A
211261296 | 1.48 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3014AL* | 82*TA36045V14*** | 17800 | 16.5 | 10.5 | 8.5 | 18200 | 18500 | 101.6% | 2.22 | 12300 | R-410A
214649702 | 2.72 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36C34+TDR | MGH96M080C4A | 32600 | 16.5 | 11 | 8.3 | 34400 | 26200 | 76.16% | 2.39 | 24800 | R-410A
212362567 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VC960803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362615 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+MBVC1201**-1A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214608689 | 2.65 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B34+TDR | CP9C080B12MP13 | 31800 | 17.5 | 9.9 | 8.5 | 33400 | 23400 | 70.06% | 2.04 | 25000 | R-410A
216977230 | 2.9 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-036-230A** | LH29/36F*+TXV | SL297UH080NV48C* | 34800 | 17 | 11 | 9 | 34200 | 28000 | 81.87% | 1.9 | 27600 | R-454B
206765493 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0451712A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16800 | 78.5% | 2 | 20800 | R-410A
214595149 | 1.85 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | A(E,F)M254+TDR |  | 22200 | 15.2 | 9.8 | 8.5 | 26200 | 23400 | 89.31% | 1.92 | 19200 | R-410A
214649698 | 2.78 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36D44+TDR | MGH96M080B3A | 33400 | 16.5 | 11.7 | 8.5 | 34400 | 25800 | 75% | 2.3 | 24600 | R-410A
214649700 | 2.82 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48D44+TDR | MGH96M080B3A | 33800 | 16.5 | 11.7 | 8.5 | 34400 | 25800 | 75% | 2.3 | 24600 | R-410A
214649699 | 2.75 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48C34+TDR | MGH96M080B3A | 33000 | 16.5 | 11.7 | 8.5 | 34400 | 25800 | 75% | 2.3 | 24600 | R-410A
206765845 | 1.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *97CMN0602120A* | 23600 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
206765863 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L17A*+WALLCON | *80CTL0701716A* | 24200 | 16.5 | 11 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
206766864 | 1.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EHD4X30AAL+WALLCON | *80CTL0701412A* | 23800 | 16 | 10.5 | 8.1 | 21800 | 16700 | 76.61% | 1.98 | 20800 | R-410A
216677994 | 1.97 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X36M17A* | *96VTN0601412B* | 23600 | 15.2 | 9.8 | 8.5 | 24000 | 19400 | 80.83% | 1.9 | 18900 | R-454B
216678273 | 2.03 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | D5CURAH24AAK | EA*5X37M21A* | *97VTN0601716A* | 24400 | 15.5 | 10 | 8.5 | 23000 | 19000 | 82.61% | 1.96 | 18400 | R-454B
211261606 | 1.5 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 926SA36060V14*** | 18000 | 16 | 10.5 | 8.5 | 18600 | 18500 | 99.46% | 2.22 | 12500 | R-410A
211261825 | 1.46 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 82*TA48070V17*** | 17500 | 16.5 | 10.5 | 8.5 | 17900 | 18600 | 103.9% | 2.24 | 12200 | R-410A
215668804 | 2.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU1002120A* | 33000 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215669231 | 2.8 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X48M21A*+WALLCON | *97CMN0602120B* | 33600 | 17.5 | 9.5 | 9 | 35200 | 25200 | 71.59% | 1.9 | 30400 | R-454B
215683573 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**2414AM*+UI | 58TN*B070C14**12 | 22800 | 17 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
212614364 | 2.48 | No | No | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH30ABK | F,PE*E33936 |  | 29800 | 15.2 | 8.5 | 8.3 | 33400 | 27000 | 80.84% | 1.78 | 22600 | R-410A
214807390 | 4.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTU60D5XHS1+JMC20D2SN1+TXV |  | 53000 | 19 | 12 | 8.5 | 53000 | 38000 | 71.7% | 2 | 36600 | R-454B
214649707 | 2.75 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36C34+TDR | MGH96M100C5A | 33000 | 16.5 | 11 | 8.3 | 34400 | 26200 | 76.16% | 2.38 | 24800 | R-410A
214649708 | 2.83 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36D44+TDR | MGH96M100C5A | 34000 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
212975084 | 1.43 | Yes | Yes | DAY & NIGHT | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH18ABK | EA*4X24L17A* | *96VTN0401712B* | 17200 | 16 | 10.5 | 8.5 | 18200 | 19400 | 106.6% | 2.34 | 12300 | R-410A
213773377 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X42L21A*+WALLCON | *80CTL0451712B* | 23600 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.94 | 20800 | R-410A
212632889 | 3.79 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-048-230A** | LD41/59Y9 | EL296DF090XV60C* | 45500 | 20 | 12 | 9.1 | 42000 | 35000 | 83.33% | 1.84 | 40000 | R-410A
215683649 | 1.93 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3617AM*+UI | 58TN*B070C14**12 | 23200 | 17 | 10 | 9 | 23600 | 16600 | 70.34% | 1.98 | 20000 | R-454B
215683717 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 59TN6C100C21**22 | 24000 | 17.5 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
216820407 | 4.21 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RCFY6024STANM | FR951V0855A21M4 | 50500 | 16 | 10 | 8.1 | 50500 | 38500 | 76.24% | 2 | 42000 | R-454B
216820440 | 4.25 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RCFY6024STANM | FR97MV0855A21DH | 51000 | 17 | 10 | 10 | 51000 | 38000 | 74.51% | 2 | 42000 | R-454B
216820539 | 4.08 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RCFY6021STAAM | FR801V1005A21UHS | 49000 | 17 | 10 | 8.1 | 49000 | 39000 | 79.59% | 2 | 42000 | R-454B
216820625 | 4.04 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RCFY6021STAAM | FR951V0855A21M4 | 48500 | 16 | 10 | 8.1 | 48500 | 39500 | 81.44% | 2 | 42500 | R-454B
216820174 | 3.46 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4824STANM | FR802V1255A24UH | 41500 | 18 | 10 | 8.1 | 41500 | 37400 | 90.12% | 2.1 | 40000 | R-454B
216819991 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4824STANM | FR97MV0855A21DH | 41000 | 17 | 10 | 8.1 | 41000 | 37800 | 92.2% | 2.1 | 40000 | R-454B
212362764 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3137*6A*+TXV | G*VC960803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362783 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VM970803BNB* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362633 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VM970804CNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362634 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CSCF3642N6D*+TXV | A*VM971005CNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212632772 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD30/36Y9 | SLP99DF110XV60C* | 33400 | 20 | 13 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 32800 | R-410A
214649693 | 2.68 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36C34+TDR | MGH96M060B3A | 32200 | 16.5 | 11 | 8.3 | 34400 | 26200 | 76.16% | 2.39 | 24800 | R-410A
215683591 | 1.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**2417AM*+UI | 59MN7C080C17**14 | 22800 | 16.5 | 10 | 9 | 24000 | 16900 | 70.42% | 1.94 | 20400 | R-454B
215683593 | 1.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**2417AM*+UI | 59TN6C040C14**10 | 22400 | 15.5 | 9 | 8.5 | 24400 | 17200 | 70.49% | 1.82 | 20800 | R-454B
215683675 | 1.98 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3717AM*+UI | 58TN*B090C17**16 | 23800 | 17 | 10.5 | 9 | 23400 | 16500 | 70.51% | 2 | 19800 | R-454B
205750632 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *80CTL0451712A* | 24200 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2 | 20800 | R-410A
205751002 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X37L21A*+WALLCON | *80CTL0701716A* | 32800 | 17.5 | 11.5 | 8.5 | 33000 | 25200 | 76.36% | 1.98 | 32000 | R-410A
205751211 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X43L21A*+WALLCON | *96CTN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
215669502 | 2.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6121AM*+UI | 59CU5B060C17**16 | 34600 | 17.5 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
214630374 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | PL36H210P299 | 59CU5A060C17**16 | 24000 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 2 | 19600 | R-410A
214630387 | 1.95 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | V,C36H175P149 | 59CU5B060C17**16 | 23400 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.96 | 19800 | R-410A
214630406 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | PL36H210P299 | 59MN7C060C17**14 | 24000 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 2 | 19600 | R-410A
214389923 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG3K960 | 58TN*B090C21**20 | 44000 | 21 | 11.7 | 9.5 | 44500 | 35800 | 80.45% | 2.3 | 42500 | R-410A
214610140 | 3.67 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP18AZ48AJVC | TCFZ6021SEAAM | FR98MV1005A21UP | 44000 | 19 | 10 | 8.1 | 43500 | 45500 | 104.6% | 1.9 | 45000 | R-410A
214610142 | 3.71 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP18AZ48AJVC | TCFZ6021SEAAM | FR97MV1005A21DH | 44500 | 19 | 10 | 8.1 | 43500 | 45000 | 103.4% | 2 | 44500 | R-410A
212362765 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3137*6A*+TXV | G*VM970603BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362767 | 2.83 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+MBVC1201**-1A*+TXV |  | 34000 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362784 | 2.77 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VM970804CNB* | 33200 | 19 | 12 | 8.2 | 33600 | 24400 | 72.62% | 1.8 | 21400 | R-410A
212362799 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VC960804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
213773847 | 2 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L24A*+WALLCON | *97CMN1202422B* | 24000 | 16.5 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
206765548 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0701412A* | 24400 | 17.5 | 11.5 | 8.5 | 21200 | 16600 | 78.3% | 2.02 | 20600 | R-410A
206765566 | 1.95 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L14A*+WALLCON | *80CTL0701412A* | 23400 | 17 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
216057003 | 2.68 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X36A1 | 5TAMXD04AV31 |  | 32200 | 18.1 | 10.5 | 8.5 | 33200 | 25200 | 75.9% | 2.1 | 31000 | R-454B
213773827 | 2.02 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L24A*+WALLCON | *80CTL1352422B* | 24200 | 17 | 11 | 8.1 | 21000 | 16500 | 78.57% | 2.02 | 20400 | R-410A
216453146 | 3.67 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X48A1 | 5PX*B006AS3 | S8V2B080M4PCB | 44000 | 19.2 | 11.7 | 9.4 | 47000 | 33400 | 71.06% | 2.1 | 42500 | R-454B
216057019 | 4.42 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X60A1 | 5TAMXD07AV51 |  | 53000 | 18.1 | 10 | 8.5 | 54000 | 39000 | 72.22% | 1.9 | 48000 | R-454B
215869121 | 3.71 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X48A1 | 5TXCB006AS3 | S9V2B060U4VSB+LRP | 44500 | 18.1 | 10 | 8.5 | 46000 | 35400 | 76.96% | 2.1 | 43000 | R-454B
204300382 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X42AAL+WALLCON | *80CTL0701412A* | 32400 | 17 | 11 | 8.1 | 33200 | 25000 | 75.3% | 1.94 | 31800 | R-410A
204298978 | 2.63 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X42L21A*+WALLCON | *97CMN0801714A* | 31600 | 17 | 11 | 8.1 | 33400 | 24800 | 74.25% | 1.86 | 31600 | R-410A
213772767 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *97CMN0601714B* | 24200 | 15.5 | 10.5 | 8.1 | 20000 | 16700 | 83.5% | 2 | 20800 | R-410A
213773037 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *80CTL0451712B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
204300082 | 2.68 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X36AAL+WALLCON | *80CTL1352422A* | 32200 | 16.5 | 11 | 8.1 | 33200 | 24600 | 74.1% | 1.94 | 31400 | R-410A
212628025 | 2.78 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.5 | 34000 | 29200 | 85.88% | 2.81 | 26400 | R-410A
212628041 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C36+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.5 | 34000 | 30200 | 88.82% | 2.85 | 27000 | R-410A
212628061 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TL8E100C20UH11 | 33200 | 17.5 | 10 | 8.5 | 34000 | 27400 | 80.59% | 2.69 | 25400 | R-410A
212628110 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V100C20MP12 | 33000 | 17.5 | 9 | 8.5 | 34000 | 28400 | 83.53% | 2.7 | 26000 | R-410A
215938449 | 3.75 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | C5H3V48*K*AAA* | EVD5X61M21A*+WALLCON | *80CTL0901716B* | 45000 | 21 | 12 | 8.1 | 53500 | 37600 | 70.28% | 1.95 | 43000 | R-454B
214630423 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*032* | C36A***L159 | 59TN6B060C17**14 | 23600 | 16 | 11 | 8.1 | 19800 | 16300 | 82.32% | 1.94 | 19800 | R-410A
216820640 | 4.04 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RCFY6021STAAM | FR951V0705A21M4 | 48500 | 16 | 10 | 8.1 | 48500 | 39500 | 81.44% | 2 | 42500 | R-454B
216820239 | 4.25 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RCFY6024STANM | FR98MV1155A24UP | 51000 | 17 | 10 | 10 | 51000 | 38000 | 74.51% | 2 | 42000 | R-454B
212621565 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B24+TDR | TPLC100C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32200 | 27600 | 85.71% | 2.44 | 25000 | R-410A
212621618 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8V100C20MP12 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212621619 | 2.38 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8V120C20MP12 | 28600 | 15.6 | 8.4 | 8.5 | 32400 | 27400 | 84.57% | 2.7 | 25000 | R-410A
212621632 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TPLC100C20MP13 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27400 | 84.57% | 2.45 | 25000 | R-410A
212362801 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VC961005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362816 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VC960603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
206765755 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *96CTN0601714A* | 23400 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
206765782 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *97CMN0801714A* | 23600 | 16.5 | 11 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
212632753 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Z9 | SLP99DF070XV36B* | 33400 | 21 | 12.5 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 33000 | R-410A
212632767 | 2.78 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | SL25XPV-036-230A** | LD31/36Z9 | SLP99DF090XV60C* | 33400 | 20 | 13 | 8.7 | 34400 | 29400 | 85.47% | 1.76 | 33000 | R-410A
213281547 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | C(A,C,D,E)42D24+TDR | Y81E080C20LMPS1 | 32400 | 16.6 | 8 | 8.1 | 36000 | 26400 | 73.33% | 2.83 | 25400 | R-410A
214584502 | 1.88 | Yes | No | BOSCH | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | BOVA-36HDN1-M20G | D(A,C,E)36C44+TDR |  | 22600 | 15.2 | 12 | 9 | 24000 | 20000 | 83.33% | 1.97 | 19400 | R-410A
213355439 | 2.9 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | L(E,G)M48C6 |  | 34800 | 18 | 9 | 8.2 | 36000 | 26400 | 73.33% | 2.82 | 25400 | R-410A
215295718 | 2.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | HE35936 | *96VTN1202422A* | 35600 | 16 | 10 | 8.1 | 36800 | 34600 | 94.02% | 1.88 | 28400 | R-410A
215869123 | 3.79 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X48A1 | 5TXCC007AS3 | S9V2C100U5VSB+LRP | 45500 | 18.1 | 10 | 8.5 | 46000 | 35200 | 76.52% | 2.1 | 43000 | R-454B
215869137 | 4.5 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X60A1 | 5PX*D010AS3 | S9V2C100U5VSB+LRP | 54000 | 18.1 | 10 | 8.5 | 55000 | 39500 | 71.82% | 2 | 49000 | R-454B
211174179 | 3.67 | Yes | No | COMFORT-AIRE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HRG1548S1R-**A | C(A,C,D,E)60D34+TDR | GUH96C110C5M | 44000 | 15.5 | 12.4 | 8.4 | 45000 | 31600 | 70.22% | 2.86 | 13400 | R-410A
216057013 | 3.83 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X48A1 | 5TAMXD06AV41 |  | 46000 | 18.1 | 10.5 | 8.5 | 45500 | 34800 | 76.48% | 2.1 | 42500 | R-454B
213773067 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *80CTL0902120B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
213773087 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *95CSU0601716B* | 23600 | 16.5 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.92 | 20800 | R-410A
213772517 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X48AAL+WALLCON | *97CMN0801714B* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2.02 | 20600 | R-410A
215669381 | 2.87 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X60M24A*+WALLCON | *97CMN0802120B* | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215668556 | 2.82 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M17A*+WALLCON | *80CTL0701412B* | 33800 | 17.5 | 9.5 | 9 | 35800 | 25600 | 71.51% | 1.86 | 30800 | R-454B
214649694 | 2.78 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)36D44+TDR | MGH96M060B3A | 33400 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
214649705 | 2.85 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48D44+TDR | MGH96M080C4A | 34200 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
214777200 | 4.33 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV602C*A+TXV | TL9E100C20UH11 | 52000 | 19 | 11 | 8.5 | 51500 | 38000 | 73.79% | 2 | 35800 | R-454B
214777201 | 3.71 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV602C*A+TXV | TM9E080C16MP12 | 44500 | 18 | 11 | 8.5 | 43500 | 34000 | 78.16% | 2 | 33200 | R-454B
214777215 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CV602C*A+TXV | TMLE130D20MP11 | 54000 | 19 | 11 | 8.5 | 53000 | 39500 | 74.53% | 2 | 37000 | R-454B
216981021 | 3.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | H,YG88*60+TXV-BLEED | Y82E100C16LMPS1 | 45000 | 17 | 11 | 9 | 43500 | 32200 | 74.02% | 2 | 33000 | R-454B
215439775 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D36+TDR | TM9V080C16MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.66 | 25400 | R-410A
215669671 | 2.9 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *95CSU0802120B* | 34800 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
215669789 | 2.8 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *80CTL0701716B* | 33600 | 16.5 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.78 | 31000 | R-454B
215669837 | 2.8 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU0601716B* | 33600 | 16 | 9 | 8.5 | 35800 | 25600 | 71.51% | 1.76 | 31000 | R-454B
206133467 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *80CSU1002120A* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
206133799 | 2.02 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L17A*+WALLCON | *95CSU0601716A* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16800 | 78.5% | 1.98 | 20800 | R-410A
213607588 | 1.51 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | PF4TNXB24L* |  | 18100 | 16.5 | 11 | 8.5 | 18200 | 18200 | 100% | 2.2 | 12400 | R-410A
213773687 | 2 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X48L21A*+WALLCON | *80CTL0451712B* | 24000 | 16.5 | 10.5 | 8.1 | 21000 | 16700 | 79.52% | 2 | 20600 | R-410A
215295741 | 2.75 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE24936 | *96VTN1202422B* | 33000 | 16 | 9 | 8.45 | 36200 | 34200 | 94.48% | 2 | 28000 | R-410A
215295768 | 2.87 | No | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | H,GE8J936 | *96VTN1202422B* | 34400 | 16 | 9.5 | 8.5 | 36200 | 34200 | 94.48% | 2.02 | 28000 | R-410A
216453148 | 3.67 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X48A1 | 5PX*B006AS3 | S8V2B060M4PCB | 44000 | 19.2 | 11.7 | 9.7 | 46500 | 33600 | 72.26% | 2.1 | 42500 | R-454B
216980433 | 2.65 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | FRH2TY3621STANN |  | 31800 | 19 | 12 | 8.5 | 31800 | 27400 | 86.16% | 2 | 28800 | R-454B
215668764 | 2.85 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *96CTN0601714B* | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215668796 | 2.75 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X42M21A*+WALLCON | *80CSU0601716A* | 33000 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
206771327 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X37L21A*+WALLCON | *97CMN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
216613178 | 4.33 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY60AJVC | RH2VY6024STACN |  | 52000 | 18 | 11.7 | 10 | 50500 | 38000 | 75.25% | 2 | 40000 | R-454B
216453088 | 1.8 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X24A1 | 5TXCB003AS3 | S8V2B080M4PCB | 21600 | 20.6 | 11.5 | 10 | 24200 | 18300 | 75.62% | 2.1 | 23000 | R-454B
216453104 | 2.93 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X36A1 | 5PX*B006AS3 | S8V2B060M4PCB | 35200 | 20 | 12.5 | 9.4 | 32200 | 25000 | 77.64% | 2.1 | 31600 | R-454B
216453138 | 3.02 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X36A1 | 5TXCD010AS3 | S8V2D120M5PDB | 36200 | 20.8 | 13 | 10 | 32000 | 24600 | 76.88% | 2.2 | 31200 | R-454B
215869097 | 2.75 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X36A1 | 5PX*C007AS3 | S9V2C100U5VSB+LRP | 33000 | 18.1 | 10.5 | 8.5 | 33200 | 25400 | 76.51% | 2.1 | 31200 | R-454B
215869147 | 4.5 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X60A1 | 5TXCC009AS3 | S9V2C100U5VSB+LRP | 54000 | 18.1 | 10 | 8.5 | 55500 | 39500 | 71.17% | 2 | 49000 | R-454B
215669853 | 2.82 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | ESH5X36M12A*+WALLCON | *95CSU1002122B* | 33800 | 16.5 | 9.5 | 8.5 | 35800 | 25400 | 70.95% | 1.76 | 30800 | R-454B
215669989 | 2.83 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | ESH5X42M12A*+WALLCON | *80CTL0702120B* | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.76 | 30600 | R-454B
216453084 | 1.83 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X24A1 | 5PX*BD06AS3 | S8V2B080M4PDB | 22000 | 21.4 | 11.7 | 10 | 23400 | 18100 | 77.35% | 2.2 | 22400 | R-454B
213145654 | 3 | Yes | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | DLCURAH36ABK | PL36H175P159+AEFE4B* |  | 36000 | 16 | 10 | 8.1 | 38000 | 35000 | 92.11% | 1.82 | 28600 | R-410A
215669551 | 2.88 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *97CMN0602120B* | 34600 | 18 | 10 | 9 | 34600 | 25000 | 72.25% | 1.9 | 30000 | R-454B
215669651 | 2.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *80CTL1102120B* | 35000 | 18.5 | 10.5 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
216819026 | 1.75 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2417MTANM | FR801V0704A17UH | 21000 | 17 | 10 | 8.1 | 20800 | 17000 | 81.73% | 1.9 | 18200 | R-454B
215683911 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 59CU5B080C21**20 | 34400 | 17.5 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
215683941 | 2.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**4221AM*+UI | 58TN*B070C21**20 | 33000 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215683961 | 2.77 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**4221AM*+UI | 59MN7C080C21**20 | 33200 | 17.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
215683993 | 2.88 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**4321AM*+UI | 59CU5B100C21**22 | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30200 | R-454B
212362549 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | A*VS800604BUA* | 33600 | 18.5 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362583 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | A*VC800805C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
215675695 | 3.96 | No | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *80CTL0451712B* | 47500 | 18 | 9.5 | 9 | 50000 | 37600 | 75.2% | 1.98 | 47500 | R-454B
212362584 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3642C6C*+TXV | A*VC801005C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
214807358 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTU36B5XDS1+JMET08BS2N1+TXV |  | 23000 | 19 | 12 | 9 | 23000 | 17800 | 77.39% | 2 | 17400 | R-454B
205751090 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X37L21A*+WALLCON | *80CTL0901716A* | 33000 | 18 | 11.7 | 8.5 | 32800 | 25000 | 76.22% | 2 | 31800 | R-410A
215933626 | 2.82 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *95CSU1002122B* | 33800 | 19.5 | 11.7 | 9 | 34600 | 26400 | 76.3% | 1.94 | 30200 | R-454B
215933526 | 2.8 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H3V36*K*AAA* | ESH5X48M12A*+WALLCON | *80CSU1002120A* | 33600 | 19.5 | 11.5 | 9 | 34800 | 26600 | 76.44% | 1.94 | 30600 | R-454B
213307376 | 2.6 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | DM36A36+TDR | TM9Y080C16MP11 | 31200 | 18.3 | 9.3 | 8.1 | 33600 | 28000 | 83.33% | 2.6 | 25600 | R-410A
211377731 | 2.73 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DBCN1 | TM9V060B12MP12 | 32800 | 17 | 9.5 | 8.1 | 33000 | 23400 | 70.91% | 1.98 | 25000 | R-410A
211377888 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DBCN1 | TM9E080B12MP12 | 34000 | 17.5 | 9.5 | 8.1 | 34000 | 24400 | 71.76% | 2.06 | 25800 | R-410A
211378315 | 2.8 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DXXN1+TXV | TM8V080B12MP12 | 33600 | 17 | 9.5 | 8.1 | 33600 | 23600 | 70.24% | 2.02 | 25400 | R-410A
211378890 | 2.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DBCN1 | TL8E100C20UH11 | 34000 | 17.5 | 10 | 8.5 | 34000 | 24000 | 70.59% | 2.12 | 25400 | R-410A
215669642 | 2.92 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6124AM*+UI | 58TN*B110C21**20 | 35000 | 18.5 | 10.5 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
216551711 | 1.9 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP19AY24AJVC | RCFY2421HEAAM | FR98MV1005A21UP | 22800 | 21 | 13 | 10 | 22800 | 18500 | 81.14% | 1.8 | 21200 | R-454B
213350199 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Y82E120C20LMPS1 | 31600 | 18.4 | 9.3 | 8.5 | 33200 | 27800 | 83.73% | 2.7 | 25400 | R-410A
213320464 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9E060B12MP12 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
213320482 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES040A12SMPS1 | 33200 | 18 | 10 | 8.4 | 33000 | 30000 | 90.91% | 2.79 | 26600 | R-410A
213320497 | 2.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES080C20LMPS1 | 32800 | 18 | 10 | 8.5 | 33400 | 28400 | 85.03% | 2.71 | 25800 | R-410A
213320500 | 2.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES080C20SMPS1 | 32800 | 18 | 10 | 8.5 | 33400 | 28400 | 85.03% | 2.71 | 25800 | R-410A
213320515 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES100C20LMPS1 | 32800 | 17.5 | 9.5 | 8.5 | 33400 | 27600 | 82.63% | 2.7 | 25400 | R-410A
213320516 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES100C20LMPS1 | 32200 | 17.5 | 9.4 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A
216055660 | 2.6 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TL9E100C20UH11 | 31200 | 17 | 10.5 | 8.5 | 31600 | 25400 | 80.38% | 2 | 27800 | R-454B
216055661 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8E080B12MP11 | 30800 | 18 | 10.5 | 8.5 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
214807374 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTU36B5XDS1+TXV | Y81E080B12SMPS1 | 33200 | 18 | 11.7 | 8.5 | 30400 | 24800 | 81.58% | 2 | 26800 | R-454B
213278581 | 2.83 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B361 | D(A,C,E)36A44+JMVT12BC2N1+TDR |  | 34000 | 18 | 8.9 | 8.1 | 36000 | 26400 | 73.33% | 2.81 | 25400 | R-410A
213274537 | 3.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | THF2B48T21 | D(A,C,E)60A44+TDR | TM8Y080C16MP11 | 43000 | 16 | 11.5 | 8.2 | 44500 | 31600 | 71.01% | 3.11 | 30800 | R-410A
213772267 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *80CTL0701412B* | 24200 | 16.5 | 10.5 | 8.1 | 21200 | 16600 | 78.3% | 2 | 20600 | R-410A
213772417 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EHD4X42AAL+WALLCON | *96CTN1202422B* | 24200 | 16 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 2 | 20600 | R-410A
213367382 | 1.93 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AB3* | H,PG31930 | 59TP6C100V21**22 | 23200 | 17 | 9.5 | 8.5 | 24800 | 22800 | 91.94% | 1.92 | 18100 | R-410A
213772717 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X25L17A*+WALLCON | *80CTL0451712B* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 2 | 20800 | R-410A
213772867 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *80CTL0901716B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.9 | 20800 | R-410A
213772917 | 1.95 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *96CTN0601714B* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16700 | 77.31% | 1.9 | 20800 | R-410A
213773117 | 1.97 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *97CMN1002122B* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
216055777 | 2.53 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TMLE120C16MP11 | 30400 | 18 | 11.2 | 8.5 | 30200 | 24800 | 82.12% | 2 | 26400 | R-454B
216055795 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C100C16MP13 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27200 | R-454B
216056866 | 3.42 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C120D20MP13 | 41000 | 17.5 | 11.5 | 8.1 | 44000 | 33400 | 75.91% | 2 | 32400 | R-454B
216055844 | 3.33 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | TL8E080C16UH11 | 40000 | 16.5 | 11.2 | 8.1 | 44000 | 33600 | 76.36% | 2 | 32400 | R-454B
216055981 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | D(A,C,E)60A3K+TDR | TPLC080C16MP13 | 40500 | 16.5 | 11.5 | 8.1 | 43500 | 33400 | 76.78% | 2 | 31800 | R-454B
216055813 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES080C16SMPS1 | 31000 | 18 | 11 | 8.5 | 30800 | 25000 | 81.17% | 2 | 27000 | R-454B
216055827 | 2.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C16SMPS1 | 31600 | 18 | 11.2 | 8.1 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
216056028 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z9ES080C16SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
216056030 | 3.46 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Z9ES080C16SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 46500 | 33800 | 72.69% | 2 | 32800 | R-454B
216055828 | 2.62 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | Z8ES120C16SMPS1 | 31400 | 18 | 11 | 8.5 | 31200 | 25200 | 80.77% | 2 | 27400 | R-454B
213803489 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ET080C16LMPS1 | 33600 | 18.5 | 9.5 | 8.1 | 32600 | 29800 | 91.41% | 2.74 | 26400 | R-410A
212362570 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3743*6D*+TXV | A*VC961005CNB* | 33600 | 19 | 12 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362611 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | A*VM970603BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362613 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | A*VM970804CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212621650 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | CPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621652 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42A44+TDR | CPLC100C20MP13 | 31800 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621685 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8V100C20MP12 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621701 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM8V100C20MP12 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621734 | 2.47 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TMLV120C20MP12 | 29600 | 15.9 | 8 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621751 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TMLV120C20MP12 | 32600 | 16.5 | 9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621783 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TPLC120C20MP13 | 30000 | 16 | 8.6 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
212621786 | 2.62 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TPLC120C20MP13 | 31400 | 16.5 | 8.9 | 8.1 | 32400 | 27800 | 85.8% | 2.44 | 25200 | R-410A
215683971 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**4321AM*+UI | 58CU*A040C17**12 | 34400 | 18 | 10 | 9 | 35200 | 25200 | 71.59% | 1.88 | 30400 | R-454B
215684057 | 2.83 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*4212AM*+UI | 58CU*A060C17**16 | 34000 | 16.5 | 9.5 | 8.5 | 35600 | 25400 | 71.35% | 1.78 | 30600 | R-454B
215683687 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA024A*030* | CAA**3721AM*+UI | 58CU*A040C17**12 | 24000 | 18 | 10.5 | 9 | 23200 | 16300 | 70.26% | 2.02 | 19600 | R-454B
214807366 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTM36B5ADS1 | TP9C060B12MP13 | 23000 | 17 | 12 | 9 | 23000 | 17600 | 76.52% | 2 | 17100 | R-454B
206771444 | 2.63 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *97CMN0801714A* | 31600 | 17 | 11 | 8.1 | 33400 | 24800 | 74.25% | 1.86 | 31600 | R-410A
206771561 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L24A*+WALLCON | *97CMN1002122A* | 31800 | 17.5 | 11.5 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
212362815 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VS960603BUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362832 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CSCF3642N6D*+TXV | G*VC801005C*A* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216613179 | 1.77 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RH2VY3617STACN |  | 21200 | 18 | 11.7 | 9.5 | 20600 | 17000 | 82.52% | 2 | 18100 | R-454B
214610141 | 3.67 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP18AZ48AJVC | TCFZ6021SEAAM | FR962V0855A21M4 | 44000 | 18 | 10 | 8.1 | 43500 | 45500 | 104.6% | 2 | 45000 | R-410A
214610124 | 1.9 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP18AZ24AJVC | TCFZ2421HEAAM | FR802V1004A17UH | 22800 | 20 | 12.5 | 8.5 | 22800 | 26000 | 114% | 2.1 | 25400 | R-410A
215674023 | 3.63 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *80CTL0451712B* | 43500 | 17 | 9 | 9 | 49000 | 35000 | 71.43% | 2.02 | 43500 | R-454B
206765710 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L17A*+WALLCON | *80CTL0901716A* | 23600 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
215683899 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 58TN*B070C17**16 | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.9 | 30400 | R-454B
214573993 | 2.7 | Yes | Yes | COMFORTMAKER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | CVH837GKA2* | EA*4X48L24A*+WALLCON | *95CSU1002122B* | 32400 | 17.5 | 11.5 | 8.5 | 32200 | 24800 | 77.02% | 2 | 31400 | R-410A
216819165 | 1.75 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2417MTANM | FR962V0603A17M4 | 21000 | 17 | 10 | 8.1 | 21000 | 17100 | 81.43% | 1.9 | 18200 | R-454B
216819235 | 1.75 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2421MTANM | FR98MV0703A17UP | 21000 | 18 | 10 | 8.1 | 20800 | 17000 | 81.73% | 1.9 | 18200 | R-454B
211379131 | 2.77 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC48FBCN1 | YP9C100C20MP13 | 33200 | 17 | 9 | 8.5 | 32000 | 23400 | 73.12% | 2.04 | 25000 | R-410A
211377679 | 2.8 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAUB36DXXN1+TXV | YP9C080B12MP13 | 33600 | 17.5 | 10 | 8.5 | 33400 | 23400 | 70.06% | 2.04 | 25000 | R-410A
211377713 | 2.65 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC30CXXN1+TXV | TM9V060B12MP12 | 31800 | 16.5 | 9 | 8.1 | 33000 | 23200 | 70.3% | 1.96 | 26000 | R-410A
211377813 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DXXN1+TXV | TM9V040A10MP12 | 32400 | 16.5 | 9.5 | 8.1 | 32600 | 23000 | 70.55% | 1.96 | 24800 | R-410A
211378281 | 2.63 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB30CXXN1+TXV | TPLC080B12MP13 | 31600 | 16.5 | 9 | 8.1 | 32800 | 23000 | 70.12% | 1.96 | 25600 | R-410A
214649695 | 2.75 | Yes | Yes | MIDEA | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | MOVB-60HDN1-M18M | D(A,C,E)48C34+TDR | MGH96M060B3A | 33000 | 16.5 | 11.7 | 8.5 | 34600 | 26000 | 75.14% | 2.41 | 24800 | R-410A
211378299 | 2.82 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFC36DBCN1 | TPLC080B12MP13 | 33800 | 17 | 9.5 | 8.1 | 34000 | 24200 | 71.18% | 2.04 | 25600 | R-410A
211378347 | 2.7 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB30CXXN1+TXV | YPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 23600 | 70.24% | 2 | 26400 | R-410A
211378429 | 2.83 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAUB36DXXN1+TXV | YPLC060A12MP13 | 34000 | 17.5 | 9.5 | 8.1 | 34000 | 24200 | 71.18% | 2.06 | 25600 | R-410A
211378465 | 2.8 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DBCN1 | TMLE120C16MP11 | 33600 | 17.5 | 10 | 8.1 | 33000 | 23200 | 70.3% | 2.04 | 24800 | R-410A
211378531 | 2.78 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHC36DXXN1+TXV | TMLE100B12MP11 | 33400 | 17.5 | 9.5 | 8.1 | 33000 | 23400 | 70.91% | 2.02 | 24800 | R-410A
211378549 | 2.77 | No | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAHB36DXXN1+TXV | TMLE100B12MP11 | 33200 | 17.5 | 9.5 | 8.1 | 33000 | 23400 | 70.91% | 2.02 | 25000 | R-410A
214442672 | 3.71 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | YH2F48TB21 | L(E,G)M48F4 |  | 44500 | 15.2 | 12 | 8.1 | 45500 | 37400 | 82.2% | 3.63 | 34400 | R-410A
216056458 | 1.75 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E040A12MP11 | 21000 | 16.5 | 11.7 | 9 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216055460 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8V080B12MP12 | 22400 | 17 | 12 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18100 | R-454B
216055545 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TMLE040A12MP11 | 20800 | 16.5 | 11.7 | 8.5 | 22400 | 17200 | 76.79% | 2 | 17400 | R-454B
216055593 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ES060A12SMPS1 | 20800 | 17.5 | 11.7 | 8.5 | 22400 | 17300 | 77.23% | 2 | 17500 | R-454B
216055595 | 1.8 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES080B12SMPS1 | 21600 | 18 | 12 | 8.1 | 22400 | 18500 | 82.59% | 2 | 18300 | R-454B
216055611 | 1.73 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | Z8ET060A12LMPS1 | 20800 | 18.8 | 11.7 | 8.5 | 22800 | 17700 | 77.63% | 2 | 18000 | R-454B
216055626 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES040A10SMPS1 | 19500 | 17 | 11.2 | 8.5 | 23000 | 17800 | 77.39% | 2 | 18400 | R-454B
213773187 | 2.02 | Yes | No | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L17A*+WALLCON | *80CTL0901716B* | 24200 | 16.5 | 10.5 | 8.1 | 21400 | 16700 | 78.04% | 1.98 | 20800 | R-410A
214442624 | 3.71 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | H,PG48960 | 59TN6C120C24**22 | 44500 | 21 | 12 | 9.5 | 44000 | 35800 | 81.36% | 2.36 | 42000 | R-410A
205751122 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EA*4X43L21A*+WALLCON | *80CTL0701716A* | 32800 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 1.98 | 32000 | R-410A
206135925 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EN(A,D,W)4X48L21**+WALLCON | *80CSU1002120A* | 32400 | 17 | 11.5 | 8.1 | 33000 | 24800 | 75.15% | 1.94 | 31400 | R-410A
215669322 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6024AM*+UI | 58TN*B110C21**20 | 34400 | 18.5 | 10.5 | 9 | 34200 | 24600 | 71.93% | 1.92 | 29600 | R-454B
215669342 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6024AM*+UI | 59CU5B080C21**20 | 34400 | 18 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
215669392 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6024AM*+UI | 59MN7C120C24**22 | 34400 | 18.5 | 10 | 9 | 34200 | 24800 | 72.51% | 1.9 | 29800 | R-454B
206772317 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EN(A,D,W)4X48L21**+WALLCON | *96CTN1002122A* | 32400 | 17.5 | 11.7 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31400 | R-410A
206772660 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X36AAL+WALLCON | *80CTL0901716A* | 32400 | 17 | 11 | 8.1 | 33200 | 24600 | 74.1% | 1.94 | 31600 | R-410A
212380551 | 1.97 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | V,C36H175P159 | 58TN*A090C17**16 | 23600 | 21 | 13.5 | 8.5 | 24800 | 19300 | 77.82% | 2.48 | 23600 | R-410A
212380585 | 2 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA424A*031* | PL36H210P299 | 59TN6B060C17**14 | 24000 | 20 | 13 | 8.5 | 25000 | 19500 | 78% | 2.5 | 24000 | R-410A
214063090 | 4.5 | Yes | Yes | TRANE | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 4TWV8X60A1 | FG49960+P0V0D000M50SC+RP |  | 54000 | 18 | 12 | 8.2 | 49500 | 38500 | 77.78% | 1.75 | 48500 | R-410A
212621866 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | CP9C120D20MP13 | 30600 | 16.6 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621883 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42B34+TDR | TM9V120D20MP12 | 32000 | 17 | 9.4 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212621885 | 2.52 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM9V120D20MP12 | 30200 | 16.5 | 9.1 | 8.5 | 32400 | 28200 | 87.04% | 2.79 | 25400 | R-410A
212621900 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | TP9C120D20MP13 | 30600 | 16.6 | 9 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621903 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B44+TDR | TP9C120D20MP13 | 32600 | 17 | 9.5 | 8.1 | 32400 | 28200 | 87.04% | 2.51 | 25400 | R-410A
212621951 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D24+TDR | TM9V040A10MP12 | 30000 | 16.6 | 9.1 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212621952 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9V040A10MP12 | 32200 | 17 | 9.5 | 8.1 | 33200 | 27400 | 82.53% | 2.41 | 25200 | R-410A
212621985 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM9E100C20MP12 | 32000 | 15.5 | 9.9 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
216056876 | 3.46 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | Y81E120C20SMPS1 | 41500 | 17.5 | 11.5 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
214650240 | 4.5 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | CTU60D5XHS1+TXV | TP9C120D20MP13 | 54000 | 19 | 11 | 9 | 54500 | 39500 | 72.48% | 2 | 37600 | R-454B
213320510 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES100C16LMPS1 | 32200 | 18 | 9.4 | 8.5 | 33200 | 28200 | 84.94% | 2.7 | 25600 | R-410A
216055672 | 2.55 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8E100B12MP11 | 30600 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27400 | R-454B
216055690 | 2.58 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8V080C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055692 | 2.6 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TM8V100C16MP12 | 31200 | 18 | 10.5 | 8.1 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216055697 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM8Y080C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216057009 | 2.73 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X36A1 | 5TAMXD07AV51 |  | 32800 | 17.5 | 10.5 | 8.5 | 32200 | 24800 | 77.02% | 2.1 | 30400 | R-454B
213613563 | 1.47 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | L(E,G)M24D4 |  | 17600 | 15.2 | 9.8 | 8.2 | 19200 | 18300 | 95.31% | 2.2 | 12800 | R-410A
212362763 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3137*6A*+TXV | G*VC960603BNB* | 33600 | 18 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362777 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VC960803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362820 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VC961005CNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362845 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CSCF3642N6D*+TXV | G*VM971205DNB* | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216055699 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y080C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216055974 | 3.42 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)60A3K+TDR | TP9C100C20MP13 | 41000 | 18 | 10.5 | 8.5 | 44500 | 33800 | 75.96% | 2 | 33000 | R-454B
216056010 | 3.38 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH860E2S11 | C(A,C,D,E)48A3K+TDR | Z8ES120C20SMPS1 | 40500 | 17.5 | 11.2 | 8.1 | 45000 | 34000 | 75.56% | 2 | 33400 | R-454B
211378588 | 2.83 | Yes | No | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | XAFB36DBCN1 | TM8E100B12MP11 | 34000 | 18 | 10 | 8.1 | 33800 | 23800 | 70.41% | 2.06 | 25400 | R-410A
216055751 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)36B3K+TDR | TM9Y100C16MP11 | 30800 | 18 | 10.5 | 8.5 | 31000 | 25200 | 81.29% | 2 | 27400 | R-454B
216055758 | 2.58 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | TMLE080B12MP11 | 31000 | 18 | 10.5 | 8.1 | 31400 | 25400 | 80.89% | 2 | 27600 | R-454B
216055833 | 2.57 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | C(A,C,D,E)48A3K+TDR | Z8ET080B12LMPS1 | 30800 | 19 | 11.2 | 8.1 | 30000 | 24800 | 82.67% | 2 | 26400 | R-454B
214650381 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | CTU36B5XDS1+TXV | Y81E080B12SMPS1 | 23000 | 19 | 12 | 9.5 | 23000 | 18600 | 80.87% | 2 | 18300 | R-454B
216055438 | 1.77 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM8E040A12MP11 | 21200 | 17 | 11.7 | 8.5 | 22600 | 17200 | 76.11% | 2 | 17500 | R-454B
216055442 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM8E060A12MP11 | 21000 | 17.5 | 11.2 | 9 | 23000 | 17900 | 77.83% | 2 | 18200 | R-454B
216055467 | 1.72 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM8Y060A12MP11 | 20600 | 17.5 | 10.5 | 8.5 | 22600 | 18400 | 81.42% | 2 | 18600 | R-454B
216055488 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9E060A10MP12 | 19500 | 16 | 10 | 9 | 23000 | 18100 | 78.7% | 2 | 18600 | R-454B
212622001 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TM9E100C20MP12 | 33400 | 15.5 | 10 | 8.1 | 33200 | 27000 | 81.33% | 2.43 | 25000 | R-410A
212622067 | 2.7 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM8Y060A12MP11 | 32400 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622069 | 2.5 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B24+TDR | TM8Y060A12MP11 | 30000 | 17.4 | 9.5 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622084 | 2.73 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C34+TDR | TM8Y060A12MP11 | 32800 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622086 | 2.77 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM8Y060A12MP11 | 33200 | 18 | 10 | 8.1 | 33400 | 27400 | 82.04% | 2.42 | 25200 | R-410A
212622100 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM8Y080B12MP11 | 32400 | 18 | 9.9 | 8.4 | 33400 | 27400 | 82.04% | 2.63 | 25200 | R-410A
212622118 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TM8Y080B12MP11 | 32200 | 18 | 9.9 | 8.5 | 33400 | 27400 | 82.04% | 2.65 | 25200 | R-410A
212622284 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42B34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
216055492 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9E060A10MP12 | 21000 | 17 | 10.5 | 9 | 22800 | 18100 | 79.39% | 2 | 18600 | R-454B
216055497 | 1.85 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TM9E060B12MP12 | 22200 | 17 | 11.7 | 8.1 | 22600 | 18300 | 80.97% | 2 | 18500 | R-454B
216055540 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | TM9Y080B12MP11 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18500 | 81.14% | 2 | 18600 | R-454B
216055556 | 1.88 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TMLE080B12MP11 | 22600 | 17 | 12 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216055581 | 1.87 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A3K+TDR | TPLC080B12MP13 | 22400 | 17 | 12 | 8.1 | 22600 | 17700 | 78.32% | 2 | 18000 | R-454B
216055583 | 1.67 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24A3K+TDR | Z8ES040A12SMPS1 | 20000 | 17.5 | 11.2 | 9 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
212622287 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.1 | 33600 | 28200 | 83.93% | 2.64 | 25800 | R-410A
212622385 | 2.78 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TL9E100C20UH11 | 33400 | 17 | 10 | 8.1 | 33600 | 29000 | 86.31% | 2.69 | 26200 | R-410A
212622419 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A34+TDR | TL9E080C16UH11 | 31200 | 17.4 | 9.3 | 8.3 | 33600 | 28000 | 83.33% | 2.62 | 25600 | R-410A
212622905 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM9E080B12MP12 | 32400 | 17.5 | 9.9 | 8.4 | 33800 | 27400 | 81.07% | 2.62 | 25400 | R-410A
212623038 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TM9E080B12MP12 | 30800 | 17.2 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623072 | 2.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9E080B12MP12 | 33200 | 17.5 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.65 | 25400 | R-410A
212623089 | 2.58 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8E120C16MP11 | 31000 | 17.9 | 9.8 | 8.3 | 33800 | 28800 | 85.21% | 2.73 | 26200 | R-410A
216551889 | 3.79 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP19AY48AJVC | RCFY4821SEAAM | FR962V0855A21M4 | 45500 | 19 | 11.7 | 10 | 45500 | 42000 | 92.31% | 2.1 | 42000 | R-454B
216055606 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)36A4K+TDR | Z8ES100B12SMPS1 | 21000 | 19 | 11.2 | 9.5 | 22800 | 18000 | 78.95% | 2 | 18400 | R-454B
216055608 | 1.63 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z8ET060A12LMPS1 | 19500 | 18 | 11.2 | 9 | 23000 | 17700 | 76.96% | 2 | 18100 | R-454B
215674083 | 3.67 | No | No | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V48*K*AAA* | EA*5X48M21A*+WALLCON | *95CSU0601716B* | 44000 | 17 | 9 | 9 | 49000 | 34600 | 70.61% | 2.04 | 43000 | R-454B
212623103 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48A34+TDR | TM9Y100C20MP11 | 32200 | 15.5 | 9.4 | 8.1 | 33800 | 27400 | 81.07% | 2.38 | 25400 | R-410A
212623106 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM8E060A12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
206771102 | 2.62 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X36L21A*+WALLCON | *97CMN0801714A* | 31400 | 17 | 11 | 8.1 | 33400 | 24600 | 73.65% | 1.84 | 31400 | R-410A
215669572 | 2.9 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**6121AM*+UI | 59MN7C100C21**22 | 34800 | 18.5 | 10.5 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
206765728 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X36L21A*+WALLCON | *80CTL0701716A* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20800 | R-410A
206765926 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *80CTL0451712A* | 24200 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2 | 20800 | R-410A
206765980 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X37L21A*+WALLCON | *97CMN0601714A* | 24200 | 16 | 11 | 8.1 | 21200 | 16800 | 79.25% | 2 | 20800 | R-410A
206771759 | 2.68 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X48L21A*+WALLCON | *80CTL0701716A* | 32200 | 17.5 | 11.5 | 8.1 | 32600 | 25000 | 76.69% | 1.96 | 31600 | R-410A
206772380 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EN(A,D)4X48L24**+WALLCON | *96CTN1202422A* | 32400 | 17.5 | 11.7 | 8.1 | 32800 | 24800 | 75.61% | 1.96 | 31400 | R-410A
206772831 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X42AAL+WALLCON | *80CTL0901716A* | 32600 | 17 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31600 | R-410A
206773448 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *95CSU1002122A* | 31800 | 17.5 | 11 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
212362556 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CA*F3137*6A*+TXV | A*VM970803BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212623123 | 2.75 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E060A12MP11 | 33000 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623136 | 2.45 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B24+TDR | TM8E100B12MP11 | 29400 | 17.2 | 9.4 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212362609 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | ASZV903610A* | CHPF3743C6B*+TXV | A*VS960805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
216891267 | 2.68 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | RCFY3621MTANM | FR951V0603A17UH | 32200 | 18 | 12 | 10 | 32200 | 28200 | 87.58% | 2.1 | 29800 | R-454B
214610126 | 2.85 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | FRP18AZ36AJVC | TCFZ6021SEAAM | FR97MV1005A21DH | 34200 | 19 | 12.5 | 8.5 | 34200 | 43000 | 125.7% | 2.2 | 40500 | R-410A
214608803 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D36+JMET12CS2N1+TDR |  | 33000 | 17.5 | 9 | 8.5 | 32600 | 28000 | 85.89% | 2.79 | 25000 | R-410A
216054683 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | CPLC080C16MP13 | 31000 | 18 | 11 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216054699 | 2.58 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8V100C16MP12 | 31000 | 18 | 10.5 | 8.5 | 31200 | 25400 | 81.41% | 2 | 27600 | R-454B
216054702 | 2.57 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TM8Y100C16MP11 | 30800 | 18 | 11 | 8.5 | 30400 | 25000 | 82.24% | 2 | 26800 | R-454B
216891400 | 1.77 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2421MTANM | FR801V1004A17UH | 21200 | 17 | 11.7 | 8.1 | 20800 | 16900 | 81.25% | 1.9 | 18100 | R-454B
213612033 | 1.83 | Yes | No | RUUD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RP15AZ24AJ2N | D(A,C,E)24A34+TDR | R962V0603A17M4S | 22000 | 15.4 | 11.8 | 8.1 | 22800 | 16400 | 71.93% | 2.84 | 15900 | R-410A
212623137 | 2.68 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36B34+TDR | TM8E100B12MP11 | 32200 | 18 | 9.9 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623139 | 2.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C34+TDR | TM8E100B12MP11 | 32600 | 18 | 10 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
216891770 | 2.7 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | RCFY3624MTANM | FR962V0855A21M4 | 32400 | 19 | 12 | 10 | 32400 | 28000 | 86.42% | 2.1 | 29600 | R-454B
216891568 | 2.63 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | RCFY3617STANM | FR802V0754A17UH | 31600 | 19 | 12 | 8.5 | 31600 | 27600 | 87.34% | 2 | 29000 | R-454B
212362756 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | AMVE36CP1400A* |  | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362761 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3137*6A*+TXV | G*VC960403BNB* | 33600 | 18 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
206771462 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *97CMN1002122A* | 31800 | 17 | 11.5 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
206771480 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L21A*+WALLCON | *96CTN1002122A* | 31800 | 17 | 11.5 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
204300452 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X48AAL+WALLCON | *80CTL0902120A* | 32600 | 17 | 11 | 8.1 | 33000 | 25000 | 75.76% | 1.98 | 31600 | R-410A
204300602 | 2.7 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA** | EHD4X48AAL+WALLCON | *97CMN0602120A* | 32400 | 16.5 | 11 | 8.1 | 33200 | 25200 | 75.9% | 1.94 | 32000 | R-410A
215669531 | 2.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X61M21A*+WALLCON | *95CSU1002122B* | 35000 | 18 | 10 | 9 | 34400 | 24800 | 72.09% | 1.92 | 29800 | R-454B
213320495 | 2.68 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES080C16SMPS1 | 32200 | 18 | 9.9 | 8.5 | 33200 | 27400 | 82.53% | 2.7 | 25200 | R-410A
216819789 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4824STANM | FR97MV1005A21DH | 41000 | 18 | 10 | 8.1 | 41000 | 37800 | 92.2% | 2.1 | 40000 | R-454B
216819905 | 3.38 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4821STANM | FR801V0504A17UHU | 40500 | 16 | 10 | 8.1 | 40500 | 38000 | 93.83% | 2 | 40500 | R-454B
212623155 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42C24+TDR | TM8E100B12MP11 | 30400 | 17.5 | 9 | 8.5 | 33800 | 27400 | 81.07% | 2.64 | 25400 | R-410A
212623172 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | TMLE060A12MP11 | 30800 | 17.7 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
206765620 | 1.95 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EA*4X30L17A*+WALLCON | *97CMN0801714A* | 23400 | 16 | 10.5 | 8.1 | 21600 | 16800 | 77.78% | 1.9 | 20800 | R-410A
206766873 | 1.98 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA3* | EHD4X30AAL+WALLCON | *80CTL0901716A* | 23800 | 16 | 10.5 | 8.1 | 21800 | 16700 | 76.61% | 1.98 | 20800 | R-410A
205750664 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *96CTN0601714A* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
205750680 | 2.02 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *97CMN0601714A* | 24200 | 16 | 11 | 8.1 | 21200 | 16800 | 79.25% | 2 | 20800 | R-410A
205750744 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *97CMN0602120A* | 24400 | 16.5 | 11 | 8.1 | 21200 | 16700 | 78.77% | 2.02 | 20600 | R-410A
216054734 | 2.63 | No | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | D(A,C,E)36A4K+TDR | TP9C100C20MP13 | 31600 | 18 | 9.8 | 8.5 | 32400 | 26000 | 80.25% | 2 | 28400 | R-454B
213320490 | 2.63 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ES080C16LMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 27400 | 82.53% | 2.7 | 25200 | R-410A
213320507 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES100B12SMPS1 | 32200 | 18.5 | 9.4 | 8.1 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
216819240 | 1.73 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2421MTANM | FR951V0603A17UH | 20800 | 17 | 10 | 8.1 | 20800 | 17100 | 82.21% | 1.9 | 18300 | R-454B
215668756 | 2.88 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V36*K*AAA* | EA*5X37M21A*+WALLCON | *97CMN1002122B* | 34600 | 18 | 10 | 9 | 35200 | 25000 | 71.02% | 1.9 | 30400 | R-454B
216494141 | 2.72 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 293VAN036**AA* | CE(P,V)3621G34*+TXV | 88*TB48070C17*** | 32600 | 19 | 11 | 9.5 | 33600 | 26600 | 79.17% | 2 | 30000 | R-454B
213320443 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E080B12MP11 | 32800 | 18 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.61 | 25800 | R-410A
213320454 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.1 | 33600 | 28600 | 85.12% | 2.66 | 26000 | R-410A
213320493 | 2.63 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ES080C16SMPS1 | 31600 | 17.9 | 9.8 | 8.5 | 33200 | 27400 | 82.53% | 2.7 | 25200 | R-410A
216891336 | 2.7 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | RCFY3621MTANM | FR962V1005A21M4 | 32400 | 18 | 12 | 10 | 32400 | 28000 | 86.42% | 2.1 | 29400 | R-454B
216891503 | 2.63 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY36AJVC | RCFY3617STANM | FR801V0754A17UH | 31600 | 19 | 12 | 8.5 | 31600 | 27600 | 87.34% | 2 | 29000 | R-454B
214629304 | 2.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ36AB3* | C36A***L129 | 59SU5B060M17**16 | 34200 | 16 | 9 | 8.1 | 36800 | 34600 | 94.02% | 1.86 | 28400 | R-410A
215565300 | 1.87 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | TM8E100B12MP11 | 22400 | 17 | 12 | 9 | 23000 | 18000 | 78.26% | 2 | 18400 | R-454B
212362774 | 2.8 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CA*F3743*6D*+TXV | G*VC960403BNB* | 33600 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362825 | 2.82 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CSCF3642N6D*+MBVC1201**-1A*+TXV |  | 33800 | 18.5 | 11.5 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212623205 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A44+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623206 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36B34+TDR | TMLE100B12MP11 | 32200 | 18 | 9.9 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212362791 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VC800804C*A* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
212362792 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3642C6C*+TXV | G*VS800805CUA* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
206771534 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L24A*+WALLCON | *80CTL1352422A* | 31800 | 17.5 | 11.5 | 8.1 | 33000 | 24400 | 73.94% | 1.9 | 31200 | R-410A
212362817 | 2.78 | Yes | Yes | GOETTL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | GSZV903610A* | CHPF3743C6B*+TXV | G*VC960803BNB* | 33400 | 18 | 11 | 8.2 | 34000 | 24400 | 71.76% | 1.8 | 21600 | R-410A
206133387 | 1.97 | Yes | No | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *80CSU0601716A* | 23600 | 16.5 | 10.5 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20800 | R-410A
206133437 | 2.03 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X37L21A*+WALLCON | *80CSU0401712A* | 24400 | 17 | 11 | 8.5 | 21200 | 16600 | 78.3% | 2.04 | 20600 | R-410A
206772723 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X42AAL+WALLCON | *80CTL1352422A* | 32600 | 17 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.96 | 31600 | R-410A
206772921 | 2.72 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EHD4X48AAL+WALLCON | *96CTN1202422A* | 32600 | 17 | 11 | 8.1 | 33000 | 24800 | 75.15% | 1.98 | 31600 | R-410A
212623220 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D24+TDR | TMLE100B12MP11 | 31200 | 17.8 | 9.7 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623221 | 2.8 | Yes | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48D34+TDR | TMLE100B12MP11 | 33600 | 18 | 10 | 8.1 | 33800 | 27400 | 81.07% | 2.44 | 25400 | R-410A
212623304 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | CP9C080C16MP13 | 30800 | 17.2 | 9 | 8.1 | 33800 | 27400 | 81.07% | 2.45 | 25400 | R-410A
211261777 | 1.49 | Yes | Yes | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ18AB3* | CAP**3017AL* | 82*TA36070V14*** | 17900 | 16.5 | 10.5 | 8.5 | 18300 | 18500 | 101.1% | 2.22 | 12300 | R-410A
213320444 | 2.68 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | TM8E080B12MP11 | 32200 | 18 | 9.4 | 8.4 | 34000 | 28000 | 82.35% | 2.59 | 25800 | R-410A
213320446 | 2.75 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E080C16MP11 | 33000 | 18 | 10 | 8.4 | 34000 | 28400 | 83.53% | 2.74 | 26000 | R-410A
213320487 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ES080B12SMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.68 | 26200 | R-410A
214568834 | 1.95 | Yes | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA825A*031* | H,PE7J936 | 59TN6B060C17**14 | 23400 | 16 | 10.5 | 8.1 | 20000 | 16300 | 81.5% | 1.92 | 19800 | R-410A
214608690 | 2.68 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | CM36B34+TDR | CP9C080C16MP13 | 32200 | 17.5 | 9.9 | 8.1 | 33800 | 23800 | 70.41% | 2.08 | 25000 | R-410A
213320455 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM8E120C16MP11 | 33200 | 18 | 10 | 8.4 | 34000 | 28800 | 84.71% | 2.77 | 26200 | R-410A
215425704 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*30+TXV | TM9E040A10MP12 | 22200 | 16 | 10.5 | 8.65 | 21200 | 17700 | 83.49% | 1.94 | 17400 | R-454B
215425729 | 1.83 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE24*36+TXV | TM9V040A10MP12 | 22000 | 16 | 10.5 | 8.55 | 21200 | 17100 | 80.66% | 1.92 | 16700 | R-454B
215425731 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*24+TXV | TM9V040A10MP12 | 22200 | 16 | 10.5 | 8.65 | 21200 | 17100 | 80.66% | 1.94 | 16700 | R-454B
215675815 | 4 | Yes | Yes | HEIL | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | H5H0V48*K*AAA* | EVM5X60M21A*+WALLCON | *97CMN1002122B* | 48000 | 19 | 10 | 9 | 50000 | 36800 | 73.6% | 2 | 46500 | R-454B
213320530 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES120C20SMPS1 | 32800 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
215669681 | 2.92 | Yes | Yes | TEMPSTAR | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | T5H0V36*K*AAA* | EA*5X61M24A*+WALLCON | *95CSU1002122B* | 35000 | 18.5 | 10 | 9 | 34400 | 24600 | 71.51% | 1.92 | 29800 | R-454B
213320520 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ES120C16LMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
214807372 | 2.77 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH836E2S11 | CTU36B5XDS1+TXV | Y82E080B12LMPS1 | 33200 | 19 | 11.7 | 9 | 30400 | 24800 | 81.58% | 2 | 26800 | R-454B
213320501 | 2.68 | No | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES080C20SMPS1 | 32200 | 18 | 9.9 | 8.5 | 33200 | 28200 | 84.94% | 2.71 | 25600 | R-410A
216057048 | 1.88 | Yes | No | COLEMAN | HRCU-A-C (Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR |  | 22600 | 15.2 | 11 | 8.5 | 22800 | 21200 | 92.98% | 2.72 | 18700 | R-454B
215425738 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*24+TXV | TM9V060B12MP12 | 22200 | 17 | 11 | 8.65 | 21200 | 17200 | 81.13% | 1.94 | 16900 | R-454B
215425747 | 1.92 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE33*30+TXV | TM9V080B12MP12 | 23000 | 17 | 12 | 9 | 21400 | 17900 | 83.64% | 2 | 17600 | R-454B
215425758 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*30+TXV-BLEED | TM9Y060B12MP11 | 22200 | 17 | 11 | 8.65 | 21200 | 17300 | 81.6% | 1.94 | 17000 | R-454B
215425790 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE24*36+TXV | Y82E060A12LMPS1 | 21800 | 18 | 11 | 8.55 | 21200 | 17300 | 81.6% | 1.92 | 17100 | R-454B
215425797 | 1.82 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE24*36+TXV | Y82E080B12LMPS1 | 21800 | 18 | 11 | 9 | 21200 | 17500 | 82.55% | 1.92 | 17200 | R-454B
215425799 | 1.85 | Yes | Yes | YORK | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | H,YE32*24+TXV | Y82E080B12LMPS1 | 22200 | 18 | 11 | 9.1 | 21200 | 17500 | 82.55% | 1.94 | 17200 | R-454B
213320488 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES080B12SMPS1 | 33000 | 18 | 9.5 | 8.4 | 33000 | 29600 | 89.7% | 2.76 | 26400 | R-410A
213320527 | 2.73 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES120C20LMPS1 | 32800 | 17.5 | 9.5 | 8.5 | 34000 | 28000 | 82.35% | 2.66 | 25800 | R-410A
216624575 | 1.97 | Yes | No | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL18KSLV-024-230** | L*18/36V*+TXV+LEFE3A* |  | 23600 | 15.2 | 11.7 | 8.5 | 22400 | 19600 | 87.5% | 1.75 | 18000 | R-454B
212623407 | 2.8 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36C34+TDR | TM8Y120C20MP11 | 33600 | 18 | 9.5 | 8.3 | 33800 | 30200 | 89.35% | 2.82 | 27000 | R-410A
212623487 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C24+TDR | TM8Y100C20MP11 | 32600 | 18 | 9 | 8.4 | 33800 | 30000 | 88.76% | 2.83 | 26800 | R-410A
212623490 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D24+TDR | TM8Y120C20MP11 | 32600 | 18 | 9 | 8.4 | 33800 | 30000 | 88.76% | 2.83 | 26800 | R-410A
212623507 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36C24+TDR | TM8Y120C20MP11 | 31800 | 18 | 9.4 | 8.5 | 33800 | 30000 | 88.76% | 2.85 | 26800 | R-410A
212623523 | 2.65 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42A34+TDR | TM9V100C20MP12 | 31800 | 17.5 | 9.4 | 8.4 | 33800 | 28200 | 83.43% | 2.67 | 25800 | R-410A
212623537 | 2.63 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | TM9V100C20MP12 | 31600 | 17.5 | 9.3 | 8.5 | 33800 | 28200 | 83.43% | 2.7 | 25800 | R-410A
212623555 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36D24+TDR | TM9E040A10MP12 | 31200 | 17 | 9.5 | 8.1 | 33400 | 28400 | 85.03% | 2.42 | 25800 | R-410A
212623605 | 2.72 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TM9Y060B12MP11 | 32600 | 17.5 | 9.5 | 8.1 | 34000 | 29400 | 86.47% | 2.43 | 26600 | R-410A
206133377 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *80CSU0401712A* | 23600 | 17 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
206133779 | 1.97 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH825GKA2* | EA*4X36L21A*+WALLCON | *95CSU0802120A* | 23600 | 16.5 | 11 | 8.1 | 21400 | 16600 | 77.57% | 1.94 | 20600 | R-410A
212628125 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D36+TDR | TP9C100C20MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 28400 | 83.53% | 2.46 | 26000 | R-410A
213320473 | 2.75 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | TM9E100C16MP12 | 33000 | 18 | 10 | 8.1 | 33600 | 27200 | 80.95% | 2.65 | 25200 | R-410A
213320524 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D34+TDR | Z8ES120C16SMPS1 | 33600 | 18 | 9.5 | 8.4 | 33000 | 30400 | 92.12% | 2.84 | 26800 | R-410A
212626390 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36D26+TDR | TM9E100C16MP12 | 30400 | 17.5 | 9 | 8.5 | 33600 | 27200 | 80.95% | 2.66 | 25200 | R-410A
213320483 | 2.77 | Yes | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES040A12SMPS1 | 33200 | 18 | 10 | 8.1 | 32600 | 29800 | 91.41% | 2.68 | 26400 | R-410A
216819472 | 3.54 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4824MTANM | FR962V0855A21M4 | 42500 | 17 | 10 | 8.1 | 42500 | 33600 | 79.06% | 2 | 36200 | R-454B
216819672 | 3.42 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4824STANM | FR98MV1155A24UP | 41000 | 17 | 10 | 8.1 | 41000 | 37800 | 92.2% | 2.1 | 40000 | R-454B
206771021 | 2.62 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X36L17A*+WALLCON | *80CTL0701412A* | 31400 | 17.5 | 11 | 8.1 | 33400 | 24400 | 73.05% | 1.84 | 31400 | R-410A
206771255 | 2.73 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X37L21A*+WALLCON | *80CTL0701716A* | 32800 | 17.5 | 11.5 | 8.5 | 33000 | 25200 | 76.36% | 1.98 | 32000 | R-410A
214052502 | 1.97 | Yes | Yes | LENNOX | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | EL22XPV-024-230A** | HG80936 | ML296UH045XV36B* | 23600 | 20 | 13 | 8.5 | 21600 | 15200 | 70.37% | 1.88 | 13600 | R-410A
213613593 | 2 | No | No | BRYANT HEATING AND COOLING SYSTEMS | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 38MURAQ24AA3* | L(E,G)M36L4 |  | 24000 | 15.5 | 9 | 9 | 25400 | 22600 | 88.98% | 2.89 | 20200 | R-410A
213320526 | 2.63 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ES120C20LMPS1 | 31600 | 17.5 | 9.3 | 8.5 | 33800 | 27800 | 82.25% | 2.66 | 25600 | R-410A
206771525 | 2.65 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X42L24A*+WALLCON | *80CTL0902120A* | 31800 | 17.5 | 11.5 | 8.1 | 33200 | 24400 | 73.49% | 1.9 | 31400 | R-410A
215683901 | 2.87 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 58TN*B070C21**20 | 34400 | 18 | 10 | 9 | 35400 | 25200 | 71.19% | 1.88 | 30400 | R-454B
215683919 | 2.85 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**3721AM*+UI | 59MN7C080C17**14 | 34200 | 17.5 | 9.5 | 9 | 35400 | 25400 | 71.75% | 1.88 | 30600 | R-454B
215683951 | 2.77 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CAA**4221AM*+UI | 59CU5B080C21**20 | 33200 | 17.5 | 9.5 | 8.5 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
216055644 | 1.75 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | Z9ES080B12SMPS1 | 21000 | 17 | 11.7 | 8.5 | 22800 | 18100 | 79.39% | 2 | 18300 | R-454B
216055645 | 1.83 | Yes | Yes | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B3K+TDR | Z9ES080B12SMPS1 | 22000 | 17 | 12 | 8.1 | 22600 | 18100 | 80.09% | 2 | 18200 | R-454B
212623639 | 2.7 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | CPLC080B12MP13 | 32400 | 17 | 9.5 | 8.1 | 33600 | 29400 | 87.5% | 2.42 | 26400 | R-410A
212623672 | 2.55 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TL9E060B12UH11 | 30600 | 17.7 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623688 | 2.75 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)42D34+TDR | TL9E060B12UH11 | 33000 | 18 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.4 | 25600 | R-410A
212623705 | 2.67 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)36A44+TDR | TM9E060B12MP12 | 32000 | 17.5 | 9.4 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623721 | 2.53 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48B24+TDR | TM9E060B12MP12 | 30400 | 17 | 9.1 | 8.1 | 34000 | 28000 | 82.35% | 2.39 | 25800 | R-410A
212623822 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)42D24+TDR | CP9C060B12MP13 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623825 | 2.6 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48D24+TDR | CP9C060B12MP13 | 31200 | 17.3 | 9.2 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623840 | 2.73 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48B34+TDR | CP9C060B12MP13 | 32800 | 17.5 | 9.5 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623857 | 2.57 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | C(A,C,D,E)48C24+TDR | TM9V060B12MP12 | 30800 | 17.2 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
212623873 | 2.77 | No | No | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48C34+TDR | TM9V060B12MP12 | 33200 | 17.5 | 9 | 8.1 | 34000 | 27800 | 81.76% | 2.42 | 25600 | R-410A
215565316 | 1.72 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z8ES040A12SMPS1 | 20600 | 17.5 | 11.2 | 9.5 | 23000 | 18100 | 78.7% | 2 | 18500 | R-454B
215565317 | 1.73 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)37E2J+TDR | Z8ES060A12SMPS1 | 20800 | 17.5 | 11.7 | 9 | 22600 | 17300 | 76.55% | 2 | 17600 | R-454B
215670406 | 2.87 | No | No | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | CSAH*6012AM*+UI | 58TN*B070C14**12 | 34400 | 16.5 | 9.5 | 8.5 | 34800 | 25000 | 71.84% | 1.78 | 30200 | R-454B
213320525 | 2.8 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES120C16SMPS1 | 33600 | 18 | 9.5 | 8.1 | 32600 | 30200 | 92.64% | 2.73 | 26600 | R-410A
216054585 | 1.77 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | C(A,C,D,E)24D2K+TDR | TM9V060B12MP12 | 21200 | 17 | 11.7 | 8.5 | 22800 | 18000 | 78.95% | 2 | 18300 | R-454B
216054599 | 1.88 | Yes | Yes | COLEMAN | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HH824E2S11 | D(A,C,E)24B4K+TDR | TM9Y060B12MP11 | 22600 | 17 | 11.7 | 8.5 | 22800 | 18400 | 80.7% | 2 | 18700 | R-454B
214271747 | 3.67 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | PL60H210P299 | 58TN*B090C21**20 | 44000 | 21 | 11.7 | 9.5 | 44000 | 35800 | 81.36% | 2.38 | 42000 | R-410A
214271782 | 3.75 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 25VNA448A*031* | PL60H210P179 | 58TN*B110C21**20 | 45000 | 21 | 12 | 9.5 | 43500 | 35600 | 81.84% | 2.36 | 42000 | R-410A
206771696 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X43L21A*+WALLCON | *97CMN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
206771714 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X43L21A*+WALLCON | *96CTN1002122A* | 33000 | 17.5 | 11.7 | 8.5 | 33000 | 25200 | 76.36% | 2 | 31800 | R-410A
206771723 | 2.75 | Yes | Yes | AIRQUEST | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HVH837GKA2* | EA*4X43L21A*+WALLCON | *80CTL0901716A* | 33000 | 18 | 11.7 | 8.5 | 32800 | 25000 | 76.22% | 2 | 31800 | R-410A
213320486 | 2.75 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)48A34+TDR | Z8ES080B12LMPS1 | 33000 | 18 | 9.5 | 8.1 | 32600 | 29400 | 90.18% | 2.66 | 26200 | R-410A
216453106 | 2.98 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V0X36A1 | 5PX*D008AS3 | S8V2D120M5PDB | 35800 | 20.6 | 13 | 10 | 32200 | 25000 | 77.64% | 2.2 | 31600 | R-454B
215869095 | 2.65 | Yes | Yes | AMERICAN STANDARD | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 5A6V8X36A1 | 5PX*C005AS3 | S9V2C080U5VSB+LRP | 31800 | 18.1 | 10 | 8.5 | 32800 | 25400 | 77.44% | 2.1 | 31000 | R-454B
216819149 | 1.75 | Yes | No | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY24AJVC | RCFY2417MTANM | FR97MV0703A17DH | 21000 | 18 | 10 | 8.1 | 21000 | 17000 | 80.95% | 1.9 | 18200 | R-454B
215670606 | 2.78 | Yes | Yes | CARRIER | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | 27VNA036A*030* | FE5BN(B,X)C36L*+UI |  | 33400 | 18.5 | 10 | 9 | 35800 | 25600 | 71.51% | 1.86 | 31000 | R-454B
216891419 | 3.58 | Yes | Yes | FRIEDRICH | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | RD18AY48AJVC | RCFY4824MTANM | FR801V0755A21DZ | 43000 | 18 | 11.7 | 8.5 | 43000 | 33200 | 77.21% | 2.1 | 36000 | R-454B
213320517 | 2.63 | No | No | CHAMPION HEATING AND COOLING | HRCU-A-CB (Split System: Heat Pump with Remote Outdoor Unit-Air-Source) | Centrally-Ducted | HMH72B341 | D(A,C,E)36A34+TDR | Z8ES100C20SMPS1 | 31600 | 17.5 | 9.3 | 8.5 | 33200 | 27400 | 82.53% | 2.71 | 25200 | R-410A